## Export
Agency | WO # | Description | Location Full Desc. | Category of Works | Trade Group | Trade | Vendor Name | Priority | Status | Reported Date | Target Comp | Actual Comp | Comp Status | Completion Notes
MSA-DTWD | WA3285616 | RETROSPECTIVE WORK ORDER-Donot attend Lift out of order | Carlisle Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 3 | CLOSE | 04 Jan 2017 | 2017-01-10 17:00:00 | 2017-01-04 07:15:00 | Pass | Retrospective work order raised
MSA-DCS | WA1013741 | Unit 1 House 1 Cell 1, 3 & 4 Reed switch magnets loose | West Kimberley Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Optic Security Group Norwest | 3 | COMP | 17 Mar 2017 | 2017-03-24 17:00:00 | 2017-09-19 12:30:00 | Fail
MSA-DCS | WA1128845 | Unit 1 cell 20, gpo faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Materials (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 26 Jun 2017 | 2017-07-03 17:00:00 | 2017-06-27 11:00:00 | Pass
MSA-DCS | WA1130479 | Turner- TV not getting signal aerial fine | Banksia Hill Detention Centre | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | COMMERCIAL ANTENNA SYSTEMS | 2 | COMP | 29 Jun 2017 | 2017-07-04 17:00:00 | 2017-07-20 09:45:00 | Fail
MSA-DCS | WA1132789 | Lock on back gate not working | Walcott Centre (Central West Metro ) | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | COMP | 04 Jul 2017 | 2017-07-05 10:07:39 | 2017-07-04 12:00:00 | Pass
MSA-DCS | WA1135258 | Unit 6-D wing-bottom bunk personal light not working cell D7 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 10 Jul 2017 | 2017-07-13 17:00:00 | 2017-07-11 09:15:00 | Pass
MSA-DCS | WA1158709 | Veggie Prep - The Whole Unit-electrical plug needs to be attached to processing machine | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 21 Jul 2017 | 2017-07-28 17:00:00 | 2017-07-21 10:00:00 | Pass
MSA-DCS | WA1158712 | Unit 2- D Wing- Lights need new thombstones & passage lights 6-7 11-12 areas | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 21 Jul 2017 | 2017-07-28 17:00:00 | 2017-07-21 12:30:00 | Pass
MSA-DCS | WA1192461 | Level 1- Walkway- Flickering light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 24 Aug 2017 | 2017-08-29 17:00:00 | 2017-08-29 11:30:00 | Pass
MSA-DCS | WA1193396 | Unit 5- D5- light cover damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 28 Aug 2017 | 2017-08-30 17:00:00 | 2017-08-31 11:00:00 | Fail
MSA-DFES | WA1196764 | Station officers bathroom, broken glass door | CFRS Armadale | GMP-BR | Building | Doors (BU) | GREG'S GLASS | 2 | COMPFIN | 04 Sep 2017 | 2017-09-07 17:00:00 | 2017-10-03 14:30:00 | Fail
MSA-DFES | WA1196976 | Broken power pit near, applied training car park-Warning may be asbestos | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 04 Sep 2017 | 2017-09-11 17:00:00 | 2017-09-08 14:15:00 | Pass
MSA-DCS | WA1197142 | unit 4 cell 34 exhaust fan faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 05 Sep 2017 | 2017-09-11 17:00:00 | 2017-09-13 15:00:00 | Fail
MSA-DCS | WA1197580 | SOG Pod- Crypt- Replace damaged double GPO near sink | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 05 Sep 2017 | 2017-09-12 17:00:00 | 2017-09-05 15:32:00 | Pass
MSA-DFES | WA1198877 | Change room 4 & 5- lights not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 07 Sep 2017 | 2017-09-14 17:00:00 | 2017-09-08 15:00:00 | Pass
MSA-DFES | WA1199367 | Cockburn Central - Main Entrance Foyer - Fire panel fault. | CFRS Success-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 08 Sep 2017 | 2017-09-09 19:43:49 | 2017-09-11 14:00:00 | Fail
MSA-DFES | WA1199717 | Wellness office-light above desk needs repairing, it has gone out | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 11 Sep 2017 | 2017-09-14 17:00:00 | 2017-09-13 13:40:00 | Pass
MSA-DCS | WA1225273 | Unit 3 - D Wing-SO concerned that after a water leak in cell GPO's | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 22 Sep 2017 | 2017-10-02 17:00:00 | 2017-09-22 14:47:00 | Pass
MSA-DCS | WA1230716 | Unit 3 - B Wing light & cover on landing broken ,please repair | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 06 Oct 2017 | 2017-10-13 17:00:00 | 2017-10-11 10:00:00 | Pass
MSA-DCS | WA1248995 | WWTP - Temporaty plant is working at 50% capacity | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 2 | COMP | 11 Oct 2017 | 2017-10-16 17:00:00 | 2017-10-12 11:00:00 | Pass
MSA-DFES | WA1277199 | Lights faulty in various areas | CFRS Kiara | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 01 Nov 2017 | 2017-11-06 17:00:00 | 2017-11-07 12:50:00 | Fail
MSA-MRWA | WA1277826 | Cafe- are AC units- Please investigate and rectify the Daiken AC units. System has stopped working | Don Aitken Centre MRWA Head Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | COMP | 02 Nov 2017 | 2017-11-03 17:00:00 | 2017-11-13 15:30:00 | Fail
MSA-MRWA | WA1280120 | Basement level server room lost power - please reset the CRAC units | Don Aitken Centre MRWA Head Office | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | COMP | 08 Nov 2017 | 2017-11-08 11:55:02 | 2017-11-08 10:30:00 | Pass
MSA-DCS | WA1331385 | Level 4- Light is flickering RM 4.1 | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 04 Dec 2017 | 2017-12-07 17:00:00 | 2017-12-21 15:30:00 | Fail
MSA-DCS | WA1345467 | Outpatients ceiling lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 19 Dec 2017 | 2017-12-20 08:13:59 | 2017-12-19 11:00:00 | Pass
MSA-DCS | WA1347381 | Unit 6 C12 bottom bunk lght not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 20 Dec 2017 | 2017-12-21 11:15:03 | 2017-12-20 13:20:00 | Pass
MSA-DCS | WA1347396 | Infirmary - Plant-Room North multiple lights out | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 20 Dec 2017 | 2017-12-29 17:00:00 | 2017-12-20 15:20:00 | Pass
MSA-DCS | WA1347441 | Unit 13 - Switchboard room Lights out | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 20 Dec 2017 | 2017-12-29 17:00:00 | 2017-12-21 09:30:00 | Pass
MSA-DCS | WA1347912 | SOG Pod - Crypt - GPO not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 21 Dec 2017 | 2018-01-02 17:00:00 | 2017-12-21 11:30:00 | Pass
MSA-DCS | WA1351070 | Waste water treatment plant- not processing correctly | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 1 | COMP | 02 Jan 2018 | 2018-01-03 07:18:08 | 2018-01-03 13:30:00 | Fail
MSA-DCS | WA1353767 | EC9 Power fence fail (lightning strikes)-Seme on site | West Kimberley Regional Prison | WSM-BR-RC | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 Jan 2018 | 2018-01-15 17:00:00 | 2019-03-14 09:46:00 | Fail | WORK ORDER COMPLETED
MSA-DCS | WA1353918 | new WWTP media filter leaking from base | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | MAK Industrial Water Solutions Pty Ltd | 3 | COMP | 08 Jan 2018 | 2018-01-15 17:00:00 | 2018-01-10 16:00:00 | Pass
MSA-DCS | WA1374596 | Unit C6 cell light tombstone has perished | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 17 Jan 2018 | 2018-01-22 17:00:00 | 2018-01-17 13:30:00 | Pass
MSA-DCS | WA1376978 | Unit 6- A & C Wing- washing machine not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 18 Jan 2018 | 2018-01-22 17:00:00 | 2018-02-05 14:00:00 | Fail
MSA-DCS | WA1377215 | WWTP- ARS pump keeps going out on thermo overload | Karnet Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | MAK Industrial Water Solutions Pty Ltd | 1 | COMP | 18 Jan 2018 | 2018-01-19 10:17:56 | 2018-01-22 11:00:00 | Fail
MSA-DCS | WA1377221 | WWTP- New clarifier tank not operating correclty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | MAK Industrial Water Solutions Pty Ltd | 1 | COMPFIN | 18 Jan 2018 | 2018-01-19 10:20:53 | 2018-02-22 15:00:00 | Fail
MSA-DCS | WA1388558 | Banksia Hill Detention Centre-North Sally Port Admissions-Gate sensor box damaged. | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | COMPFIN | 31 Jan 2018 | 2018-02-02 17:00:00 | 2018-01-31 09:49:00 | Pass
MSA-DCS | WA1388926 | Admin Office- Amplifier in Deputy Supers Office is not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 31 Jan 2018 | 2018-02-07 17:00:00 | 2018-01-31 14:00:00 | Pass
MSA-DCS | WA1390456 | Unit 1 - B Wing-Light cover missing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 02 Feb 2018 | 2018-02-07 17:00:00 | 2018-02-27 14:30:00 | Fail
MSA-DCS | WA1398689 | Unit 1- Office light fitting faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 07 Feb 2018 | 2018-02-14 17:00:00 | 2018-03-07 14:30:00 | Fail
MSA-DCS | WA1408509 | Unit 4 A11 power socket not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 12 Feb 2018 | 2018-02-15 17:00:00 | 2018-02-12 10:20:00 | Pass
MSA-DCS | WA1408528 | Unit 6 - A Wing - kitchen power fault | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 12 Feb 2018 | 2018-02-13 08:11:09 | 2018-02-12 14:30:00 | Pass
MSA-DCS | WA1408532 | Unit 14 - The Whole Unit - Unit 14 cell B16 light switch cover broken and D11 lightswitch broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 12 Feb 2018 | 2018-02-13 08:17:47 | 2018-02-13 10:30:00 | Fail
MSA-DCS | WA1408535 | Unit 13 - B & D - B9, B10 & B11 main lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 12 Feb 2018 | 2018-02-13 08:20:20 | 2018-02-13 13:00:00 | Fail
MSA-DCS | WA1409716 | Unit 2 A wing ceiling light cover broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 13 Feb 2018 | 2018-02-15 17:00:00 | 2018-02-13 15:00:00 | Pass
MSA-DCS | WA1412772 | Lobby CCTV monitor has lost power | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 14 Feb 2018 | 2018-02-15 06:53:19 | 2018-02-14 09:30:00 | Pass
MSA-DCS | WA1412776 | S O P - A7-wall light flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 14 Feb 2018 | 2018-02-15 06:55:44 | 2018-02-15 12:00:00 | Fail
MSA-DCS | WA1412780 | Unit 6 B/D dayroom fridge power point damaged | Casuarina Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 14 Feb 2018 | 2018-02-15 07:00:50 | 2018-02-15 10:00:00 | Fail
MSA-DCS | WA1412912 | Admin - Tearoom-Power continually tripping in Admin tearoom | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 14 Feb 2018 | 2018-02-15 08:06:32 | 2018-02-14 12:00:00 | Pass
MSA-DCS | WA1424540 | MPU - M13- Cell light switch loose | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 16 Feb 2018 | 2018-02-23 17:00:00 | 2018-02-16 11:00:00 | Pass
MSA-DCS | WA1426632 | Print Shop electric valve release on Hidelburg 4 colour machine is faulty | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 20 Feb 2018 | 2018-02-23 17:00:00 | 2018-02-22 10:00:00 | Pass
MSA-DCS | WA1441316 | Unit 5 A/C dayroom power outlets have blown | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 06 Mar 2018 | 2018-03-07 06:38:50 | 2018-03-07 09:30:00 | Fail
MSA-DCS | WA1441317 | Unit 1 A4 power point has come away from wall | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 06 Mar 2018 | 2018-03-07 06:41:38 | 2018-03-06 14:00:00 | Pass
MSA-DCS | WA1441318 | Admin tearoom power plug cracked | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 06 Mar 2018 | 2018-03-07 06:44:19 | 2018-03-06 10:00:00 | Pass
MSA-DCS | WA1441323 | Unit 1 D wing cleaning store light switch loose and off wall | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 06 Mar 2018 | 2018-03-07 06:48:54 | 2018-03-06 12:00:00 | Pass
MSA-DCS | WA1441367 | Unit 4 A&C wings including showers have numerous fluros damaged | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 06 Mar 2018 | 2018-03-12 17:00:00 | 2018-03-07 11:30:00 | Pass
MSA-DCA | WA3586543 | RETROSPECTIVE WORK ORDER-Ground Floor- Goods lift- broken emergency stop button-See notes | Maritime Museum Victoria Quay | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 07 Mar 2018 | 2018-03-08 17:00:00 | 2018-03-08 10:30:00 | Pass | COMPLETED
MSA-DCS | WA1454536 | Unit 13 - C7- Lock to cell jams in the locked position | Casuarina Prison | GMP-BR- HO | Security | Keys & Access (SE) | Lock It Locksmiths | 2 | COMP | 15 Mar 2018 | 2018-03-20 17:00:00 | 2018-03-15 12:00:00 | Pass
MSA-DCS | WA1465106 | Infirmary - HC2- Cell Light not working HC2 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 19 Mar 2018 | 2018-03-20 08:13:24 | 2018-03-22 09:30:00 | Fail | Job completed
MSA-DCS | WA1465157 | Unit 5 - B&D - Toaster needs a new plug attatched, wires are exposed. Its in the computer room | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 19 Mar 2018 | 2018-03-20 08:30:18 | 2018-03-19 13:00:00 | Pass | COMPLETED
MSA-DCS | WA1465173 | Unit 2 - B13 - GMPO not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 19 Mar 2018 | 2018-03-20 08:33:10 | 2018-03-20 12:30:00 | Fail | COMPLETED
MSA-DCS | WA1465211 | Unit 5 - C1 - GPO Blocked, unable to plug something in. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 19 Mar 2018 | 2018-03-20 08:47:29 | 2018-03-19 15:00:00 | Pass | COMPLETED
MSA-DCS | WA1465811 | Veggie Prep - Commision potato rumbler, decommsion the other | Casuarina Prison | GMP-BR- HO | Electrical | Materials (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 19 Mar 2018 | 2018-03-20 13:24:35 | 2018-03-20 10:00:00 | Pass | COMPLETED
MSA-DCS | WA1466879 | Outcare- light switch near visits broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 20 Mar 2018 | 2018-03-21 06:56:19 | 2018-03-20 15:00:00 | Pass | COMPLETED
MSA-DCS | WA1467659 | Unit 6 C8 power point is damaged | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 21 Mar 2018 | 2018-03-22 07:04:29 | 2018-03-21 10:00:00 | Pass | COMPLETED
MSA-DCS | WA1467775 | SCU A wing light damaged-- ladder required | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 21 Mar 2018 | 2018-03-26 17:00:00 | 2018-03-21 12:30:00 | Pass | COMPLETED
MSA-DCS | WA1468571 | Light Issues - Unit 3- A4-Light Faulty, only info received. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 22 Mar 2018 | 2018-03-23 09:20:00 | 2018-03-22 12:00:00 | Pass | COMPLETED
MSA-DCS | WA1469105 | MPU M7 bed light damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 23 Mar 2018 | 2018-03-24 06:57:49 | 2018-03-23 10:30:00 | Pass | COMPLETED
MSA-DCS | WA1469652 | Unit 1 - A wing - Officer reports all Awing cell lights are not working - Information below | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 23 Mar 2018 | 2018-03-24 14:35:33 | 2018-03-23 15:40:00 | Pass | COMPLETED
MSA-DCS | WA1480878 | Unit 14 - C6-Light Switch Missing | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 04 Apr 2018 | 2018-04-05 09:54:23 | 2018-04-04 14:00:00 | Pass | COMPLETED
MSA-DCS | WA1481070 | Unit 5 - B10-Personal light cover has been removed needs reattching. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 04 Apr 2018 | 2018-04-05 12:11:28 | 2018-04-10 14:00:00 | Fail | COMPLETED
MSA-DCS | WA1502128 | Outcare kitchen has damaged fluros | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 16 Apr 2018 | 2018-04-18 17:00:00 | 2018-04-18 09:00:00 | Pass | COMPLETED
MSA-DCS | WA1541284 | Unit 4 dayroom south PA speaker faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 3 | CLOSE | 16 May 2018 | 2018-05-23 17:00:00 | 2018-05-16 12:30:00 | Pass | COMPLETED
MSA-DCS | WA1550810 | Level 1- W1.113- Fluro light globes above desk/walkway is flickering | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 22 May 2018 | 2018-05-25 17:00:00 | 2018-05-22 13:30:00 | Pass | COMPLETED
MSA-DCS | WA1553101 | Level 9- Reception area above lounges- Lights need replacing as below | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 25 May 2018 | 2018-05-30 17:00:00 | 2018-05-25 13:00:00 | Pass | COMPLETED
MSA-DCS | WA1554743 | Level 8- WS8.29- Light Flickering | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 29 May 2018 | 2018-05-30 11:37:57 | 2018-05-29 13:30:00 | Pass | COMPLETED
MSA-DCS | WA1554787 | L4-two blow lights in the hall way outside the ladies toilet cubicles | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 29 May 2018 | 2018-06-01 17:00:00 | 2018-05-29 15:30:00 | Pass | COMPLETED
MSA-DCS | WA1554890 | Lenard- C Wing Cell 03- Smashed power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 29 May 2018 | 2018-06-01 17:00:00 | 2018-06-01 12:30:00 | Pass | COMPLETED
MSA-DCS | WA1554916 | Kichen southside Kings ParK side WSQ- Ceiling light above photocopier & kitchen bench lights | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 29 May 2018 | 2018-06-01 17:00:00 | 2018-05-30 08:30:00 | Pass | COMPLETED
MSA-DCS | WA1554944 | L4 rm 4.A-Flickering light tube in resources (photo copy) room near small kitchen on west side of | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 29 May 2018 | 2018-06-01 17:00:00 | 2018-05-30 10:00:00 | Pass | COMPLETED
MSA-DCS | WA1555108 | Level 3- W3.53- Blown light globes | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 30 May 2018 | 2018-06-01 17:00:00 | 2018-05-31 13:00:00 | Pass | COMPLETED
MSA-DCS | WA1555324 | L4-W4.117-flickering light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 30 May 2018 | 2018-06-05 17:00:00 | 2018-05-30 11:30:00 | Pass | COMPLETED
MSA-DCS | WA1555708 | Level 8 WS8.89 light out near small round table | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 30 May 2018 | 2018-05-31 15:45:41 | 2018-05-31 14:00:00 | Pass | COMPLETED
MSA-DCS | WA1555945 | Level 3 desk W3.12-Light globe replacement required. | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 2 | CLOSE | 31 May 2018 | 2018-06-06 17:00:00 | 2018-05-31 11:00:00 | Pass | COMPLETED
MSA-DCS | WA1556109 | Level 1 Room - RM1.A Flashing light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | DCS-Electrical - Programmed Facility Management | 1 | CLOSE | 31 May 2018 | 2018-06-01 12:29:10 | 2018-06-01 09:00:00 | Pass | COMPLETED
MSA-DCS | WA1665949 | Repair generator that failed during shutdown reference inv 7798110 | Banksia Hill Detention Centre | GMP-BR- HO | Equipment Hire | Compressors, Generators (EH) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 3 | CLOSE | 06 Jul 2018 | 2018-07-13 17:00:00 | 2018-08-17 08:30:00 | Fail | job completed as per conversation with Shannyn from Cummins
MSA-DCS | WA1652185 | admin / stores no tv reception | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL ANTENNA SYSTEMS | 3 | CLOSE | 26 Jul 2018 | 2018-08-02 17:00:00 | 2018-11-07 12:45:00 | Fail | Job completed as per notes from vendor
MSA-MRWA | WA1664096 | L7-Male toilets-Left hand vertical fluorescent light adjacent to the mirror in the toilets is out. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 06 Aug 2018 | 2018-08-09 17:00:00 | 2018-08-08 09:20:00 | Pass | Comp
MSA-MRWA | WA1694054 | Level 5 Kitchen please replace flickering fluro | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 20 Aug 2018 | 2018-08-27 17:00:00 | 2018-08-20 14:09:00 | Pass | All 6 bulbs changed out in level 5 kitchen
MSA-MRWA | WA1694967 | Basement men’s lockers: Faulty lockers as per notes below: | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 2 | CLOSE | 21 Aug 2018 | 2018-08-24 17:00:00 | 2018-08-24 08:31:00 | Pass | Lockers require new keys, locker 18 requires new lock. Reported issues for locksmith to attend and rectify
MSA-MRWA | WA1695156 | Level 5 529 Supply area light panel is loose | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 22 Aug 2018 | 2018-08-23 17:00:00 | 2018-08-22 08:45:00 | Pass | Refixed grill into position
MSA-MRWA | WA1695386 | Lvl 5, Rm 520: Please replace flickering light. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 22 Aug 2018 | 2018-08-29 17:00:00 | 2018-08-24 18:00:00 | Pass | light changed out
MSA-MRWA | WA1695417 | Lvl 6, Male Bathroom: right hand urinal is overflowing – slowly onto the floor | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Drainage (PD) | MR - Handyperson - PFM | 2 | CLOSE | 22 Aug 2018 | 2018-08-27 17:00:00 | 2018-08-22 14:04:00 | Pass | Plumber assigned to rct as unable to unblock
MSA-MRWA | WA1695470 | Lvl 1, Female Bathroom: Replace 3x shower heads to ladies showers that have bad corrosion. | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Materials (PD) | MR - Handyperson - PFM | 3 | CLOSE | 22 Aug 2018 | 2018-08-29 17:00:00 | 2018-09-05 13:25:00 | Fail | Parts arrived and shower heads removed and fitted with new ones
MSA-MRWA | WA1695475 | Level 4 - 480 The drawer to the cupboard needs the brackets tighten as they have come loose. | Don Aitken Centre MRWA Head Office | GMP-BR | Furniture | Domestic Furniture (FU) | MR - Handyperson - PFM | 3 | CLOSE | 22 Aug 2018 | 2018-08-29 17:00:00 | 2018-08-22 12:05:00 | Pass | Re fitted rails on each drawers with new screws
MSA-MRWA | WA1695476 | Lvl 7: many lights out/failed throughout level 7, please rectify | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 22 Aug 2018 | 2018-08-29 17:00:00 | 2018-08-24 18:18:00 | Pass | Lights changed out
MSA-MRWA | WA1695498 | Lvl 7: Power conduit and section of Partition has come loose please rectify. | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 3 | CLOSE | 22 Aug 2018 | 2018-08-29 17:00:00 | 2018-10-11 10:50:00 | Fail | Complete
MSA-MRWA | WA1696607 | Ground Floor, Records Area - flickering light | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 24 Aug 2018 | 2018-08-27 17:00:00 | 2018-08-24 09:50:00 | Pass | Removed flickering light and replaced with new. Back in working order
MSA-DTAG | WA1765332 | ** Invoice Purpose Only - Do NOT Attend ** Retrospective PO: Ref 41234 | Central Law Courts | GMP-BR-HO | ICT/Audiovisual | Maintenance (AV) | Icon Logic Pty Ltd | 3 | CLOSE | 04 Sep 2018 | 2018-09-10 17:00:00 | 2018-09-05 14:00:00 | Pass | Field complete
MSA-DTAG | WA1765336 | ** Invoice Purpose Only - Do NOT Attend ** Retrospective PO: Ref 41236 | Central Law Courts | GMP-BR-HO | ICT/Audiovisual | Maintenance (AV) | Icon Logic Pty Ltd | 3 | CLOSE | 05 Sep 2018 | 2018-09-11 17:00:00 | 2018-09-06 16:00:00 | Pass | Field complete
MSA-DCS | WA1782450 | ** Invoice Purpose Only - Do NOT Attend ** Retrospective PO: Dairy Unit Genset Investigation Works | Karnet Prison Farm | GMP-BR- HO | Electrical | Generator Systems (EL) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 3 | CLOSE | 24 Sep 2018 | 2018-10-01 17:00:00 | 2018-10-16 13:00:00 | Fail | Job completed Actual completion dates & times 20.08.2018 - 0700 - 1300
MSA-DTAG | WA1765343 | ** Invoice Purpose Only - Do NOT Attend ** Retrospective PO: Ref 41266 | Central Law Courts | GMP-BR-HO | ICT/Audiovisual | Maintenance (AV) | Icon Logic Pty Ltd | 2 | CLOSE | 25 Sep 2018 | 2018-09-27 17:00:00 | 2018-09-26 11:30:00 | Pass | Field complete
MSA-DCS | WA1751667 | Store area - Boom gate not working. Cars are stuck in | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 30 Sep 2018 | 2018-09-30 17:11:37 | 2018-09-30 15:00:00 | Pass | COMPLETED
MSA-DCS | WA1759982 | SHU, Control Room: Camera/monitor surveillance issues as per below notes: | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Oct 2018 | 2018-10-04 14:45:53 | 2018-10-04 15:00:00 | Fail | Attended SHU, found multiple monitors and cameras offline, traced issue to power cable removed when moving desk by staff, restored and brought back online, functioning correctly.
MSA-DCA | WA1928518 | INVOICING PURPOSE ONLY-Lift fault-Ref 46344347 | Collection and Research Centre Welshpool | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 11 Oct 2018 | 2018-10-11 17:00:00 | 2018-10-11 08:00:00 | Pass | COMPLETED
MSA-DCS | WA1813963 | Unit 2 control windows-front window not sliding correctly and 2 x side windows need locking bolt | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 30 Oct 2018 | 2018-11-06 17:00:00 | 2018-11-02 10:00:00 | Pass | job completed as per email from contractor
MSA-DTAG | WA2779196 | L1 Not Reponding - Retrospective Work Order - Do not re-attend | Midland Courthouse | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 30 Nov 2018 | 2018-12-03 17:00:00 | 2018-11-30 14:45:00 | Pass | Lift switched on security on G Floor landing so will not acccept landing calls,switched security off, tested and left in norma service. Switched by someone during power issues on the 29/11
MSA-DTAG | WA3335484 | Lift #1 not responding - retrospective work order - refer invoice 4688126217 | Midland Courthouse | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 30 Nov 2018 | 2018-11-30 17:00:00 | 2018-11-30 14:45:00 | Pass | Damage to the non-lift /escalator components caused by misue or improper use. Charges apply
MSA-DCS | WA1903400 | Back of Admin: Bee hive within CCTV camera pole - please remove | Melaleuca Prison | GMP-BR- HO | Pest Control | Specialist Pest (PC) | High Tech Pest Control | 3 | CLOSE | 06 Dec 2018 | 2018-12-13 17:00:00 | 2018-12-19 10:40:00 | Fail | COMPFIN at $0 PFM Mario to progress bee removal.
MSA-MRWA | WA1922898 | Level 8- RM 814- Flickering light outside of our office | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 07 Dec 2018 | 2018-12-12 17:00:00 | 2018-12-07 15:05:00 | Pass | Light in hall way replaced
MSA-MRWA | WA1923787 | Ground Floor West- HR- G19- Flickering light – can it please be replaced | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 10 Dec 2018 | 2018-12-13 17:00:00 | 2018-12-10 10:35:00 | Pass | Replaced flashing light with new, left in working order
MSA-MRWA | WA1924319 | Level 7- Female toilets- hand soap dispenser has come off the wall | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 2 | CLOSE | 10 Dec 2018 | 2018-12-13 17:00:00 | 2018-12-11 11:00:00 | Pass | Replaced tape and re fitted to the mirror in same location
MSA-DCS | WA2016859 | Unit 8- paint store floor- water damaged water underneath | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 01 Feb 2019 | 2019-02-05 17:00:00 | 2020-06-04 12:01:00 | Fail | Programmed requested we close off with costs to date 4/6/20
MSA-DFES | WA2720388 | Appliance Bay #1 door not operational-Vendor. For invoice purposes only-See Notes | CFRS Belmont | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 08 Feb 2019 | 2019-02-08 19:49:00 | 2019-02-28 13:45:00 | Fail | Works completed - this work order relates to WA2023691 already completed without full costs
MSA-DTWD | WA2077077 | Fire shed in carpark, fuel indicator gauge is faulty-Fire safe have taken photo's | Murdoch Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 1 | CLOSE | 26 Feb 2019 | 2019-02-27 17:00:00 | 2019-02-27 13:30:00 | Pass | Site: South Metro Tafe - MurdochWork Order #: WA2077077Original information: Fire shed in car park, fuel indicator gauge is faulty-Fire safe have taken photo'sDarren Cusack (27/02/2019) - Work NoteDate:29/2/19Start Time:12:45Finish Time:13:30Techs on Site: DarrenWorks Carried Out: Replaced faulty fuel sensor on diesel pump Materials and Equipment Used:1 x fuel sensor & conversion kit.System Status on Departure: Normal
MSA-MRWA | WA2088544 | Remediate failed Exit light by Western Fire Stairwell | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 06 Mar 2019 | 2019-03-13 17:00:00 | 2019-03-13 10:23:00 | Pass | Replaced blown exit light outside west stairwell on ground floor
MSA-MRWA | WA2092856 | Level 9 Passageway - please refit the ceiling tile near fire cupboard that has been displodged | Don Aitken Centre MRWA Head Office | GMP-BR | Carpentry | Materials (CA) | MR - Handyperson - PFM | 2 | CLOSE | 11 Mar 2019 | 2019-03-14 17:00:00 | 2019-03-11 15:50:00 | Pass | Moved panel into a better position
MSA-DCS | WA2095710 | Reception- shade sail damaged outside sallyport | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Mar 2019 | 2019-03-20 17:00:00 | 2020-05-13 14:07:00 | Fail | The shade sail will be replaced on a new work order
MSA-DTWD | WA3491756 | RETROSPECTIVE WORK ORDER-B1 lift motor rooms, Schindler to meet David Gaff Sat 23/3 at 5pm | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 22 Mar 2019 | 2019-03-25 17:00:00 | 2019-03-23 21:00:00 | Pass | Work completed refer WA2138569
MSA-MRWA | WA2141250 | Lvl 2: Replace lights: Male toilet, office 227 and 237 and east end print room. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 26 Mar 2019 | 2019-04-02 17:00:00 | 2019-05-16 13:10:00 | Fail | toilet lighting has been replaced and the other level 2 lights are LED panels and would require electricians
MSA-MRWA | WA2162405 | Ground Floor- Men's toilet has a blockage | Heavy Vehicle Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | MR - Handyperson - PFM | 1 | COMP | 09 Apr 2019 | 2019-04-10 17:00:00 | 2019-04-09 10:00:00 | Pass | Unblocked toilet. had a great time.
MSA-MRWA | WA2162824 | Basement male change room, Light out. Please remediate to working order | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 09 Apr 2019 | 2019-04-10 17:00:00 | 2019-04-09 15:30:00 | Pass | Replaced tubes with new
MSA-MRWA | WA2164762 | Ground Floor, Female toilets- light out | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 10 Apr 2019 | 2019-04-15 17:00:00 | 2019-04-10 15:01:00 | Pass | Replaced two tubes and starters in the ladies toilets
MSA-MRWA | WA2164769 | Ground Floor, Kitchenette- light out | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 10 Apr 2019 | 2019-04-15 17:00:00 | 2019-04-10 14:45:00 | Pass | Replaced dead globes in one of the diffusers in the kitchen
MSA-MRWA | WA2165411 | Lvl G, Mens Toilet: Toilet seat has fallen off please fix. | Jandakot Depot | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | MR - Handyperson - PFM | 2 | COMP | 11 Apr 2019 | 2019-04-16 17:00:00 | 2019-04-16 10:15:00 | Pass | The bolt had come loose and fell out of place loosening the seat. Refitted the bolt and rod that hold s seat in place
MSA-MRWA | WA2166801 | L5 MFD- Please replace lights and remediate to working order | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 12 Apr 2019 | 2019-04-15 17:00:00 | 2019-04-12 11:00:00 | Pass | Replaced flickering lights above the printer area
MSA-MRWA | WA2166805 | L8 8.15 Please replace and remediate to working order | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 12 Apr 2019 | 2019-04-15 17:00:00 | 2019-04-12 11:40:00 | Pass | Replaced lights above occupants desk
MSA-MRWA | WA2179529 | Level 7 7.45-Please replace light and remediate to working order | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 15 Apr 2019 | 2019-04-18 17:00:00 | 2019-04-17 15:00:00 | Pass | Replaced light to working order
MSA-DCS | WA2206342 | BR-U8: Lost TV signal to whole unit. | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Apr 2019 | 2019-04-20 09:19:49 | 2019-04-19 10:15:00 | Pass | Job attended
MSA-MRWA | WA2208131 | Control Rm, Lvl 1: Adjust control room door to close without jamming. | Traffic Operations Centre | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 3 | CLOSE | 23 Apr 2019 | 2019-05-01 17:00:00 | 2019-05-22 13:25:00 | Fail | Job will be passed on to a trade who can supply and install correct parts
MSA-MRWA | WA2211009 | Lvl 1, First Aid Room: Flickering light, please replace light tube. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 26 Apr 2019 | 2019-05-01 17:00:00 | 2019-04-29 10:20:00 | Pass | Replaced flickering light with new tube, back in working order
MSA-DCA | WA2219893 | eastern work room ajacent boardroom, electronic stricker fail to open | State Library of WA-Main Building-Level 3-3.9 - Board Room | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 01 May 2019 | 2019-05-02 17:00:00 | 2019-05-02 16:00:00 | Pass | Electronic strike was replacedJob is not going to have a claim from Assa due to a paperwork issue Has been close on our endNote by Joe Dowling
MSA-MRWA | WA2220473 | Level 7, 731- Light out please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 01 May 2019 | 2019-05-02 17:00:00 | 2019-05-02 13:30:00 | Pass | Replaced blown light with new
MSA-MRWA | WA2220531 | Level 7, 721- Light out please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 01 May 2019 | 2019-05-02 17:00:00 | 2019-05-02 13:20:00 | Pass | Replaced blown light with new
MSA-MRWA | WA2220544 | Level 7, 720- Light out please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 01 May 2019 | 2019-05-02 17:00:00 | 2019-05-02 13:10:00 | Pass | Replaced blown light with new
MSA-DCS | WA2223252 | Unit 6, Cell B9- window not closing properly | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 May 2019 | 2019-05-10 17:00:00 | 2020-05-11 12:00:00 | Fail | RECONDITIONED VENT FITTED
MSA-MRWA | WA2223358 | Lvl 1, North West end near window- Light flickering please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 03 May 2019 | 2019-05-06 17:00:00 | 2019-05-03 09:45:00 | Pass | Replaced flickering light with new
MSA-MRWA | WA2223720 | Lvl 2, RM 124- Adjust monitor height – desk occupant Luke Morgan | Road Network Operation Centre (RNOC) | GMP-BR | Furniture | Office Furniture (FU) | MR - Handyperson - PFM | 2 | CLOSE | 03 May 2019 | 2019-05-08 17:00:00 | 2019-05-07 10:12:00 | Pass | No issue just had to move arm slightly
MSA-MRWA | WA2225144 | Lvl 5, IT area: Various lights out please attend and remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 06 May 2019 | 2019-05-07 17:00:00 | 2019-05-07 13:30:00 | Pass | Replaced 4 lights in the IT area
MSA-MRWA | WA2228573 | Level 2, East Print Area- lights out | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 09 May 2019 | 2019-05-14 17:00:00 | 2019-05-10 13:14:00 | Pass | This was handed over to a trade
MSA-DTWD | WA2232937 | S Block, Rm S6 - Flume cupboard solenoid keeps tripping power, reset does not work. | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | SW HART & CO | 2 | CLOSE | 13 May 2019 | 2019-05-16 17:00:00 | 2019-06-05 07:00:00 | Fail | reinstalled repaired panel
MSA-MRWA | WA2233055 | Level 8, Room 802- reinstall fluro tubes to fittings | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | COMP | 13 May 2019 | 2019-05-16 17:00:00 | 2019-05-14 11:00:00 | Pass | Refitted globes I had previously removed
MSA-MRWA | WA2233068 | Lvl 7: Please replace emergency exit globes near photocopier and room 746. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | MR - Handyperson - PFM | 1 | CLOSE | 13 May 2019 | 2019-05-14 17:00:00 | 2019-05-15 15:25:00 | Fail | Replaced blown tube with new
MSA-MRWA | WA2248173 | Ground Floor, G08- flickering light | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 16 May 2019 | 2019-05-17 17:00:00 | 2019-05-16 13:22:00 | Pass | Replaced light
MSA-MRWA | WA2248242 | L8 Executive Kitchen-Flickering light please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 16 May 2019 | 2019-05-17 17:00:00 | 2019-05-16 11:04:00 | Pass | Replaced flickering light with new tube retuned to working order
MSA-MRWA | WA2248371 | L8 corridor-Light out nearest room 803 | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 16 May 2019 | 2019-05-17 17:00:00 | 2019-05-17 13:30:00 | Pass | Replaced old globe with new
MSA-DTWD | WA3285642 | RETROSPECTIVE WORK ORDER-Donot attend-doors opening and closing | Bentley Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 3 | CLOSE | 21 May 2019 | 2019-05-27 17:00:00 | 2019-05-27 08:15:00 | Pass | Retrospective work order
MSA-MRWA | WA2273551 | L6 CIC-Fix broken lock to cupboard, CIC have labelled the cupboard that needs to be fixed | Don Aitken Centre MRWA Head Office | GMP-BR | Security | Locksmith (SE) | MR - Handyperson - PFM | 2 | CLOSE | 22 May 2019 | 2019-05-27 17:00:00 | 2019-05-23 14:40:00 | Pass | The hook on the inside of the cupboard had fallen off re fitted the hook and left in working order
MSA-MRWA | WA2273774 | G Floor, information services- G24- Remove fluro above Lorraine Wood | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 22 May 2019 | 2019-05-27 17:00:00 | 2019-05-23 15:00:00 | Pass | Removed globe above the desk as requested
MSA-MRWA | WA2273842 | L7 male toilet-Right Hand urinal blocked. Please unblock, isolate and put up “out of Service”sign up | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | MR - Handyperson - PFM | 1 | CLOSE | 22 May 2019 | 2019-05-23 17:00:00 | 2019-05-22 15:01:00 | Pass | Checked and cleared drain but the issue seems to be a flow problem possibly flow switch/solenoid stuck open or sensor faulty. Will have to arrange the relevant trade to attend
MSA-MRWA | WA2274464 | L6 male toilet-Urinal Flooding. Attach sign above urinal, Isolate and unblock. | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | MR - Handyperson - PFM | 1 | CLOSE | 23 May 2019 | 2019-05-24 17:00:00 | 2019-05-23 10:45:00 | Pass | Urinal drain had build up inside. Cleared and returned to working order
MSA-MRWA | WA2274499 | Lvl 6, Kitchenette- Replace blown lights & remove sticky tape hanging from ceiling in lift lobby | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | COMP | 23 May 2019 | 2019-05-30 17:00:00 | 2019-05-23 15:30:00 | Pass | Replaced globes in kitchen and removed tape from foyer area
MSA-MRWA | WA2274667 | ground office-3 x window blinds have damaged slats – please fix/report | Office and Warehouse-Malaga | GMP-BR | Building | Windows (BU) | MR - Handyperson - PFM | 3 | COMP | 23 May 2019 | 2019-05-30 17:00:00 | 2019-05-30 09:45:00 | Pass | Two blinds missing and one bracket was broken
MSA-MRWA | WA2274669 | office ground-Side door from the yard into office is hard to lock. | Office and Warehouse-Malaga | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 3 | COMP | 23 May 2019 | 2019-05-30 17:00:00 | 2019-05-30 10:00:00 | Pass | Door has a big split down the side and frame seems to be starting to deteriorate would most likely need to be replaced
MSA-MRWA | WA2276540 | Lvl G, Compactus East End: Flashing light over compactus, please remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 24 May 2019 | 2019-05-27 17:00:00 | 2019-05-24 15:00:00 | Pass | Attended job but could not change light as the compactus is too narrow for the ladder to fit in between
MSA-MRWA | WA2278048 | ground garage-Multiple lights not working please remediate | Traffic Operations Centre | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 27 May 2019 | 2019-06-04 17:00:00 | 2019-06-03 10:20:00 | Pass | Attended and job was outside of my scope and had not realised a job had been raised for me
MSA-MRWA | WA2279012 | Lvl 7, Female Toilets: Faulty lock on cubicle, please remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 1 | CLOSE | 28 May 2019 | 2019-05-29 17:00:00 | 2019-05-29 10:15:00 | Pass | Door had dropped slightly so lock was misaligned and the gears inside wore away
MSA-MRWA | WA2289654 | Lvl 1,Property Management Branch- Investigate and remediate non working fluro lights | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 07 Jun 2019 | 2019-06-14 17:00:00 | 2019-06-14 15:30:00 | Pass | Replaced lights
MSA-DCS | WA2291647 | Unit 6 Repair/replace shade cloth | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Jun 2019 | 2019-06-17 17:00:00 | 2020-07-15 12:30:00 | Fail | PROMAP ADVISED TO CLOSE OFF JOB AND COST TO DATE
MSA-DTAG | WA2292324 | Jury room for Court 37, Male toilet-constantly flushing | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Jun 2019 | 2019-06-14 17:00:00 | 2019-06-11 16:24:00 | Pass | Job doubled with wa2292595
MSA-MRWA | WA2292341 | Lvl 8, RM 814- Fluro lights are out over desk please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 11 Jun 2019 | 2019-06-12 17:00:00 | 2019-06-12 11:00:00 | Pass | Changed lights replaced with new
MSA-MRWA | WA2293735 | Ground, Near photocopier- flashing light | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 12 Jun 2019 | 2019-06-13 17:00:00 | 2019-06-13 11:30:00 | Pass | Replaced lights with new
MSA-MRWA | WA2293954 | L5 south east-Exit light out please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 12 Jun 2019 | 2019-06-13 17:00:00 | 2019-06-13 14:45:00 | Pass | Replaced globes with new
MSA-MRWA | WA2295577 | Level 7, various areas- Repair fabric on partition RM715 and RM714 | Don Aitken Centre MRWA Head Office | GMP-BR | Furniture | Office Furniture (FU) | MR - Handyperson - PFM | 3 | COMP | 13 Jun 2019 | 2019-06-20 17:00:00 | 2019-06-28 11:00:00 | Fail | Reglued fabric to partitions
MSA-MRWA | WA2295578 | L7 outside male toilets-Light flickering please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 13 Jun 2019 | 2019-06-14 17:00:00 | 2019-06-14 15:46:00 | Pass | Replace light
MSA-MRWA | WA2295579 | L7 RM717-Light flickering please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 13 Jun 2019 | 2019-06-14 17:00:00 | 2019-06-14 14:30:00 | Pass | Replace light
MSA-MRWA | WA2301082 | L7 RM 721-Please remediate fluro light | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 14 Jun 2019 | 2019-06-17 17:00:00 | 2019-06-17 11:30:00 | Pass | Replaced globe with new
MSA-MRWA | WA2301337 | Lvl 8, RM 802- Fluro light please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 14 Jun 2019 | 2019-06-19 17:00:00 | 2019-06-17 13:30:00 | Pass | Replaced tube with new
MSA-DCS | WA2339251 | Officers gym- carpet needs repairing | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jun 2019 | 2019-07-04 17:00:00 | 2020-01-20 10:30:00 | Fail | located and rectified leak, checked carpet, all ok.
MSA-DCA | WA2342386 | State Theatre Centre (Heath Ledger Theatre)- Lift in green room not working | State Theatre Centre (Heath Ledger Theatre) | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 30 Jun 2019 | 2019-06-30 12:00:21 | 2019-06-30 14:30:00 | Fail | COMP at no charge
MSA-DCS | WA2345034 | Unit 1 Cell C11-toilet is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | COMP | 01 Jul 2019 | 2019-07-04 17:00:00 | 2019-07-08 07:44:00 | Fail | Completed though a P1 close out at $0
MSA-DTAG | WA2345853 | Lvl 1, DPP main office: The carpet needs to be dried and removed where it is mouldy under a cabinet. | Perth Children's Court | GMP-BR-HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 01 Jul 2019 | 2019-07-02 17:00:00 | 2020-05-15 11:02:00 | Fail | We have removed the damaged carpet tiles, they are a discontinued colour/pattern which can not be matched. The section is under a cabinet.
MSA-DCA | WA2348257 | Passenger lift has stopped and is stuck on Lvl 1. See notes below: | Swan Bell Tower-Main Building-Ground Floor - LOBBY G1 | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 02 Jul 2019 | 2019-07-03 17:00:00 | 2019-07-03 01:40:00 | Pass | 0075 FAULT, REPLACE 61U AND 61N SWITCHES, CONFIRMOPERATION, MONITOR OPERATION AND RETURN TO SERVICE Equipment running, back to normal operation
MSA-MRWA | WA2347491 | Ground, East end- flashing light near mail area | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 02 Jul 2019 | 2019-07-03 17:00:00 | 2019-07-02 11:35:00 | Pass | Replaced flashing lights with new tubes
MSA-DFES | WA2351528 | Vehicle contact security gate- gate not running on track due to minor damage | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 03 Jul 2019 | 2019-07-04 17:00:00 | 2019-07-04 16:45:00 | Pass | Job completed -
MSA-DCS | WA2354677 | Gascoyne, Living room- Gas heater non operational | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | COMP | 08 Jul 2019 | 2019-07-11 17:00:00 | 2019-08-13 16:30:00 | Fail | Job is a duplicate, works claimed under WA2339345 Close out at $0
MSA-DCA | WA2358106 | Lift stuck on Lvl 6. Please attend Thu 11/07 before 10am. Contact 0434 517 903: | Swan Bell Tower-Main Building-Level 6 - LOBBY | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 10 Jul 2019 | 2019-07-11 17:00:00 | 2019-07-11 14:10:00 | Pass | Report - ERROR 0007, SOURCE REPLACE 30 CIGAR SW, TESTED OK, LEFT, LIFT IN SERVICE Condition on Leaving - Equipment running, back to normal operation
MSA-DCA | WA2371928 | lift has stopped on L6 then dropped and shuddered-has accured 3 times on the weekend | Swan Bell Tower-Main Building-Ground Floor - LOBBY G1 | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 15 Jul 2019 | 2019-07-16 17:00:00 | 2019-07-15 15:29:00 | Pass | LIFT OPERATING ON ARRIVAL, 0108, 0101 & 0026 FAULTS,CHECKED ENCODER, CHECKED CAR SLIDES, ORDERED NEW CAR SLIDES, RETURNED TO SERVICE- Equipment running, back to normal operation
MSA-DCS | WA2372242 | Unit 11, Cell C2- shower screen is leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Jul 2019 | 2019-07-16 11:45:11 | 2019-07-17 17:43:00 | Fail | New order number allocated to Midolo contractor, no charge
MSA-DTWD | WA2371781 | A block L2-Repair Fume Hoods A310 and A318 not operating | East Perth Campus | GMP-BR | Equipment Hire | Equipment / Vehicles With Operator (EH) | SW HART & CO | 3 | CLOSE | 15 Jul 2019 | 2019-07-19 17:00:00 | 2019-09-25 11:30:00 | Fail | INVOICED ON 118082
MSA-DCS | WA2402942 | Unit 5, D2- Grille on cell window has been tampered with & needs repair. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 Jul 2019 | 2019-07-26 17:00:00 | 2020-05-11 14:30:00 | Fail | RE CONDITIONED VENT INSTALLED
MSA-DTAG | WA2403390 | Magistrate chambers 1 leak coming through the roof-Please attend Monday | Armadale Courthouse | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 Jul 2019 | 2019-07-24 17:00:00 | 2020-05-05 16:58:00 | Fail | located leak and rectified
MSA-MRWA | WA2404699 | Lvl 2, Desk 148- Adjust monitor arms as per staff members requirements | Road Network Operation Centre (RNOC) | GMP-BR | Security | Monitoring (SE) | MR - Handyperson - PFM | 2 | CLOSE | 22 Jul 2019 | 2019-07-25 17:00:00 | 2019-07-25 11:45:00 | Pass | Removed top two screens and lifted bottom screens to users request
MSA-DCS | WA2408819 | Obs Post 5: Repair/replace vinyl floor. | Hakea Prison | SPA-GR | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 24 Jul 2019 | 2019-07-31 17:00:00 | 2020-05-28 09:55:00 | Fail | replaced the vinyl
MSA-MRWA | WA2408774 | Lvl 2, North Plantroom: Repair door handle on ATS switchboard. Notes below: | Road Network Operation Centre (RNOC) | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 3 | CLOSE | 24 Jul 2019 | 2019-07-31 17:00:00 | 2019-07-30 14:52:00 | Pass | Denied access on site FM said his handyman will remedy issue
MSA-MRWA | WA2413053 | Lvl 3, Kitchenette- replace fluro tube in kitchenette | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 29 Jul 2019 | 2019-07-30 17:00:00 | 2019-07-29 11:00:00 | Pass | Replaced lights with new globes in kitchen
MSA-MRWA | WA2413304 | Various lights out: Replace all flicking/blown on Lvl G& Reception: | Heavy Vehicle Services | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 29 Jul 2019 | 2019-08-05 17:00:00 | 2019-07-31 15:30:00 | Pass | Changed reported lights and conducted walkthrough and changed extra lights found to be out
MSA-DCS | WA2414974 | Unit 7: Front glass doors: Frame and doors damaged. | Hakea Prison | SPA-BR | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Jul 2019 | 2019-08-02 17:00:00 | 2020-07-15 09:15:00 | Fail | FRONT DOORS REPLACED
MSA-MRWA | WA2414630 | L7 747 blown light please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 30 Jul 2019 | 2019-07-31 17:00:00 | 2019-07-30 11:52:00 | Pass | Removed light and found the tombstone was broken reported to be replaced
MSA-MRWA | WA2414639 | L7 725 Flickering light please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 30 Jul 2019 | 2019-07-31 17:00:00 | 2019-07-30 11:45:00 | Pass | Replaced flickering light with new tube
MSA-MRWA | WA2416405 | Lvl G, Rm G11: Flickering overhead light. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 31 Jul 2019 | 2019-08-05 17:00:00 | 2019-08-01 11:26:00 | Pass | Removed flashing light and replaced with new. Left in working order
MSA-MRWA | WA2418484 | Disable Toilet - Northern End: Metal cover of door lock - fallen off. Notes below: | Road Network Operation Centre (RNOC) | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 3 | CLOSE | 31 Jul 2019 | 2019-08-07 17:00:00 | 2019-08-05 12:20:00 | Pass | Replaced cover on disabled toilet lock
MSA-MRWA | WA2420212 | L3 male toilet Please arrange to unblock toilet level 3 men’s. | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 2 | CLOSE | 31 Jul 2019 | 2019-08-05 17:00:00 | 2019-08-01 10:50:00 | Pass | Failure on job says doors? Request was for a blockage but original report was for flowing water? Attended and found no issues
MSA-MRWA | WA2423592 | Level 7, cubicle 718-Description: fasten material back to partition. | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Internal Screens (BU) | MR - Handyperson - PFM | 1 | CLOSE | 01 Aug 2019 | 2019-08-01 17:00:00 | 2019-08-01 16:56:00 | Pass | Cleaned and restuck fabric to partition
MSA-MRWA | WA2423767 | L5 female toilet-metal cover of the soap dispenser as it has dislodged-see notes | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Materials (PD) | MR - Handyperson - PFM | 2 | CLOSE | 01 Aug 2019 | 2019-08-06 17:00:00 | 2019-08-01 09:55:00 | Pass | Attempted to reinstate but piece it too worn to be held in place and unable to screw due to the moving parts of the dispenser. Piece was removed as it does not affect function of Despenser
MSA-DTWD | WA2428178 | Lift 7- panel has come off inside of lift | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 02 Aug 2019 | 2019-08-07 17:00:00 | 2019-08-13 08:00:00 | Fail | No completion notes
MSA-MRWA | WA2427509 | Basement Car Park: A ceiling light out in Executive & several out in Main. Notes below: | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 02 Aug 2019 | 2019-08-07 17:00:00 | 2019-08-02 15:54:00 | Pass | Replaced various blown lights
MSA-DFES | WA2428555 | Front roller door in engine bay not working- no power | DO NOT USE - TO BE DECOMMISSIONED VFRS Mandurah-Main Building-Ground Floor | GMP-BR | Electrical | General Electrical (EL) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 04 Aug 2019 | 2019-08-05 17:00:00 | 2019-08-09 12:00:00 | Fail | No completion notes
MSA-DCS | WA2430287 | BR- Unit 9 A & B wing day room PA not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Aug 2019 | 2019-08-07 08:16:12 | 2020-06-03 13:00:00 | Fail | Run new cable for Unit 9 A and B wing and replaced faulty speaker. Test unit 9 PA ,ok and back to normal operations. Job completed.
MSA-MRWA | WA2432476 | Near 8.27 Faulty light, please remediate | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 08 Aug 2019 | 2019-08-09 17:00:00 | 2019-08-08 14:00:00 | Pass | Replaced flashing light with new tube
MSA-MRWA | WA2432739 | Near 7.39 Please remove light above desk. John Moran is the occupant | Don Aitken Centre MRWA Head Office-Main Building-Seventh Floor | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 08 Aug 2019 | 2019-08-09 17:00:00 | 2019-08-09 10:56:00 | Pass | Removed light above occupants desk
MSA-DTWD | WA2439511 | E-Block SK2, room E72- proving cabinet door seal needs repair | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 12 Aug 2019 | 2019-08-15 17:00:00 | 2019-08-13 13:28:00 | Pass | job completed - door seal replaced
MSA-DCS | WA2441198 | Unit 9, C Wing Showers- broken tiles | Hakea Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 13 Aug 2019 | 2019-08-16 17:00:00 | 2020-06-04 12:04:00 | Fail | Programmed requested we close off with costs to date
MSA-DCS | WA2441259 | Unit 11, Cell A11- Vinyl is lifting | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Aug 2019 | 2019-08-20 17:00:00 | 2020-06-03 10:45:00 | Fail | re-siliconed all joints in cell
MSA-DTAG | WA2440839 | L1 pump room-Jockey pump alarm has been activated | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 13 Aug 2019 | 2019-08-14 17:00:00 | 2019-08-14 10:15:00 | Pass | Attended site, no evidence of any issue or activation, all okay on departure
MSA-MRWA | WA2446906 | Lvl 7, 7.24- flickering light please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 14 Aug 2019 | 2019-08-15 17:00:00 | 2019-08-15 09:00:00 | Pass | Replaced flickering light with new tube
MSA-DCS | WA2464720 | Removal of obsolete and second hand equipment | Hakea Prison | GMP-BR- HO | Equipment | Security Equipment (EQ) | Seme Solutions Pty Ltd | 3 | CLOSE | 16 Aug 2019 | 2019-08-23 17:00:00 | 2020-03-10 11:12:00 | Fail | Job complete
MSA-MRWA | WA2464559 | L2 Please perform and air quality floor sample-Contact Brendan Mitchell prior to attendance | Road Network Operation Centre (RNOC) | GMP-BR | Flooring | Concrete (FL) | Environmental Site Services | 3 | CLOSE | 16 Aug 2019 | 2019-08-23 17:00:00 | 2019-08-20 10:00:00 | Pass | Indoor air quality & Voc monitoring
MSA-MRWA | WA2464717 | Walkway near 7.30- Flickering exit light please remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | MR - Handyperson - PFM | 1 | CLOSE | 16 Aug 2019 | 2019-08-19 17:00:00 | 2019-08-26 10:22:00 | Fail | Replaced blown exit light with new tube
MSA-DCS | WA2499179 | In between SHU & MPU Camera C161 is faulty, low level video, screen is black | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Aug 2019 | 2019-08-28 17:00:00 | 2020-02-10 15:30:00 | Fail | Cameras 160 & 161, both showing same symptoms. Attempted to reprogram decoders, not successful. Recieved two replacement decoders, programmed new decoders in Gatehouse Equipment room, confirmed composite video output. Relocated new decoders to SHU Equipment alcove. Confirmed video vision from the IOU Link now visible in Gate Control.
MSA-MRWA | WA2500476 | ground reception-Please replace blown lights | Heavy Vehicle Services | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 22 Aug 2019 | 2019-08-27 17:00:00 | 2019-08-22 15:05:00 | Pass | Job completed before order was raised on the same day
MSA-MRWA | WA2501062 | L4 kitchenette-Please replace blown lights | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 23 Aug 2019 | 2019-08-28 17:00:00 | 2019-08-26 10:24:00 | Pass | Replaced blown lights
MSA-MRWA | WA2509823 | Soils & Concrete - Roof Leak – email sent to Handyman separately. | Materials Engineering Branch | GMP-BR | Roofing | Tiled Roofing (RF) | MR - Handyperson - PFM | 3 | CLOSE | 29 Aug 2019 | 2019-09-05 17:00:00 | 2019-09-05 15:36:00 | Pass | Believe this has been attended to previously
MSA-MRWA | WA2511167 | ground Old training Labs Metal stake to be removed | Materials Engineering Branch | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 3 | CLOSE | 30 Aug 2019 | 2019-09-06 17:00:00 | 2019-09-05 15:30:00 | Pass | Removed stake from ground
MSA-MRWA | WA2511352 | Lvl 8 North East Side- Ceiling tile to be replaced | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Ceiling (BU) | MR - Handyperson - PFM | 3 | CLOSE | 30 Aug 2019 | 2019-09-06 17:00:00 | 2019-09-02 12:53:00 | Pass | Readjusted drip tray and replaced wet ceiling tiles
MSA-MRWA | WA2514571 | L7 7.47 Please remove light over desk | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 02 Sep 2019 | 2019-09-03 17:00:00 | 2019-09-03 14:52:00 | Pass | Removed light above desk
MSA-DCS | WA2521469 | BR-Unit 3 D8 and C9 cell call system loud buzzing sound | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Sep 2019 | 2019-09-10 09:30:35 | 2019-10-04 14:45:00 | Fail | Replaced U3 D8 cell call point. Tested it ok after replacement. CI-CC/270/120 Refurb one X 1
MSA-DCS | WA2521709 | Unit 2. Lower landing showers floor titles loose and moving. | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Sep 2019 | 2019-09-16 17:00:00 | 2020-05-15 12:46:00 | Fail | To be completed on LVM WA3308468
MSA-DTWD | WA2840202 | Invoice purpose only for extra cost ref WA2521280-T block compressor not starting | Munster Campus (ACEPT) | GMP-BR | Equipment Hire | Compressors, Generators (EH) | Nessco Pressure Systems | 0 | CLOSE | 09 Sep 2019 | 2019-09-09 12:00:00 | 2019-09-11 12:30:00 | Fail | Job completed - Asess Air compressor fault & qoute
MSA-MRWA | WA2521352 | basement bike store-Lights out, replace as required. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 09 Sep 2019 | 2019-09-16 17:00:00 | 2019-09-16 16:08:00 | Pass | Replaced lights in basement
MSA-DCS | WA2526879 | nth west perimeter construction site duress transponder-TR-18 indicating no respons on PDA monitor | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Sep 2019 | 2019-09-17 17:00:00 | 2020-05-04 13:53:00 | Fail | Works related to ongoing project by others - No further works by SEME
MSA-MRWA | WA2576719 | Level 7, Room 7.23- flickering light please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 19 Sep 2019 | 2019-09-20 17:00:00 | 2019-09-19 10:00:00 | Pass | Replaced tubecwith new
MSA-MRWA | WA2576728 | Level 3, Kitchenette, lights out | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 19 Sep 2019 | 2019-09-20 17:00:00 | 2019-09-19 10:14:00 | Pass | Replaced with two new globes
MSA-MRWA | WA2576736 | Level 4, 4.32 - Move cabinet from 4.32 to 4.76 | Don Aitken Centre MRWA Head Office | GMP-BR | Furniture | Office Furniture (FU) | MR - Handyperson - PFM | 1 | CLOSE | 19 Sep 2019 | 2019-09-20 17:00:00 | 2019-09-19 10:43:00 | Pass | Moved cupboard to new location
MSA-MRWA | WA2576763 | Ground, Disabled toilet - Repair toilet seat | Jandakot Depot | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | MR - Handyperson - PFM | 3 | CLOSE | 19 Sep 2019 | 2019-09-26 17:00:00 | 2019-09-25 12:15:00 | Pass | Issues with Promap mobile application not updating completion/notes PFM superuser finalised and closed job out.
MSA-DCS | WA2584564 | Gatehouse, Control Room - Duress alarm transponder is faulty. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Sep 2019 | 2019-09-25 18:14:28 | 2020-04-30 16:19:00 | Fail | Report sent to PFM - Works related to Project and contractor to determine if receivers are required, if not , receivers to be de-commissioned and removed from programming
MSA-DCA | WA2585291 | New flow switch required for boiler 2 - broken switch | Perth Concert Hall-Main Building-Roof Level-Boiler Room - Plant West | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 1 | CLOSE | 26 Sep 2019 | 2019-09-27 17:00:00 | 2020-04-28 09:00:00 | Fail | Valve actuator has failed and not opening main water line valve. No fault with the flow switch as reported by others. Awaiting replacement costs and BRAF to be submitted if required. Boiler has been isolated as cannot operate with correct valve operation.
MSA-MRWA | WA2596329 | South West Exit Light - Light has blown. | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor | GMP-BR | Electrical | General Electrical (EL) | MR - Handyperson - PFM | 2 | CLOSE | 02 Oct 2019 | 2019-10-07 17:00:00 | 2019-10-03 12:05:00 | Pass
MSA-DCS | WA2598148 | Unit 7, B Wing, Kitchen - Vinyl floor has bubbled in between the kitchen and dayroom. | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 03 Oct 2019 | 2019-10-08 17:00:00 | 2020-08-17 09:00:00 | Fail | installed new studded rubber flooring
MSA-DTAG | WA2597798 | Basement, Custody Cell 1 - Pieces of plaster have come off the wall inside the toilet room. | Perth Children's Court | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 03 Oct 2019 | 2019-10-04 17:00:00 | 2020-02-13 08:30:00 | Fail | Complete - steel cover plates fitted to sides of frames
MSA-MRWA | WA2598559 | Multiple lights out within Garage and rear entry. | Traffic Operations Centre | GMP-BR | Electrical | Lighting, External (EL) | MR - Handyperson - PFM | 2 | CLOSE | 03 Oct 2019 | 2019-10-08 17:00:00 | 2019-10-07 12:29:00 | Pass | Replaced outdoor lights with new tubes and starters
MSA-MRWA | WA2599043 | Ground, Site Entry - Exit light is faulty. | Heavy Vehicle Services | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | MR - Handyperson - PFM | 3 | CLOSE | 04 Oct 2019 | 2019-10-11 17:00:00 | 2019-10-07 10:20:00 | Pass | Replaced light
MSA-DCS | WA2600257 | Gatehouse - Domestic water supply pump (valve) is faulty. | Casuarina Prison | GMP-BR- HO | Mechanical Services | Pumps (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Oct 2019 | 2019-10-14 17:00:00 | 2019-10-09 09:10:00 | Pass | Supply, remove and replace 150mm valve in pump house on domestic water. Adjust pipework to suit.
MSA-DTAG | WA2600632 | Lift 9 - The doors close really slowly; lift takes 5 seconds to register and commence moving. | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 07 Oct 2019 | 2019-10-14 17:00:00 | 2019-10-07 16:00:00 | Pass | Found lift running without issue. Tested door open buttons, checked door tracks, cleaned light rays. Security mentioned delay attake off.
MSA-DCS | WA2601100 | Unit 5, D Wing Shower Block - Rust window frame. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Oct 2019 | 2019-10-15 17:00:00 | 2020-05-13 12:30:00 | Fail | window frame repaired
MSA-DTAG | WA2601440 | Level 4, Lift - Down call button is getting stuck and making noise intermittently. | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 08 Oct 2019 | 2019-10-11 17:00:00 | 2019-10-08 16:30:00 | Pass | Repaired landing panels/indicators.
MSA-DTWD | WA2601740 | Level G, Workshops/Welding Bay - TV monitors are not working. | Clarkson Campus | GMP-BR | ICT/Audiovisual | Hardware / Equipment (AV) | K2 Audiovisual Pty Ltd | 1 | CLOSE | 08 Oct 2019 | 2019-10-09 17:00:00 | 2019-10-10 08:00:00 | Fail | No completion notes
MSA-DCS | WA2602515 | CCU (11) Office - Carpet in front of the fridge is damaged. | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Oct 2019 | 2019-10-16 17:00:00 | 2021-01-11 10:30:00 | Fail | ACCESS DENIED BY CCU STAFF - JOB CLOSED OFF WITH COSTS TO DATE
MSA-DTAG | WA2602449 | Lift 9 - Lift has been 'jumping between floors'. | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 09 Oct 2019 | 2019-10-10 17:00:00 | 2019-10-09 14:00:00 | Pass | Equipment was found to be running on arrival.
MSA-DCS | WA2603868 | BR - Official visits, non-contact booth - intercom is faulty | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Oct 2019 | 2019-10-11 09:06:37 | 2020-03-24 09:00:00 | Fail | Replaced the damage intercom for non contact boot at official visit, tested working. Job completed
MSA-DFES | WA2604252 | Work shop yard - Eletric Gate not closing | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Steel Work (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 10 Oct 2019 | 2019-10-10 17:15:18 | 2019-10-10 16:30:00 | Pass | Technician attended the site of 23 Bowen Street, O'CONNOR, W to the Exit Gate no. W21838 on the 10/10/2019. Following a full test and inspection of door components found fault to be the encoder.isolate encoder in logic door.Full test and inspection of door function completed prior to leaving site.
MSA-DTWD | WA2603836 | B block Lift No2 intermittent staff being stuck in lift | East Perth Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 10 Oct 2019 | 2019-10-10 12:50:20 | 2019-10-17 14:55:48 | Fail | Steve Meyers confirmed lift is now operational
MSA-DCS | WA2613422 | WWTP computer memory is full, new external hard drive required. | Karnet Prison Farm | GMP-BR- HO | Waste Management | Waste Removal (WM) | MAK Industrial Water Solutions Pty Ltd | 2 | CLOSE | 14 Oct 2019 | 2019-10-17 17:00:00 | 2020-02-07 08:30:00 | Fail | External hard drive supplied & installed
MSA-DCS | WA2628713 | Unit 4, A & C - Dayroom/programs room panel is damaged. | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Oct 2019 | 2019-10-18 17:00:00 | 2020-04-28 14:02:00 | Fail | completing on WA3235074
MSA-DCS | WA2628801 | Unit 1 A2 and A3 buddy door is badly damaged-Please see Tony Wicks when arrival on site | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 15 Oct 2019 | 2019-10-16 10:04:41 | 2019-12-02 14:00:00 | Fail | Supplied and installed custom manufactured door, lock, cylinders and frame strengthening brackets
MSA-DCS | WA2628954 | Grounds - Elsewhere-repair faulty main water stop valve on ring main | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Oct 2019 | 2019-10-22 17:00:00 | 2020-06-20 16:00:00 | Fail | Isolated water supply to valve on prison ring main. Drained half of pipe though drain valve. Cut bolts on valve and slid valve out to allow second half of pipe to drain. Pumped water out of valve pit. Removed valve. Installed new valve. Returned pressure to main and tested valve.
MSA-DTAG | WA2629307 | No pictures showing on mutlt cameras. | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Oct 2019 | 2019-10-16 17:00:00 | 2020-04-06 15:06:00 | Fail | removed all cabling & installed new POE injector but to no avail. Installed POE injector again & re terminated all cabling. tested operation& all is working.
MSA-DTWD | WA2778698 | A block AF26 & AF28 Air Con - AC2 not cooling AF26 and AF28-See notes | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 15 Oct 2019 | 2019-10-18 17:00:00 | 2020-01-16 10:12:00 | Fail | Decommission and remove existing package unit A/CWaited for builder to replace platformInstalled new unit in existing locationInstalled new ductingInstalled new hand rail, gate and ladder hookCommissioned systemCleaned site and disposed of rubbish
MSA-DCS | WA2630829 | Kitchen, back of kitchen, Screed lip on the loading dock, ramp area - chipped/uneven pavement. | Hakea Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Oct 2019 | 2019-10-23 17:00:00 | 2020-07-20 15:00:00 | Fail | CUT ASPHALT, DIG FOOTING AND POUR NEW CONCRETE
MSA-DTAG | WA2631739 | 1903 basement-Lift 4 is out of service | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 16 Oct 2019 | 2019-10-17 17:00:00 | 2019-10-17 09:30:00 | Pass | No costs associated with this work order
MSA-DCS | WA2644887 | Unit 9 C Wing showers second & third - need tile and grout repair | Hakea Prison | GMP-BR- HO | Carpentry | Materials (CA) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Oct 2019 | 2019-10-23 17:00:00 | 2020-10-28 11:31:00 | Fail | TILES REPLACED AND GROUTED A NEWED
MSA-DTAG | WA2645461 | Level 4, Male Public Toilet - Block toilet. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Oct 2019 | 2019-10-22 17:00:00 | 2019-11-20 11:55:00 | Fail | Complete
MSA-DTWD | WA2645082 | A Block, Roof Access - Broken sensor in Lift Plant Room. | East Perth Campus | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 17 Oct 2019 | 2019-10-24 17:00:00 | 2019-10-18 08:30:00 | Pass | DETECTOR DOES NOT NEED TO BE REPLACED
MSA-DCS | WA2664684 | Unit 14, Plant Room - Water hose on guardian is frayed. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Oct 2019 | 2019-10-25 17:00:00 | 2020-02-03 14:00:00 | Fail | Measured hoses to suit. Collected new hoses from supplier. Installed new hoses on guardian unit. Tested for leaks. Removed rubbish.
MSA-DCS | WA2664700 | Unit 5, Plant Room - Calorifier is leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Oct 2019 | 2019-10-25 17:00:00 | 2020-07-24 16:00:00 | Fail | Noticed leak on flange on top of unit, when in plant room. Collected new gasket. Repaired damaged gasket and tested. Rechecked in afternoon. No leaks.
MSA-DTWD | WA2664930 | C Block, Ground, Male Toilets - Damaged tiles. | Midland Campus | GMP-BR | Building | Internal Walls (BU) | Programmed Building Projects | 2 | CLOSE | 18 Oct 2019 | 2019-10-23 17:00:00 | 2019-10-31 08:57:00 | Fail | Building contractor attended on October and has repaired the damaged tiles.
MSA-DCS | WA2665168 | Blocked toilet in the reception area | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Oct 2019 | 2019-10-20 09:28:52 | 2019-10-21 08:16:00 | Fail | Claim for $0.00, double up of Job is same as WA2665077
MSA-DCS | WA2665820 | Internal PX, MW has turned blue, entire internal perimeter | Hakea Prison-Main Gatehouse | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Oct 2019 | 2019-10-21 09:20:52 | 2019-10-21 07:00:00 | Pass | Internal PX MW turned blue. Phoned site and spoke to Control Room. MW fault has since then restore. Site has tested operations done perimeter checks and confirmed all is working fine.
MSA-DCS | WA2666561 | Unit 1, Cell A9- toilet is faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Oct 2019 | 2019-10-28 17:00:00 | 2019-10-28 10:47:00 | Pass | This job is a double up and is being actioned under work order WA2604315
MSA-DCS | WA2666572 | ISU B & kitchen-Emergency tones not heard in these areas (ISU B & main kitchen) | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Oct 2019 | 2019-10-28 17:00:00 | 2020-05-24 11:25:00 | Fail | Investigated emergency tone fault, replaced CI-8, and amplifier multiple components.Confirmed emergency tones working.Tested Ok.Job Complete
MSA-DTWD | WA2666833 | block A ground Lift, the entire button pad has come away from the lift wall, exposing the electrics | Joondalup Kendrew Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 21 Oct 2019 | 2019-10-22 17:00:00 | 2019-10-21 13:15:00 | Pass | On investigation found COP button panel loose. Tighten fixing screws as required. Run and monitor - No costs associated with this work order
MSA-DCS | WA2667809 | medical centre repair eve's -see Jim when onsite for location | Hakea Prison | GMP-BR- HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Oct 2019 | 2019-10-28 17:00:00 | 2020-10-12 09:28:00 | Fail | MULTIPLE REPAIRS MADE TO MEDICAL CENTER ROOF
MSA-DCS | WA2668688 | unit 1 gym various broken floor boards damaged | Wooroloo Prison Farm | GMP-BR- HO | Flooring | Timber (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 22 Oct 2019 | 2019-10-25 17:00:00 | 2020-04-30 09:30:00 | Fail | Attended to install jarrah floorboards and found maintenance have installed MDF and were happy with that.
MSA-DTAG | WA2672440 | Lift no 2 - dropped with a staff member in it, requires checking / maintenance | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 22 Oct 2019 | 2019-10-25 17:00:00 | 2019-10-23 14:30:00 | Pass | No costs associated with this work order
MSA-DTAG | WA2673332 | 1903 - goround level, Judicial corridor (behind court 1), - judges elevator out of service | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 23 Oct 2019 | 2019-10-28 17:00:00 | 2019-11-26 10:00:00 | Fail | No costs associated with this work order
MSA-DTWD | WA2673273 | Admin side, ground level, Lift - lift is making loud clunky sounds like its hitting the wall. | West One Services | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 23 Oct 2019 | 2019-10-24 17:00:00 | 2019-10-23 15:50:00 | Pass | GUIDE SHOES-ROLLER - BROKEN
MSA-DCS | WA2674863 | gate control visits TV monitor keeps resetting itself | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 24 Oct 2019 | 2019-10-25 07:37:17 | 2020-04-02 09:00:00 | Fail | No charges under warranty
MSA-DCS | WA2675257 | Please investigate fault with MDAS in Unit 2 C Block | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Oct 2019 | 2019-10-31 17:00:00 | 2019-10-29 09:00:00 | Pass | Produced report and supplied to M. Kovac for review- works complete
MSA-DTWD | WA2675138 | K & J blocks alarm faults | Balga Campus | GMP-BR | Security | Monitoring (SE) | Casa Security Pty Ltd | 0 | CLOSE | 24 Oct 2019 | 2019-10-24 13:35:01 | 2019-10-24 15:15:00 | Fail | job completed- rectified issues with codes
MSA-MRWA | WA2675436 | Desktop support area - Flickering light please remediate | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 24 Oct 2019 | 2019-10-25 17:00:00 | 2019-10-25 11:00:00 | Pass | Had to be handed over to electritions as tombstone is broken
MSA-DCS | WA2691184 | Unit 7, B Wing- vinyl on the floor has lifted | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Oct 2019 | 2019-11-04 17:00:00 | 2020-08-17 09:00:00 | Fail | DOUBLE UP - REPAIRS COMPLETED ON WA2598148 BY VINYL REPAIR CONTRACTORINV0ICED COST TO DATE - LABOUR AND LIL BIT MATERIALS ONLY
MSA-DTWD | WA2690728 | B Block, Roof, AHU9 -CHW Valve 0% when 80% cooling call | Midland Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 28 Oct 2019 | 2019-10-31 17:00:00 | 2020-05-20 12:04:00 | Fail | Work Order closed due to age as instructed by Brayden Hay.
MSA-DCS | WA2694319 | Administration, Movements Office - Carpet needs resticking as its lifting | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Oct 2019 | 2019-11-01 17:00:00 | 2020-06-29 11:30:00 | Fail | OLD CARPET UPLIFTED & REPLACED WITH CARPET TILES
MSA-DCS | WA2694356 | BR - External camera 40 not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Oct 2019 | 2019-11-05 17:00:00 | 2020-02-24 09:00:00 | Fail | Used EWP to access camera. Power to the camera tested ok. No image from camera. Removed and replaced the camera and lens. Tested ok to the gatehouse. Parts used:Panasonic WV-CP504Computar CCTV lens
MSA-MRWA | WA2694855 | Ground - Business services and Route assessment flickering lights | Heavy Vehicle Services | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 29 Oct 2019 | 2019-11-01 17:00:00 | 2019-11-01 11:27:00 | Pass | lights changed
MSA-DTAG | WA2695858 | Lift not functioning | Midland Courthouse | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 30 Oct 2019 | 2019-10-31 17:00:00 | 2019-10-30 15:45:00 | Pass | Completed - no charge
MSA-MRWA | WA2695857 | L7 room L.09 Re affix partition fabric. | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 1 | CLOSE | 30 Oct 2019 | 2019-10-31 17:00:00 | 2019-10-31 14:37:00 | Pass | Refitted fabric
MSA-MRWA | WA2695918 | Level 7, Male toilet- Liquid Nail door vent in place | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 2 | CLOSE | 30 Oct 2019 | 2019-11-04 17:00:00 | 2019-11-01 14:20:00 | Pass | Refixed grill to door
MSA-MRWA | WA2696023 | Level 8, Room 805- Flickering light in corridor please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 30 Oct 2019 | 2019-10-31 17:00:00 | 2019-10-31 14:59:00 | Pass | Replaced globe with new
MSA-DCS | WA2696638 | front gate roof sheeting above control coming away from building | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 31 Oct 2019 | 2019-11-05 17:00:00 | 2021-02-25 09:00:00 | Fail | REPAIRS CARRIED OUT & ROOF SHEETING SECURED
MSA-DTWD | WA2702295 | L Block Community Services Lift - does not work via swipe card stuck on G Level | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 01 Nov 2019 | 2019-11-06 17:00:00 | 2019-11-01 15:30:56 | Pass | Door errors- Cleaned upper and lower tracks and will check the software is up to date - No costs associated with this work order
MSA-MRWA | WA2702629 | G09 - Flickering light please remediate. | Don Aitken Centre MRWA Head Office-Main Building-Ground Floor | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 01 Nov 2019 | 2019-11-08 17:00:00 | 2019-11-05 10:16:00 | Pass | Replaced with new tube
MSA-DFES | WA2702801 | Malaga FS-Main Building - engine door no1 not closing, manual operation working | CFRS Malaga-Main Building | GMP-BR | Electrical | General Electrical (EL) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 02 Nov 2019 | 2019-11-02 13:03:59 | 2019-11-02 11:45:00 | Pass | To be closed - works being completed on WA2706714Double up
MSA-DCS | WA2703507 | Unit 7, A Wing- Clothes drier appears to work but fails to heat up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Nov 2019 | 2019-11-11 17:00:00 | 2019-11-06 12:44:00 | Pass | Not plumbing related
MSA-DTAG | WA2703604 | Lift 9 is out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 04 Nov 2019 | 2019-11-05 17:00:00 | 2019-11-04 14:15:00 | Pass | Lift stuck lvl4, doors closed. Err 148, 10, 149. Checked KTC’s. All ok. Checked KTS at lvl4. Found RHS door lock not making.Contact misaligned. Adjusted & tested. All ok. Lift in service.
MSA-DCA | WA2705479 | Lift No 5 stuck on Level 2 with the doors open | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 05 Nov 2019 | 2019-11-08 17:00:00 | 2019-11-06 10:45:00 | Pass | Investigated JFIS tripping fault, checked over possible causes for phase imbalance.
MSA-DTAG | WA2705412 | Custody Cell 1 - pieces f plaster have come off the wall inside the toilet room | Perth Children's Court-Courts 1 to 6-Basement | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 05 Nov 2019 | 2019-11-06 17:00:00 | 2020-07-17 12:40:00 | Fail | INSTALL STEEL COVER PLATES TO DOOR AND WALL
MSA-MRWA | WA2704778 | G09- Flickering light, please provide | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 05 Nov 2019 | 2019-11-06 17:00:00 | 2019-11-05 10:15:00 | Pass | Replaced light with new tube
MSA-DCS | WA2705875 | BR- Camera 62 no PT function | Hakea Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Nov 2019 | 2019-11-07 07:15:46 | 2020-04-15 16:10:00 | Fail | Found old analog PTZ camera had failed and required upgrading to a digital camera as analog parts no longer available. Sourced parts, attended site, upgraded network in gatehouse, installed network equipment in OSB Post 1, cabled, programmed and tested. Installed camera, cabled and programmed. Configured at gatehouse and confirmed camera is recording correctly.Job CompleteParts:AXIS CameraNetwork SwitchCablesConsumables
MSA-DFES | WA2706714 | Roller door No 1 failed to close | CFRS Malaga | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 06 Nov 2019 | 2019-11-06 19:08:53 | 2019-11-06 17:15:00 | Pass
MSA-DTAG | WA2706125 | Ground floor, LIFT 9 - Lift 9 has been locked on the ground floor due to frequently dropping. | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 06 Nov 2019 | 2019-11-07 17:00:00 | 2019-11-06 17:20:00 | Pass | Job completed - Multiple t4 errors at level 4. Found end rubber on landing doors worn out causing landing doors to move across causing lock to beclipped. Adjusted rubber and end bolt to reposition locks in correct position. Tested and returned to service.
MSA-DFES | WA2708057 | West end - electric gate - in fault, has been switched manual as failed to open automatically | CFRS Fremantle | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | COMPFIN | 07 Nov 2019 | 2019-11-08 17:00:00 | 2019-11-07 11:00:00 | Pass | Technician attended the site of 20 Phillimore Street, FREMANTLE, WA to the Entry gate no W21056 on the 07/11/2019. Following a full test and inspection of door components discovered power going in but none coming out the switch.Locate circuit breaker turned off bypass isolating switch.Reset breaker.Replaced 2 batteries.Checked all parameters and testes operation.Full test and inspection of door function completed prior to leaving site.
MSA-DTWD | WA2708893 | : L2 male toilet Student Services-large crack in bowl-see notes | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 07 Nov 2019 | 2019-11-14 17:00:00 | 2019-12-11 16:30:00 | Fail | replaced seals, pan sound
MSA-DTAG | WA2709350 | Lift 9 is parked on Level 4 and doors continually opening and closing | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 08 Nov 2019 | 2019-11-11 17:00:00 | 2019-11-11 13:45:00 | Pass | Unit switched off and rubber stoppers to be replaced, part ordered - No costs associated with this work order
MSA-DTAG | WA2709900 | Make good external cracking to boundary walls at Supreme Court-see notes | Supreme Court | GMP-BR-HO | Building | External Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Nov 2019 | 2019-11-15 17:00:00 | 2020-05-12 14:04:00 | Fail | Repaired brickwork
MSA-DCS | WA2710102 | Tamper alarm in the gate house. | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Nov 2019 | 2019-11-10 05:41:57 | 2020-04-17 12:19:00 | Fail | Replaced 2x Bosch outdoor enclosures
MSA-DCS | WA2711867 | All industries - PA system not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Nov 2019 | 2019-11-12 12:38:46 | 2020-05-12 09:42:00 | Fail | quote to be supplied
MSA-DTAG | WA2712250 | ground level custody - 2 stairs slip strip needs replacing | Midland Courthouse | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 11 Nov 2019 | 2019-11-14 17:00:00 | 2020-03-21 16:15:00 | Fail | stair nosings replaced
MSA-DTWD | WA2713171 | Block 3, metal fab- leaking acetoyne gas manifold | Thornlie Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | BOC LIMITED | 1 | CLOSE | 12 Nov 2019 | 2019-11-13 17:00:00 | 2019-11-12 12:00:00 | Pass | return valve on acetylene header bar. Non returnvalve is made from a stainlessball and brassseat. There are no sealsthat can be changedduring service. Customerwould like to changeNRV's to something that can be maintained.Replaced seats on pointvalves whilesystem was off
MSA-DCS | WA2715042 | Unit 1 - D3-toilet cistern leaking in ducting | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Nov 2019 | 2019-11-20 17:00:00 | 2019-11-14 09:17:00 | Pass | This is a repeat job order of order number WA2713229
MSA-DCS | WA2715615 | External zones - MW/PX external zones failure (blue) | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Nov 2019 | 2019-11-14 00:49:52 | 2020-02-23 10:18:00 | Fail | I found the entire external perimeter was failing, usually during the night.Found there was data corruption on the network, corrupting memory in field modules and crashing the network.I replaced network controller and other common components.Fault seemed to be starting around zones 19 and 20. SM17 between Zones 18 and 19 was showing unusual data behaviour.With Y data disconnected from the network and with only X data indicating on the module, when TXB cable was connected, X data would stop indicating and Y data would indicate.No other zones would not display these unusual symptoms when the same test was performed which indicated the fault was in the area of zone 19. Checked voltages, cables and connections in all zones in this area.No new components available so sourced old SM100-2 module from PFM stores in an unknown state.Began swapping modules in the problem area but fault reoccurred.Found if I disconnected TX data cable between zones 19 and 20, the system was stable.Rep
MSA-DTWD | WA2720225 | Level 2, tool store - split system not cooling | Perth Campus B5 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 14 Nov 2019 | 2019-11-21 17:00:00 | 2020-03-18 10:30:00 | Fail | AC West attended Tuesday 18th to install 7kw AC to tool storeroom
MSA-DTWD | WA2720419 | No power across the whole campus | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | NILSEN (WA) PTY LTD | 0 | CLOSE | 14 Nov 2019 | 2019-11-14 16:27:33 | 2020-06-20 15:00:00 | Fail | COMPLETED REPAIRS
MSA-DCS | WA2735254 | Gym area- Fire alarm wont clear & card trouble node 4 | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 Nov 2019 | 2019-11-16 08:59:54 | 2020-03-27 15:14:00 | Fail | Attended site and carried out the following.Was notified on arrival no escorts available till 13:00hrs1: Node 4 Kitchen has 24 volts output B Fault checked output and found no power reset output and measured line found ok.Reconnected line and left normal.2: Node 13 Gym has Az 79 latched in alarm.Checked zone but unable to find detector in alarm measured line resistance found to be 9ohms possible cable problem or damaged detector.Will require an ewp and a full day to access and change out faulty detectors.Will also require 6 Tyco conventional thermal to change out damaged detectors.Will required to be on a Wednesday between 11:30am and 3pm onlyEWP REQUIRES A BASKET WITH A TWO METER EXTENSION PLATFORM AND MUST BE ABLE TO FIT THROUGH A DOOR24/3/20 JN MS1: Graphics displaying card fault on node 4 kitchen. Found no voltage on 27vdc outputs and battery output. Power cycled kitchen node 4 and voltage returned all ok.2: Investigated gym zone disconnected and joined through mul
MSA-DCS | WA2735896 | Rear entry house - Fire hose reel is damaged | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 15 Nov 2019 | 2019-11-20 17:00:00 | 2019-11-22 09:07:00 | Fail | Attended site 22/11/2019 to replace FHRArrived on site and completed sign in process.System required pipe freezing as it was too big to drain.Replaced swing arm hose reel.Altered supply pipework to suit new hose reel.Completed site sign out process.
MSA-DCS | WA2736016 | Karnet Prison Farm - Gas oven - not working as filter cannot be cleaned in the air unit. | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Nov 2019 | 2019-11-20 17:00:00 | 2019-11-21 16:19:00 | Fail | Attended to by Kitchen equipment service guys close for $0.00
MSA-DTWD | WA2735775 | G Block, On Roof, GF21- Exhaust fan not working properly | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 3 | CLOSE | 15 Nov 2019 | 2019-11-22 17:00:00 | 2020-03-25 12:00:00 | Fail | Equipment collected form hire shop and taken to site. Meet with all tech and ran through pre start equipment check. Work area set up as per SWMS and barricaded off. Isolations put in place. Works carried out as per BRAF. Replacement of fan motor for boat engin workshop bay. Work area left tidy. Old motor removed for disposal.
MSA-DTWD | WA2768398 | Block 9- Lift alarm is sounding, lift indicating overload | Thornlie Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 18 Nov 2019 | 2019-11-19 17:00:00 | 2019-11-18 17:45:00 | Pass | Upon arrival at site, the technician performed the following:CONTROLLER - CIRCUIT BREAKER - NO ACCESS TO BUILDINGNo charges
MSA-MRWA | WA2768112 | Level 8, Room 812- Light flashing, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 18 Nov 2019 | 2019-11-19 17:00:00 | 2019-11-18 13:26:00 | Pass | Replaced light in hallway back in working order
MSA-MRWA | WA2768121 | Level 5, Room 551/552- Lights not working, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 18 Nov 2019 | 2019-11-19 17:00:00 | 2019-11-18 14:20:00 | Pass | Replaced two tubes in work area
MSA-DTAG | WA2769623 | ground lift 3 doors kept opening and closing when on the ground floor-see notes | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 19 Nov 2019 | 2019-11-22 17:00:00 | 2019-11-19 16:30:00 | Pass | Lift car door roller damaged require new. Cleared hanger of debris, should be ok in service until part is sourced and fittedtomorrow. Obr raised
MSA-DTWD | WA2769288 | Level 1 - faulty emergency phones on lifts 6 & 7 | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 19 Nov 2019 | 2019-11-19 15:32:59 | 2019-11-19 13:00:00 | Pass | No costs associated to this work order
MSA-DTWD | WA2770978 | Ground level, welding workshop - Potential leak in the MIG welding gas system. Need leak test done. | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Gas (PD) | BOC | 1 | CLOSE | 20 Nov 2019 | 2019-11-21 17:00:00 | 2019-11-20 16:00:00 | Pass | Job completed - Turned point valve off & carried out drop test on system for 0.5hr. No drop. Kim repaired hose to welder.
MSA-DCS | WA2771589 | Gatehouse, Entry gate (black internal gate) - Gate is not closing correctly | Banksia Hill Detention Centre | SPA-BR | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 21 Nov 2019 | 2019-11-25 17:00:00 | 2020-08-14 09:30:00 | Fail | Thursday 21 November 2019Inspected gate.Approx. 17m of track worn.150mm V wheels Change to U type if fit.BRAF to be submitted once pricing received on new wheel10/06/20Replaced 4 x wheels on double sliding gate.Monitored with Banksia Hill for the next 60 days to ensure replacement parts are running correctly.12/08/20Adjusted track.14/08/20Replace roller. Adjust limits
MSA-DCS | WA2771803 | ISU the cell call diverting to control issues | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Nov 2019 | 2019-11-22 09:31:38 | 2020-03-18 11:34:00 | Fail | Investigated cell call system faults, corrected faults and tested diversion function OK.Job Complete
MSA-DCS | WA2772262 | U2 H6- UPS battery failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Nov 2019 | 2019-11-22 14:06:34 | 2020-01-13 14:32:00 | Fail | Replaced APC RT1000 and load tested
MSA-DTAG | WA2800807 | Retrospective workorder Inv Purpose-Thorough clean of custody cell | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 21 Nov 2019 | 2019-11-22 17:00:00 | 2019-11-22 17:00:00 | Pass | Bio Clean
MSA-DCS | WA2780372 | Unit 1, A Wing Yard- fire hydrant is leaking | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Nov 2019 | 2019-11-26 09:09:26 | 2019-11-25 14:10:00 | Pass | While on site on 25/11/2019 completing other work the technician was requested to replace the swing arm hose reel in unit 1A block as it was leaking. Technician was escorted from the prison, through security checks and back to his van to gather extra tools and materials required. Escorted back in through security checks to unit 1A. Supplied and installed new swing arm hose reel.There was very little water to the reel and the leak was caused by a build up of pressure as the isolation valve as the isolation valve on the hose reel is faulty. Technician was unable to locate and valves on the block plan.He believes the valve is either turned off or the pipe is damaged.
MSA-DCS | WA2780549 | Main switch board door reed not alarming | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2019 | 2019-12-02 17:00:00 | 2020-05-28 21:23:00 | Fail | Installed 8input card, 4 x reed switches and programmed doors
MSA-DCS | WA2780557 | PE GR B1 in fault | Broome Regional Prison | SPA-GR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2019 | 2019-12-02 17:00:00 | 2020-04-17 12:17:00 | Fail | Tested PE beams and tamperAll working correctly
MSA-DCS | WA2780561 | AR RX in tamper | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2019 | 2019-12-02 17:00:00 | 2020-04-17 12:15:00 | Fail | Tested PE beams and tamper.All operational
MSA-DCS | WA2780563 | PE beam 6 in constant fault | Broome Regional Prison | SPA-GR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2019 | 2019-12-02 17:00:00 | 2020-04-14 14:28:00 | Fail | Relocated GR pe beamAligned and replaced tampers
MSA-DCS | WA2780567 | PE beam 7 in constant fault | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2019 | 2019-12-02 17:00:00 | 2020-04-14 14:53:00 | Fail | replaced defective tampers & investigated poor cabling terminations by previous installers
MSA-DCS | WA2780569 | PE beam 9 in constant fault | Broome Regional Prison | SPA-GR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2019 | 2019-12-02 17:00:00 | 2020-04-08 16:11:00 | Fail | Re cabled via roof Removed old conduit from roofRan cables into mss office and terminated Terminated cables in PE Beams Replaced defective tamper switchesRe installed beam set tampersChecked and tested on Gallagher System
MSA-DCS | WA2780572 | PE 3 MF4 in constant fault | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2019 | 2019-12-02 17:00:00 | 2020-04-08 16:16:00 | Fail | Re. Cabled Replaced tamper Adjusted or beam set
MSA-DCS | WA2780576 | PE beam 4 in constant fault | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Nov 2019 | 2019-12-02 17:00:00 | 2020-04-08 16:05:00 | Fail | Re cables up and replaced defective tamper s and terminations
MSA-DCS | WA2780785 | Unit 5, D Wing- air vents are rusted | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2020-07-14 14:00:00 | Fail | MANUFACTURED & FITTED NEW VENTS
MSA-DCS | WA2781417 | MPC 1 and 2 camera's not working - SEME on site | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Nov 2019 | 2019-11-26 16:36:42 | 2020-05-11 11:53:00 | Fail | Re cabled psu feed into Gallagher cabinet
MSA-DFES | WA2780604 | ground engine room, tilt door stuck on open | Kensington (old) | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2019-11-25 14:30:00 | Pass | Technician attended the site of 21 George Street, Kensington, WA to the Entry Door no. W22587 on the 25/11/2019. Following a full test and inspection of door components found wiring to pushbutton broken. Repaired cabling.Full test and inspection of door function completed prior to leaving site.
MSA-DTWD | WA2780828 | P Block, Room P011- Air Con is not working when it is really hot outside | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2020-03-30 14:00:00 | Fail | Found unit in po11 has intermittent control fault & cuts out, found parts no longer available, recommended replacing unit
MSA-MRWA | WA2780326 | IT build room Lights not working please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 25 Nov 2019 | 2019-11-26 17:00:00 | 2019-11-26 09:43:00 | Pass | Replaced two lights in the it build room
MSA-MRWA | WA2780355 | Lvl 7- Female toilets- Check/replace toilet seat | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | MR - Handyperson - PFM | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2019-11-26 09:43:00 | Pass | Passed along to plumbers
MSA-MRWA | WA2780463 | L3 kitchen Repair/Replace bin lid | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2019-11-28 12:49:00 | Pass | Replaced bin lid with a new one
MSA-MRWA | WA2780472 | L3 kitchen-Remove Frame/Hinges from Microwave Hob as per email. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | General Electrical (EL) | MR - Handyperson - PFM | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2019-11-26 13:11:00 | Pass | Removed frame around microwave
MSA-MRWA | WA2780701 | Faye's Desk - Please hang picture as per Fayes requirement | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2019-11-28 07:38:00 | Pass | Hung print in designated area
MSA-MRWA | WA2780702 | L3 3.36 repair light | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 25 Nov 2019 | 2019-11-26 17:00:00 | 2019-11-25 14:04:00 | Pass | Attended office and all led panels were on
MSA-MRWA | WA2780757 | Lvl 9, General Area- Multiple emergency exit lights out, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | MR - Handyperson - PFM | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2019-11-28 13:36:00 | Pass | Replaced exit light tubes in the gym area
MSA-MRWA | WA2780766 | Lvl 8, General Area- Multiple emergency exit lights out, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | MR - Handyperson - PFM | 2 | CLOSE | 25 Nov 2019 | 2019-11-28 17:00:00 | 2019-12-10 08:21:00 | Fail | Hand to electrician for possible upgrade
MSA-DTAG | WA2802237 | Lift 3 Lift showing ‘Out of Service’ | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 27 Nov 2019 | 2019-11-28 17:00:00 | 2019-11-27 17:45:00 | Pass | Job completed - Replaced car door roller
MSA-DTWD | WA2801571 | Block H ground all Poor water quality – foul tasting water | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 27 Nov 2019 | 2019-12-04 17:00:00 | 2020-04-06 18:00:00 | Fail | install 8x backflow devices, tested all good
MSA-DCS | WA2803551 | Gatehouse, Key issue- speaker is very quiet & unable to hear | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Nov 2019 | 2019-12-05 17:00:00 | 2020-05-06 09:09:00 | Fail | Sourced parts, attended site, repaired intercom faults and tested OKJob CompleteParts:Consumables
MSA-DFES | WA2803829 | Engine Room Doors- Remotes casing are starting to crack/wear tear- see notes below | CFRS Claremont | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | COMPFIN | 28 Nov 2019 | 2019-12-03 17:00:00 | 2019-11-29 15:00:00 | Pass | Replaced 3x remotes
MSA-DTAG | WA2803932 | L22 OPA kitchen door-Door swipe is in alarm mode and consistently beeping | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 28 Nov 2019 | 2019-12-03 17:00:00 | 2020-03-19 17:00:00 | Fail | Replaced lock on Level 22 Kitchen Door. Repaired power cable.
MSA-DTWD | WA2803101 | Intermittent monitor alarm from pump room | Leederville Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 28 Nov 2019 | 2019-11-28 17:00:00 | 2019-11-28 14:30:00 | Pass | .
MSA-DTWD | WA2803477 | Outside U block, glazing work shop - external wall has been hit by a car and unstable | Balga Campus | GMP-BR | Building | External Walls (BU) | M Construction (WA) | 0 | CLOSE | 28 Nov 2019 | 2019-11-28 14:29:01 | 2020-02-20 11:46:00 | Fail | Job complete
MSA-DTWD | WA2803639 | E-Block Room E77 Dough Break Machine trigger mechanism faulty | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 28 Nov 2019 | 2019-12-03 17:00:00 | 2020-08-18 14:20:00 | Fail | 29/11/19Arrived on site, found the trigger mech is broken but still useable, will require replacement. 18/08/20Called as requested to fit parts required fitted tested all working correctly now.
MSA-MRWA | WA2803480 | Level 2, Room 2.086- Install computer cradle to underside of desk. | Road Network Operation Centre (RNOC) | GMP-BR | Equipment | Office Appliances (EQ) | MR - Handyperson - PFM | 2 | CLOSE | 28 Nov 2019 | 2019-12-03 17:00:00 | 2019-12-02 09:27:00 | Pass | Refitted tower cradle to underside of the desk
MSA-MRWA | WA2803483 | Level 2, kitchen- Reinstall feet to kitchen tables. | Road Network Operation Centre (RNOC) | GMP-BR | Furniture | Domestic Furniture (FU) | MR - Handyperson - PFM | 2 | CLOSE | 28 Nov 2019 | 2019-12-03 17:00:00 | 2019-12-02 10:00:00 | Pass | Screwed feet back to the table legs
MSA-DCS | WA2804229 | Unit 4, Cell C2- Inside part of toilet bowl broken off (front) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Nov 2019 | 2019-12-03 17:00:00 | 2020-05-14 11:00:00 | Fail | Remove and replace broken toilet. Replace panadapter and associated pipework.
MSA-DTWD | WA2805190 | BLD 833- Security lights on 24/7 | Muresk Institute | GMP-BR | Electrical | Lighting, External (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 29 Nov 2019 | 2019-12-04 17:00:00 | 2019-12-03 09:00:00 | Pass | Job completed - replace and tested
MSA-MRWA | WA2804254 | Warehouse - Two high bay lights are failing to turn on in the warehouse | Jandakot Depot | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 29 Nov 2019 | 2019-12-06 17:00:00 | 2020-02-19 12:30:00 | Fail | Attended site and signed in. Awaited PFM to attend us on site. Went through Prestart with PFM. Used large EWP to access hi bay lights. Replaced faulty lights with LED fittings. Tested all okay. Job complete.
MSA-DCS | WA2808263 | Library front door-bottom of door is damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Dec 2019 | 2019-12-06 17:00:00 | 2020-03-27 09:50:00 | Fail | COMPLETE- NEW DOOR HUNG
MSA-DCS | WA2808499 | Unit 4 VESDA sampling point blocked | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 02 Dec 2019 | 2019-12-09 17:00:00 | 2019-12-06 12:30:00 | Pass | Hakea prison unit 4 GA/JN Attended site for low airflow issues on vesda in unit 4. Replaced capillary tubes in roof space when found blocked or cracked and cleaned out all sampling points in each wing. Air flows returned to normal on vesda and all faults cleared.
MSA-DTAG | WA2809174 | Lift - Lift not functioning | Midland Courthouse | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 02 Dec 2019 | 2019-12-03 17:00:00 | 2019-12-02 16:45:00 | Pass | Completed - no charge
MSA-DCA | WA2810114 | Gallery 7 L1 black dust falling from air con vents-also occuring in print room | Art Gallery of WA - James St - Main Building (Block B) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 03 Dec 2019 | 2019-12-06 17:00:00 | 2019-12-09 09:14:00 | Fail | COMPLETED
MSA-DCS | WA2809600 | unit 9/10 yard sink hole along large soak well cavines hole under bitumen | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 03 Dec 2019 | 2019-12-03 11:25:35 | 2019-12-03 15:00:00 | Fail | Works complete for work order
MSA-DCS | WA2809601 | zone 2 male urinal blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Dec 2019 | 2019-12-04 07:28:36 | 2019-12-04 12:30:00 | Fail | nil
MSA-DCS | WA2811362 | BoilerHouse- Plant Room- no 2 boiler not igniting/electrical issues with flow switches possible | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 04 Dec 2019 | 2019-12-05 12:21:26 | 2019-12-20 12:00:00 | Fail | Attended site to investigate faults on Boiler #1, 2 &4. Carried out the following replacements:Heater 1 - Replace flow switchHeater 2 - Replace Mod MotorHeater 4 - Replace Flow Switch
MSA-DCS | WA2811446 | Unit 8, Cell B12- Metal floor loose & vinyl is damaged | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 Dec 2019 | 2019-12-11 17:00:00 | 2020-03-24 17:15:00 | Fail | replaced damaged vinyl flooring
MSA-DCS | WA2811659 | Kitchen- Fluro light has blown | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Dec 2019 | 2019-12-09 17:00:00 | 2019-12-12 13:00:00 | Fail | Repaired lights.
MSA-DCS | WA2811701 | Faults on monitor 3x – node 5 living 2- battery load, node 11 family – m135 & m136 – break glass, no | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Automatic Fire Protection (ARA) | 3 | CLOSE | 04 Dec 2019 | 2019-12-11 17:00:00 | 2019-12-06 14:44:00 | Pass | Investigated the following;2x MCP faults in Family clear on arrival and able to be reset. Did not return.Node 5 showing battery low/disconnected on graphics but panel clear. Battery voltage okay. rebooted system and fault no longer visible - if fault reoccurs will require 2 technicians 3 hours to further investigateGatehouse Card 1, PSU fault reported - repaired on callout aleardy
MSA-DTWD | WA2810980 | Block 9- Lift is not working | Thornlie Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 04 Dec 2019 | 2019-12-05 17:00:00 | 2019-12-04 12:59:00 | Pass | CONTROLLER, CONTROLLER OTHERS,RUNNING ON ARRIVALNo Charge
MSA-DTWD | WA2811537 | BLD 834, Computer rooms 1 and 2- Various fluro lights faulty | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 04 Dec 2019 | 2019-12-09 17:00:00 | 2019-12-05 13:30:00 | Pass | Job completed - repair faulty lighting
MSA-MRWA | WA2811038 | Above Compactus- Flashing light please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 04 Dec 2019 | 2019-12-05 17:00:00 | 2019-12-05 10:42:00 | Pass | Tombstones broken will need electrician to replace
MSA-DCS | WA2836977 | Admin, Security Office - Battery backup for computer is not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 05 Dec 2019 | 2019-12-12 17:00:00 | 2020-03-12 10:12:00 | Fail | Installed replacement UPS in security, load tested OKJob CompleteParts:1 x 1500va UPS (SEME Stock)
MSA-DFES | WA2839131 | Museum - Please arrange for the bins to be cleaned in the outside compound of Garum restaurant side | DFES Education and Heritage Centre | GMP-BR | Cleaning | Cleaning (CL) | CLEANDUSTRIAL CLEANING SERVICE | 2 | CLOSE | 05 Dec 2019 | 2019-12-10 17:00:00 | 2019-12-05 18:30:00 | Pass | No completion notes
MSA-DTAG | WA2838956 | Lift not functioning. | Midland Courthouse | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 05 Dec 2019 | 2019-12-06 17:00:00 | 2019-12-05 14:45:00 | Pass | Completed - no charge
MSA-DCS | WA2840269 | Gate House Security Office-camera pole housingON PERIMITER rust causing water damage to camers A4B1 | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Dec 2019 | 2019-12-13 17:00:00 | 2020-04-24 14:33:00 | Fail | Replaced camera housing for new, (PFM stock) via cherry picker, realligned camera and tested fully operational.
MSA-DCS | WA2840277 | Gate house camera pole housing ON PERIMITER rusted causing water damage to camers B4/C1 | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Dec 2019 | 2019-12-13 17:00:00 | 2020-04-23 14:00:00 | Fail | Replaced camera housing located in zone C1 for new via cherry picker, re alligned cameras and tested operational.
MSA-DFES | WA2839899 | ground room 21-Severely broken tiles along edge strip vehicle tyres drive over threshold repair | CFRS Wangara | GMP-BR | Flooring | Tiling (FL) | AWB Co. | 2 | CLOSE | 06 Dec 2019 | 2019-12-11 17:00:00 | 2020-02-19 15:30:00 | Fail | As per BRAF
MSA-DCS | WA2840454 | Sound is not working in the Visits non contact,Contact system is faulty . | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Dec 2019 | 2019-12-07 12:38:25 | 2019-12-07 12:15:00 | Pass | Attended site and investigated the fault.Rectified problem with Jacques system in Visits.Conducted test.All ok at departure
MSA-DCS | WA2841184 | Gate House - Various alarms are activating even when not armed | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Dec 2019 | 2019-12-09 13:00:19 | 2020-05-06 12:50:00 | Fail | Attended site and checked all alarm logs. All alarms cleared. Door still to be replaced however waiting on Bandyup prison to replace door. All devices working correctly. Job complete
MSA-DCS | WA2841206 | unit 5 C13 window cracked | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Dec 2019 | 2019-12-12 17:00:00 | 2020-04-08 11:00:00 | Fail | replaced window
MSA-DCS | WA2841827 | Sally port main entrance prison driver pins malfuction | Albany Regional Prison | SPA-BR | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 09 Dec 2019 | 2019-12-09 23:37:27 | 2020-04-07 18:00:00 | Fail | 09/12/2019Disengage lock pins and by-pass limit switchHired 1 x 19ft electric scissor lift with trailer from Coates Hire AlbanyDec 19 to Apr 20WorkshopDesign, Fabricate, blast doors, paint doors, galvanise door frames, machine door pins, fabricate hinge parts.07/04/20 Replace bushes on outer doors.Install hinges inner P4 door.Install electric strike inner PA door.
MSA-DFES | WA2841091 | Engine room door No4 runners have jumped out of the guides | CFRS Belmont | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | COMPFIN | 09 Dec 2019 | 2019-12-10 17:00:00 | 2019-12-09 14:45:00 | Pass | Attended site and inspected bifold door . Noted door hit by LT unit and out of guides. Required toremove chain assembly on rhs . Repaired track and refit guide roller assembly . Replaced chainassembly and tested operations . Noted keyway stripped to other side of door and replaced .Tested operations all ok.
MSA-DCA | WA2842836 | AC throughout the building has stopped working | Shipwreck Galleries-Administration Building -Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 10 Dec 2019 | 2019-12-10 15:44:49 | 2019-12-10 16:30:00 | Fail | Attended site. AC system to have stopped operating throughout building. Applied tests and checks to find access to BMS system via desktop and remotely not responding. Applied tests and checks to find no ahu’s operating. Investigation found controls UPS system to have failed. Bypassed UPS to bring controls system and automation server back online. During investigation it was also found Batavia AHU 8 system to have a water leak causing excessive flooding in AHU plant room. Wet dry vacuumed drain, and drain pan. Cleaned up residual water and made area safe. Job to be closed out with a quotation to be submitted for supply and install of a new UPS.
MSA-DCS | WA2842351 | Unit 11, Cell D07 - blocked shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Dec 2019 | 2019-12-13 17:00:00 | 2019-12-10 13:32:00 | Pass | nil
MSA-DCS | WA2843145 | Kitchen - Blast chiller is not working | Bandyup Prison | GMP-BR- HO | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 10 Dec 2019 | 2019-12-17 17:00:00 | 2020-04-29 08:53:00 | Fail | Completed repairs to blast chiller.Re-attended after finding further details on Operations and Technical service sheets.Flashing fault cleared after 2 hr compressor sump heater satisfied.Ran through different programs and allowed time to run to completion.Unit running well.Unit is under sized compared to the size of the ovens. Pricing for a larger blast chiller. Current unit is a Tecnomac E15 65litre self contained.
MSA-DCS | WA2843630 | roof mounted Evap unit - not working correctly & rattling - | Bandyup Prison | GMP-BR- HO | Air Conditioning | Evaporative Coolers (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 11 Dec 2019 | 2019-12-12 08:37:58 | 2020-03-27 16:00:00 | Fail | Replaced bearings and belt as per BRAF on original WA number.Tested.All working okay.Staff advised.
MSA-DCS | WA2843676 | perimiter PTZ 8 camera has poor image-SEME on site | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Dec 2019 | 2019-12-18 17:00:00 | 2020-07-22 15:33:00 | Fail | cleaned fibre fibre connections and reconnected, image still has distorted line.Job to be quoted
MSA-DTWD | WA2844442 | T, U and V blocks air con not working | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 11 Dec 2019 | 2019-12-16 17:00:00 | 2020-03-06 08:00:00 | Fail | Attended Site , job already been done, the BMD people are looking after it and have sent in a braf
MSA-DCS | WA2846018 | Lights have blown/flickering- locations below | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Dec 2019 | 2019-12-17 17:00:00 | 2019-12-16 12:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA2846245 | Gate house, Pump house - Major leak in main fire system - pumps running continuously | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 13 Dec 2019 | 2019-12-13 11:37:24 | 2019-12-13 11:00:00 | Pass | Replaced jacking pump in unit 7 had to reconfigure old pipe to fit, tested and confirmed operation left system normal
MSA-DFES | WA2846825 | Engine Room rear 4 - wont close automattically - button seems sticky | CFRS Malaga | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 13 Dec 2019 | 2019-12-16 17:00:00 | 2019-12-16 16:45:00 | Pass | the roller shutter has gone past limits and could not operate, new limit switches are required.Door 3 is not closing automatically, plc has failed and will need replacing to maintain proper function of door. Quotation was submitted last December. Charging for the call out.
MSA-DTWD | WA2846557 | Sewage pit - appear to not be empting and a burning smell from control board | Rockingham Campus | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 13 Dec 2019 | 2019-12-16 17:00:00 | 2020-02-08 14:00:00 | Fail | replaced pump floats and control unit as well as other repairs
MSA-DTWD | WA2847140 | Lift 7 back button panel not working. | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 13 Dec 2019 | 2019-12-16 17:00:00 | 2019-12-16 17:30:00 | Fail | Tested operation and found all operational
MSA-DTWD | WA2847141 | Lift 5 not working | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 13 Dec 2019 | 2019-12-16 17:00:00 | 2019-12-16 16:15:00 | Pass | Traced fault to ground floor landing door lock not making and adjusted
MSA-DTWD | WA2847142 | Lift 6 back button panel not working. | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 13 Dec 2019 | 2019-12-16 17:00:00 | 2019-12-16 17:30:00 | Fail | Tested operation and found all operational
MSA-DCS | WA2854980 | control room CR centre camera 37 faulty | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Dec 2019 | 2019-12-19 17:00:00 | 2020-04-23 13:09:00 | Fail | Camera has been on test for 3 months without fail. Replace no longer required.New camera left in stores
MSA-DCS | WA2854998 | No communication from admin network switch | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 16 Dec 2019 | 2019-12-23 17:00:00 | 2020-02-24 13:00:00 | Fail | Job completed - cabled and installed siren to new gallagher panel
MSA-DTAG | WA2855038 | 1903 basement-a constant 'Licensing alarm' that pops up -see additional notes | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 16 Dec 2019 | 2019-12-17 17:00:00 | 2019-12-16 18:15:00 | Pass | Closed out at $0 under warranty
MSA-MRWA | WA2850706 | Ground floor offices - Fluctuating aircon temps - Please check air conditioning several offices | Materials Engineering Branch | GMP-BR | Air Conditioning | Ducted Split System (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 16 Dec 2019 | 2019-12-19 17:00:00 | 2019-12-17 11:00:00 | Pass | Repairs under new job number
MSA-DCA | WA2862999 | ground reception high temp alarm | Collection and Research Centre Welshpool-Bulk Wet Store | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 17 Dec 2019 | 2019-12-18 17:00:00 | 2020-02-27 16:30:00 | Fail | Attended Site. CRC BWS alarming on Hi temp. Investigation found BMS not responding to BMS. Forced system to manual control, raised a PO for Schneider to attend. Please see attached Schneider report of works carried out. BWS operating correctly.
MSA-DCS | WA2863092 | Abattior, WWTP tank split & leaking | Karnet Prison Farm | GMP-MW | Waste Management | Water Treatment (WM) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Dec 2019 | 2019-12-24 17:00:00 | 2020-03-16 14:30:00 | Fail | Waiting for approval to replace tank
MSA-DCS | WA2863505 | Location D6 & G4- Cabinets which house the electronic compounds are rusted & water is getting in | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Dec 2019 | 2019-12-20 17:00:00 | 2020-05-22 11:00:00 | Fail | Replaced corroded cabinet removed and reinstalled equipment, tested alarms.
MSA-DCS | WA2864004 | Perimeter senStar - faults - nod 6 battery fault & nod 7 supervision alarm. | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Dataline Visual Link Pty Ltd | 1 | CLOSE | 17 Dec 2019 | 2019-12-18 16:52:40 | 2019-12-18 07:30:00 | Pass | We have attended site and reset the clutter for processor 7 which has corrected the supervision issue. The battery fault reported for processor 6 is not covered under our defects liability period due to the batteries being outside of our scope of works. When Peter was on site he also noted that there is a battery fault present on processor 8 which may also require attention.
MSA-DTAG | WA2863070 | Lift No.9 - Lift 9 is intermittently going “out of Service”. | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 17 Dec 2019 | 2019-12-20 17:00:00 | 2019-12-17 14:36:00 | Pass | Lift running on arrival. Errors 202(0002), 207(0005), 149(top floor). Checked over car doors and checked car door sills, lift running fine. Could not fault lift to be monitored.
MSA-DTWD | WA2863900 | A Block - Eastern entry door, faulty latch | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 17 Dec 2019 | 2019-12-20 17:00:00 | 2019-12-19 08:30:00 | Pass | Replaced faulty lock
MSA-DCS | WA2864778 | Gardens compound- water cooler is faulty | Hakea Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 18 Dec 2019 | 2019-12-23 17:00:00 | 2020-03-25 11:39:00 | Fail | BRA declined invoicing CTD
MSA-DCS | WA2865277 | Unit 2, Day Room- Vinyl has bubbled | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Dec 2019 | 2019-12-27 17:00:00 | 2020-06-30 09:30:00 | Fail | DAMAGED VINYL UPLIFTED & REPLACED
MSA-DCS | WA2867127 | Kitchen ceiling - water damaged requiring major repairs | Bandyup Prison | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 3 | CLOSE | 19 Dec 2019 | 2019-12-30 17:00:00 | 2020-02-26 22:00:00 | Fail | Attended site and replaced water damaged sections of ceiling using gyprock.
MSA-DCS | WA2867239 | Unit 4B - Whirly Bird on the roof is not working | Wooroloo Prison Farm | SPA-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 19 Dec 2019 | 2019-12-30 17:00:00 | 2020-03-18 13:00:00 | Fail | Please see multiple work logs posted throughout duration of this job.Currently not working electrically on roof.Fan has been overhauled and ready to go once power supply had been re ran and hooked up into the isolator.
MSA-DTAG | WA2866051 | Leak in the roof in Court One next to the duty lawyer desk.L | Armadale Courthouse | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 Dec 2019 | 2019-12-24 17:00:00 | 2020-05-05 16:56:00 | Fail | located leak and rectified
MSA-DCS | WA2868566 | SHU (9), Control Room- CCTV keyboard not working (KVM Fault) | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 Dec 2019 | 2019-12-31 17:00:00 | 2020-02-06 15:35:00 | Fail | Replaced kvm and relocated cabling, tested all operating correctly. Restored system to normal.
MSA-DCS | WA2868579 | Visits hall- All cameras have gone down | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Dec 2019 | 2019-12-20 17:42:25 | 2019-12-20 14:53:00 | Pass | Reset workstation and tested cameras, confirmed correct operation
MSA-DCS | WA2870061 | Visits fixed camera 1 is not working | Bandyup Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Dec 2019 | 2019-12-24 15:10:51 | 2019-12-24 13:00:00 | Pass | Attended site and reconfigured camera recording settings and recording schedule. Reset Network video recorders and progranmed for correct operation, Fixed camera 1 all working and recording ok. Job complete
MSA-DCS | WA2870605 | Lift #9 is not working - Please attend Friday 27th December | Central Law Courts | GMP-BR- HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 24 Dec 2019 | 2019-12-31 17:00:00 | 2019-12-27 09:30:00 | Pass | No costs associated with this work order
MSA-DTAG | WA2870759 | Air-conditioning unit in the plant room is making a loud screaming noise | Central Law Courts-Main Building-Level 6-42 Plant Room | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 24 Dec 2019 | 2019-12-27 17:00:00 | 2020-07-17 10:37:00 | Fail | Works completed.
MSA-MRWA | WA2870344 | laboratory - air compressor not working | Materials Engineering Branch | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 24 Dec 2019 | 2019-12-24 12:13:32 | 2019-12-24 10:30:00 | Pass | Fuse holder replaced
MSA-DCS | WA2870968 | 3 nodes are showing fault | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 26 Dec 2019 | 2019-12-26 14:35:56 | 2019-12-26 13:00:00 | Pass | Casuarina 26/12/19 Multiple faults on graphics; -Learning Centre SIP FIP showing battery failed. Restarted PSU and fault cleared. Checked logs and multiple mains fail faults indicated since 18/12/19. Unsure of any shut down works. If problem persists will require replacement of Ampac FF 2A PSU. -Node 2 gate house Battery charge fail. Unable to clear fault battery and charger voltages okay. Card 1 PSU also indication fault. Further investigation required, new PSU and program change required to rectify. -Infirmary SIP Intermittent earth fault present. Unable to find cause as fault did not appear while on site, if fault returns will require 2x techs to investigate. Infirmary is currently under renovation/construction and fault may be related.
MSA-DFES | WA2870918 | Entry gate to the under ground parking sliding gate is not working | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Building | Roller Shutters (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 26 Dec 2019 | 2019-12-27 17:00:00 | 2019-12-26 10:30:00 | Pass | Found LH lift carriage wheel came off, circlip missing. Unjammed door , refitted wheel back ontoshaft. S&I new washers and circlip.Carried out full test of operation ok.
MSA-DCA | WA2871698 | Research associates office (near molecular labs) A/C is not operating | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Research Associates | GMP-BR | Air Conditioning | Ducted Split System (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 27 Dec 2019 | 2019-12-30 17:00:00 | 2020-02-27 10:00:00 | Fail | Attended site. Associates office CRC ac system not cooling (flashing fault symbol.) Applied tests and checks, investigation found system to have had a power interruption. Reset system and carried out tests and checks. System operating correctly.
MSA-DCS | WA2871328 | SOG Pod- pumphouse diesel fire pumps running ,fire alarms activated all units | Casuarina Prison | SPA-GR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 27 Dec 2019 | 2019-12-27 12:12:43 | 2019-12-30 15:27:00 | Fail | 27/12/19 BGPumps continually kicking in and activating alarms.On arrival to site, spoke to maintenance who informed me that Nathan from DWE had replaced blown fuse in JP control board and both JPnow active. Tested and confirmed.28/12/19 BGAttended site for pump fault. At 0050hrs pump high temp alarm activated. Reset pump controller and cleared fault. Tested Standby JP and allworking okay. Duty JO making abnormal noises and not meeting demand so tagged out to prevent over heating and any further damage.Instructed Pod to contact plumbing contractor to rectify or else issue will persist.30/12/19 BGGate/Pod staff instructed by AHS to engage ARA every 4 hours to refuel pumps. Attended site, no pump activation and both Diesels at 100%.Standby JP operating correctly. Instructed pod staff to only call 4 hours after pump activation on graphics system. Informed OIC. All okay.Stop button not working on pump controller - engaged Allied pumps to rectify issue - all working ok as tested
MSA-DCS | WA2871409 | Kitchen- Fluro lights not working in 4 fridges | Melaleuca Prison | SPA-GR | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 27 Dec 2019 | 2019-12-28 09:01:52 | 2020-04-01 12:00:00 | Fail | As per quoteReplace all lights in cool roomsSeal all conduits and entries
MSA-DCS | WA2871634 | CCU- Cell 2- Blocked drain | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Dec 2019 | 2020-01-02 17:00:00 | 2020-01-02 14:16:00 | Pass | Repaired inlet valve to wc cistern
MSA-DCS | WA2871978 | Pump House electric pump run fault. Reoccured again . | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 29 Dec 2019 | 2019-12-29 15:53:52 | 2020-02-07 08:57:00 | Fail | 28/12/19 - isolated diesel fire pump. Investigated cause. Tested jacking pumps and discovered that the primary jacking pump was faulty, not able to pressurise system and running hot and noisey. Helwig elec disconnected and tagged out the faulty pump to allow fo it to be sent away for servicing. Secondary jacking pump was test numerous times for correct operation. Pump started and stopped at the correct pressures.29/12/19 - Isolated diesel fire pump. Tested jacking pump. Helwig elec were required to install new fuse and circuit breaker, to get jacking pump running. Jacking pump stop/start pressures tested and working correctly. Action plan organised with Pod/Principle officer and gate house if problem occurs again. 30/12/19 - Inspected pump house operations. Informed new gate house, POD staff and maintenance staff of the pump failure and action taken, because of the failure of jacking pump over the weekend.30/12/19 - Disconnected faulty jacking pump. Removed connecting pipework. C
MSA-DCS | WA2872563 | Pharmacy Stores area - roof leak near roller door - see Dom | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Dec 2019 | 2020-01-07 17:00:00 | 2020-03-19 11:34:00 | Fail | rectified leak
MSA-DTAG | WA2872307 | Lift 9 is out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 30 Dec 2019 | 2019-12-31 17:00:00 | 2019-12-30 13:25:00 | Pass | Lift stuck lvl4, err149, 708, 148, 003, 202, 1209, 065. Replaced centre L/door isolators & adjusted pick up rollers on lvl3,4,5.Tested. Doors not clipping rollers while travelling. Err65 still present. Requires new PHS inductors. Lift out of service.
MSA-DTAG | WA2872688 | Basement, Custody Cell- An accused has defacaeted in the drinking fountain | Perth Children's Court | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | OCS SERVICES PTY LTD | 1 | CLOSE | 30 Dec 2019 | 2019-12-31 17:00:00 | 2019-12-31 09:00:00 | Pass | Bio Clean
MSA-DCS | WA2872958 | Unit 8 Cell A12 toilet pan leaking from flange through wall in the cell | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 31 Dec 2019 | 2020-01-06 17:00:00 | 2020-03-15 14:00:00 | Fail | Works completed as far as possible due to condition of floor in cell.
MSA-DCS | WA2873498 | Health Centre, treatment room 1- double sliding doors falling off rollers & tracks | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 31 Dec 2019 | 2020-01-08 17:00:00 | 2020-03-30 12:30:00 | Fail | Attended site and assessed what repairs were required, sliding doors need to be modified using heavy duty track and roller system.Supplied and installed new heavy duty track to door head.Supplied and installed new heavy duty rollers rated to support 120kg to solid core doors.
MSA-DFES | WA2873511 | Rear engine room door for light tank- door has come off the rollers | CFRS Claremont | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | COMPFIN | 31 Dec 2019 | 2020-01-02 17:00:00 | 2020-01-02 13:30:00 | Pass | Found LH lift carriage wheel came off, circlip missing. Unjammed door , refitted wheel back ontoshaft. S&I new washers and circlip.Carried out full test of operation ok.
MSA-DCS | WA2875912 | * WARRANTY* Zone 7 omnitrax constantly alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Dataline Visual Link Pty Ltd | 0 | CLOSE | 02 Jan 2020 | 2020-01-02 12:08:29 | 2020-01-02 12:00:00 | Pass | Checked processor 3 for Zone 7 false alarms. Found no issues with settings. Rebooted and reset clutter. No alarms noted after an hour of monitoring.
MSA-DCS | WA2875913 | * WARRANTY* Senstar node 8, side 4 supervision keeps alarming | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Dataline Visual Link Pty Ltd | 1 | COMP | 02 Jan 2020 | 2020-01-03 08:11:55 | 2020-01-02 12:00:00 | Pass | Checked processor 8 for intermittent supervision alarms. Found clutter hap between current and historic with 20+dB gap. Reset clutter and monitored system for an hour. All okay.
MSA-DCS | WA2876316 | MVR 6 is offline & Max pro slave is offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Jan 2020 | 2020-01-09 17:00:00 | 2020-03-30 12:00:00 | Fail | BRAF declined, job to be completed with costs to date
MSA-DCS | WA2876339 | External gardens - CVP pump is not running | Hakea Prison | SPA-GR | Equipment | Gardening / Landscaping Equipment (EQ) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 02 Jan 2020 | 2020-01-03 12:38:21 | 2020-10-14 16:00:00 | Fail | Received approval to remove pump on the 10-6-2020, pump schedule for removal 12-6-2020.14/10/20 - Installed new Grundfos pump, replaced faulty indicator lights and corroded discharge, test and commissioned the new pump.
MSA-DCA | WA2876956 | Water leak from chilled water pipe line. | Perth Concert Hall-Main Building-Ground Floor-Chiller Room | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 03 Jan 2020 | 2020-01-06 17:00:00 | 2020-01-18 13:11:00 | Fail | Carried out localised freezing of pipework to enable repair to leaking pipework section. Complete leak reapair and check, All ok. Carried out re-lagging of pipework. Left All ok.
MSA-DCS | WA2876755 | PTZ 4 has no movement | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Jan 2020 | 2020-01-10 17:00:00 | 2020-05-21 15:37:00 | Fail | FLIR camera sent from Seme office.Removed faulty camera and installed with FLIR camera.Camera confirmed correct operation
MSA-DCS | WA2876757 | PTZ 13 has no tilt | West Kimberley Regional Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Jan 2020 | 2020-01-10 17:00:00 | 2020-07-15 18:48:00 | Fail | Terminated camera and installed 8port network switch and Axis POE injector.replaced fibre patch leads with 2x SC to LC. installed 2x Planet MGB-SX in EC12 and unit 1 office.installed Novaris surge protection and din rail in EC12.powered camera and checked functionality
MSA-DCS | WA2876975 | Unit 1 - A & C gate lock hard to lock/faulty/exercise yard | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 03 Jan 2020 | 2020-01-10 17:00:00 | 2020-04-27 10:00:00 | Fail | replaced lock, fixings and adjust escutcheon
MSA-DCS | WA2878459 | Retrospective work order - Investigate and repair damages in Urquhart Unit - att 4/1 | Banksia Hill Detention Centre | SPA-BR | Building | General Building (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 04 Jan 2020 | 2020-01-05 07:00:00 | 2020-02-25 15:00:00 | Fail | COMPLETE - ALL DAMAGES REPAIRED
MSA-DCS | WA2878191 | Unit 1 house 3 whole house off line | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jan 2020 | 2020-01-06 17:01:35 | 2020-01-14 18:04:00 | Fail | Ups failed to turn onUsed APC RT1000 from site stock.Seme to replace site stock
MSA-DCS | WA2878566 | unit 1 house 1 and 3 entry doors not securing | West Kimberley Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jan 2020 | 2020-01-06 19:30:22 | 2020-01-15 16:12:00 | Fail | Replaced gallagher controller from Seme stock in unit 1 house 1 Tested both door locks and confirmed correct operation
MSA-DCS | WA2878607 | Unit 8, A12 - toilet bowl is loose from the floor and leaking from rear seal | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Jan 2020 | 2020-01-07 11:53:54 | 2021-01-07 14:00:00 | Fail | Works completed as far as possible for condition of floor in cell.
MSA-DCS | WA2878683 | Unit 1, House 8- Security equipment cupboard is beeping & flashing | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Jan 2020 | 2020-01-13 17:00:00 | 2020-01-14 18:08:00 | Fail | Removed bypass and load tested ups, failed after 30seconds Replaced with APC RT1000 from site stock Seme to replace site stock
MSA-DTAG | WA2878667 | Bio Clean required in Custody Cell 2, There is blood on the floor, walls and door | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 0 | CLOSE | 06 Jan 2020 | 2020-01-06 16:31:51 | 2020-01-06 20:00:00 | Fail | Cleaned Cell 2 after blood was reported.
MSA-DTAG | WA2878897 | Ground floor - Lift 9 is showing "out of service" | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 06 Jan 2020 | 2020-01-07 17:00:00 | 2020-01-07 10:30:00 | Pass | No costs associated with this work order
MSA-DCS | WA2879385 | Unit 13, B&D Cell D1- floor needs to be regrouted as it constantly leaks | Casuarina Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Jan 2020 | 2020-01-14 17:00:00 | 2021-06-03 15:00:00 | Fail | TILE RPAIRS CARRIED OUT, WATERPROOFIN
MSA-DCS | WA2880206 | gate house PDA fault keeps coming up on screen | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Jan 2020 | 2020-01-08 13:55:41 | 2020-01-13 23:26:00 | Fail | Traced cables to,receiver and replaced receiver with site spare.Fault repaired Bosch Receiver usedSite spare replaced with new
MSA-MRWA | WA2880302 | external side of building external door broken | Western Vent Building | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 07 Jan 2020 | 2020-01-10 17:00:00 | 2020-01-08 10:30:00 | Pass | Replace broken Mortice lock & supply & install ADI bolt to vent hatch door
MSA-DCS | WA2880678 | Unit 5, Cell A3- vinyl floor is lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Jan 2020 | 2020-01-15 17:00:00 | 2020-07-15 12:43:00 | Fail | RE STICK LOOSE FLOORING & INSTALLED NEW THRESHOLD TRIM TO CELL DOORWAY
MSA-DCS | WA2880892 | Kitchen -main valve leading to kitchen on ring main not shutting/needs repair | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jan 2020 | 2020-01-15 17:00:00 | 2020-04-09 08:17:00 | Fail | This job cannot be completed due to the fact the valve is within the build site and we have no access.
MSA-DCS | WA2881501 | WWTP Computer not working | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 2 | CLOSE | 08 Jan 2020 | 2020-01-13 17:00:00 | 2020-05-07 15:57:00 | Fail | Attended site and met with site contact.Signed in at gatehouse and declared computer to security officers.SO inspected box and declared it OK.Set up and installed computer.Found that Screen had a different cable connection than what was available on PC.Require either DP to DVI or a screen and cable able to connect to DP.
MSA-DCS | WA2881585 | Cameras - Perimeter camera 18 & Visit camera 11 not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Jan 2020 | 2020-01-13 17:00:00 | 2020-05-01 12:00:00 | Fail | Dismantle faulty honeywell IP PTZ camera in visits and install new, test all function and live/rec. camera back to normal operations. Job completed.
MSA-MRWA | WA2880670 | Carpark/Garage- clean leaves/ remove weeds | Traffic Operations Centre | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | MR - Handyperson - PFM | 3 | CLOSE | 08 Jan 2020 | 2020-01-15 17:00:00 | 2020-01-14 11:45:00 | Pass | Cleaned up area and removed weeds
MSA-DCS | WA2881921 | Perimeter, Zone 11 keeps activating | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jan 2020 | 2020-01-10 07:29:05 | 2020-02-04 13:45:00 | Fail | Checked though Cardax logs for zone 11 PE beam and microwave alarms. Cleaned receiver and transmitter PE beam covers. Sprayed concrete footings with bug spray. Used shovel to remove dirt left behind from installation of light Posts. Tested ok. Monitored through the day for false alarms. Microwaves tested ok also.
MSA-DCS | WA2882267 | Health admin MDAS monitor no response (R )heath admin south west and south east external | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Jan 2020 | 2020-01-14 17:00:00 | 2020-03-13 15:19:00 | Fail | Cabling removed by construction workers in health admin area . To be repaired by construction contractor.No further attendance required by Seme.
MSA-DCS | WA2882431 | Investigate possible water leak between water meter and water storage tank | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jan 2020 | 2020-01-14 17:00:00 | 2021-02-19 09:20:00 | Fail | 24/1/20 - tested main water line between street water meter and holding tanks. Pipework is ok and no leaks present.
MSA-DCS | WA2882436 | L1 group room Hot water tap not working, filter light flashing | East Perth | SPA-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jan 2020 | 2020-01-14 17:00:00 | 2020-03-17 15:15:00 | Fail | COMPLETED
MSA-DCS | WA2882548 | Health Care CNM office - A/C spilt is leaking | Bandyup Prison | GMP-BR- HO | Air Conditioning | Ducted Split System (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 09 Jan 2020 | 2020-01-10 12:54:48 | 2020-03-24 15:00:00 | Fail | Removed old indoor and outdoor systems. Replaced with suitable wall split as per BRAF.Installed condensate pump.Tested new system.Staff advised for working OK and office to resume.
MSA-DCS | WA2883626 | Unit 6 - B Wing- Approx 8 floor tiles are missing | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Jan 2020 | 2020-01-16 17:00:00 | 2021-02-24 14:01:00 | Fail | REPLACED BROKEN AND RETIRED FLOOR TILES
MSA-DCS | WA2883776 | Stores - Netting on the roof has come down & needs to be hooked back up. May need to be replaced | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Jan 2020 | 2020-01-17 17:00:00 | 2020-03-20 15:00:00 | Fail | BIRD NETTING REPAIRED
MSA-DCS | WA2883823 | Unit 14, Whole Unit- Cell window vents are stiff & will not close, they all need to be repaired | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Jan 2020 | 2020-01-17 17:00:00 | 2020-05-01 10:33:00 | Fail | We eased and lubricated 8 vents, prison to report another job for the rest.
MSA-DCS | WA2883876 | Unit 2, Camera C9 has damaged cover & mounting | Bunbury Regional Prison | GMP-BR-RC | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jan 2020 | 2020-01-11 09:15:38 | 2020-01-17 17:59:00 | Fail | Accessed camera from boom lift, removed damaged camera and brackets, installed new camera and bracket , installed POE injector and programmed camera into indigo system, confirmed recordings .Indigo PTZ and poe injector from Seme stock
MSA-DCS | WA2884465 | Fire Panel Faults + Master Control Room | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 10 Jan 2020 | 2020-01-15 17:00:00 | 2020-03-12 07:38:00 | Fail | 10/01/2020Attended site Friday 7:15pm.Unit14 Fault & Various alarms in the control room.On arrival denied access due to no escort available.Advised by onsite personnel that the callout was a priority 2.12/03/2020 KSattended unit 14 and found panel normal with no faults.Left normal.
MSA-DTWD | WA2884227 | BLD 840 - Electrical driven projector screen won’t move up or down | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 10 Jan 2020 | 2020-01-15 17:00:00 | 2020-01-14 09:30:00 | Pass | Replaced Faulty limit switch
MSA-MRWA | WA2884620 | alarm has been tripped, please investigate, and re-set alarm | Materials Engineering Branch | GMP-BR | Security | Security Management System (SE) | MCS Security Group | 0 | CLOSE | 11 Jan 2020 | 2020-01-11 20:28:55 | 2020-02-19 11:02:00 | Fail | Due to response time of 90 mins (day), MCS will not be charging.
MSA-DCA | WA2885299 | chiller from air-con in fault | Collection and Research Centre Welshpool | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 12 Jan 2020 | 2020-01-12 21:31:57 | 2020-01-12 23:00:00 | Fail | COMPLETED
MSA-DCS | WA2886880 | Gymnasium - Camera on gym roof not moving | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Jan 2020 | 2020-01-16 17:00:00 | 2020-01-17 13:30:00 | Fail | Attended site.Found faulty camera power supply.Replaced with new (Tactical Technologies mod.TPS24-6AC supplied by SEME).Tested all PTZ functions of Gym PTZ cameras (camera 179 and camera 180).All back to normal and operational.
MSA-DCS | WA2886897 | Gate House - Control Room-RESPONSE ROAD GATE FAULTY NOT CLOSING | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 13 Jan 2020 | 2020-01-16 17:00:00 | 2020-04-14 11:30:00 | Fail | Removed existing limits and remove support brackets. Install new switches and brackets. Wire in and test operation. Adjust as required. All working.
MSA-DCS | WA2886927 | Unit 4, A & C, programs room - Hole in panel in wall, needing repairs | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Jan 2020 | 2020-01-20 17:00:00 | 2020-04-28 13:56:00 | Fail | completing on WA3235074
MSA-DCS | WA2886945 | Yard office AC loss P26 maint/WS communication work failure | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Jan 2020 | 2020-01-13 17:16:33 | 2020-01-16 12:42:00 | Fail | Installed Bosch transponder ea500B from WKRP site stock System online with no faults showing
MSA-DCS | WA2886981 | Zone 14 MWH failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Jan 2020 | 2020-01-20 17:00:00 | 2020-01-31 10:30:00 | Fail | Replaced zone14 Microwave high with new ultrawave set. All replaced and programmed ok. Job complete, site stock used
MSA-DCS | WA2887385 | BR - control room - external zone 11 microphonics in constant alarm | Hakea Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jan 2020 | 2020-01-14 11:45:20 | 2020-03-13 11:30:00 | Fail | Checked plot graph for false alarms over the last 2 days. Laid cable straight in the trenches and filled them in. Walk tested and checked calibration. Tested ok.
MSA-DCS | WA2887414 | Zone 3- mircowave is not activating | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Jan 2020 | 2020-01-13 20:07:08 | 2020-02-09 14:47:00 | Fail | Sourced parts, attended site, repaired fault with Zone 3 outer Flex PS processor which was generating excessive noise. Tested Microwave OK.Job Complete
MSA-DTAG | WA2887494 | L5 court 55-Request a special clean ASAP. Individual in custody spat over the custody doc -see notes | Central Law Courts | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | OCS SERVICES PTY LTD | 0 | CLOSE | 13 Jan 2020 | 2020-01-13 16:40:59 | 2020-01-13 17:00:00 | Fail | No completion notes
MSA-DCS | WA2890277 | unit cells A4 and A14 medical hatch locks faulty and been open inside cell | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 14 Jan 2020 | 2020-01-15 07:39:13 | 2020-06-03 12:00:00 | Fail | Job completed - Attend site, survey hatches, require replacement. Onsite supply and install two hatches and required plates.
MSA-DCS | WA2890344 | unit 4 PA system not working | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Jan 2020 | 2020-01-16 17:00:00 | 2020-06-02 11:00:00 | Fail | Attended site.Replaced faulty horn speaker with new (Redback mod.C-2053 10 W horn speaker - supplied by SEME).Replaced damaged cable (30m figure 8 cable - supplied by SEME).Conducted test.All back to normal and operational
MSA-DCS | WA2890367 | SHU (9) - Viewing camera in A04 not clear picture | Casuarina Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Jan 2020 | 2020-01-17 17:00:00 | 2020-03-13 12:30:00 | Fail | Replaced existing analogue camera with IP corner mount camera. Installed Truen is decoder and connected to Maxpro, confirmed video recording on Gatehouse NVR
MSA-DCS | WA2890393 | Unit 3, House 1- Electronic locks & door frames damaged | West Kimberley Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jan 2020 | 2020-01-21 17:00:00 | 2020-02-26 11:00:00 | Fail | Door frame is still.damaged and unsure when it will.be repaired Lock has been put into PFM site stock
MSA-DCS | WA2891109 | Control - UPS failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jan 2020 | 2020-01-21 17:00:00 | 2020-01-14 18:07:00 | Pass | UPS has failed, fan running but will not boot up and hold load.Replaced with APC RT1000 from site stock.Seme to replace site stock
MSA-DTAG | WA2890675 | roof - Possums are gaining entry to Court roof space – several points of entry require to be sealed | Mandurah Courthouse | GMP-BR-HO | Roofing | Tiled Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 Jan 2020 | 2020-01-21 17:00:00 | 2020-04-15 08:52:00 | Fail | sealed and repaired roof
MSA-DTWD | WA2890452 | BLD 833 Homestead- Refrigeration controls faulty on Coolroom & Freezer room | Muresk Institute | GMP-BR | Refrigeration | Coolroom (RE) | CDA Air & Solar | 2 | CLOSE | 14 Jan 2020 | 2020-01-17 17:00:00 | 2020-01-17 13:22:00 | Pass | 17/01/20 - Job Attendance (up to and including first hour of labour) to check operation of BLD 833 Homestead - Refrigeration controls faulty on Coolroom & Freezer room. 17/01/20 - Apprentice labour.Our Tech checked alarm parametres - nothing abnormal except alarm delay set to 20 minutes when default is 2hrs. Set to 60 minutes.
MSA-DTWD | WA2890773 | room 3 - Lifesaver smoke alarm faulty | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 1 | CLOSE | 14 Jan 2020 | 2020-01-15 17:00:00 | 2020-01-14 14:30:00 | Pass | Replaced smoke alarm
MSA-DTWD | WA2890808 | BLD 822A, Managers office & bathroom- light circuit blown | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 14 Jan 2020 | 2020-01-17 17:00:00 | 2020-01-14 15:30:00 | Pass | Replaced faulty HRC fuse
MSA-DTWD | WA2891035 | R block seal ceiling tiles as there is large gaps internal ceiling tiles in RO13 | Balga Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 14 Jan 2020 | 2020-01-17 17:00:00 | 2020-03-27 14:00:00 | Fail | Install 8 sections (24m) L- flashing to enclose gaps
MSA-DTWD | WA2891074 | BLD 839 Pavilion Exhaust fan faulty | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 14 Jan 2020 | 2020-01-17 17:00:00 | 2020-01-16 15:00:00 | Pass | Replaced exhaust fan
MSA-MRWA | WA2890816 | Office area- Multiple flashing/blown lights, please remediate | Heavy Vehicle Services | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | CLOSE | 14 Jan 2020 | 2020-01-17 17:00:00 | 2020-01-14 14:30:00 | Pass | Replaced flashing and blown lights with new
MSA-MRWA | WA2890818 | L7 lift lobby area Flashing light, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 14 Jan 2020 | 2020-01-15 17:00:00 | 2020-01-14 12:05:00 | Pass | Replaced flashing light with new
MSA-DCS | WA2903935 | Unit 1 Security Office RCD W 12 E tripping | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jan 2020 | 2020-01-21 17:00:00 | 2020-01-23 10:00:00 | Fail | Rcd hap tripped
MSA-DCS | WA2903941 | Gallagher time sync is out by approx.. 10 minutes | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Jan 2020 | 2020-01-21 17:00:00 | 2020-05-11 08:21:00 | Fail | Synced gps server times
MSA-DCS | WA2909066 | MPU CCTV unable to select cameras | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Jan 2020 | 2020-01-22 17:00:00 | 2020-05-26 22:47:00 | Fail | Installed and programmed new workstation.Added second 27inch monitor and wireless keyboard and mouse combo.Cabled Cat5e from switch to workstation
MSA-DCS | WA2909118 | Camera 51 not working | West Kimberley Regional Prison | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Jan 2020 | 2020-01-22 17:00:00 | 2020-03-04 22:15:00 | Fail | EWP required. Replaced PTZ with new Pelco seme stock used. All replaced and programmed and tested ok. Job complete
MSA-DCS | WA2921652 | Entry control - Evaporative ducts, seems to be working except there is no air flow in SO office | Bandyup Prison | GMP-BR- HO | Air Conditioning | Evaporative Coolers (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Jan 2020 | 2020-01-16 15:10:21 | 2020-01-17 11:13:00 | Fail | Closing down this job due to major works quote on new WA number
MSA-DFES | WA2906200 | Engine Room Door 2, cable has snapped | CFRS Rockingham | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 15 Jan 2020 | 2020-01-16 17:00:00 | 2020-04-21 11:30:00 | Fail | "Removal of the existing damaged components."Supply and installation of a new replacement sectional garage door, Thermofine: Fine ribbed-woodgrain insulated garage door Standard Colour: Jasper. 3 Clear square windows on two panels inc Grifco motor "Lifting equipment to be provided by Assa Abloy Entrance Systems"Test and check door operation."The above work is to be carried out during normal business hours.
MSA-DTAG | WA2903954 | Check alarms as location are incorrectly reported | Rockingham Justice Complex | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Jan 2020 | 2020-01-21 17:00:00 | 2020-01-30 15:30:00 | Fail | Site Audit and mapping of zones for courthouse maps and cjs maps. Rectified some points that weren’t reporting and plotted all on map.Created defect report for site to be emailed to PFM.
MSA-DCS | WA2926848 | unit 2 hut 61-66 dayroom vinyl flooring torn and worn out | Karnet Prison Farm | SPA-GR | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jan 2020 | 2020-01-23 17:00:00 | 2021-04-13 15:30:00 | Fail | FLOOR SHEETING REPLACED & NEW VINYL LAID
MSA-DCS | WA2927077 | Education 2- Fire strobe broken | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 16 Jan 2020 | 2020-01-21 17:00:00 | 2020-03-25 14:18:00 | Fail | Strobe replaced
MSA-DCS | WA2927216 | gate house, control room - perimeter PTZ camera are lagging | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Jan 2020 | 2020-01-21 17:00:00 | 2020-06-12 11:00:00 | Fail | Upgrade network from 10/100 fibre modems for communications link servicing unit 1, Health, Admin and security office back to the main comms room to 1Gbs TCP/IP Ethernet connection to core switch.
MSA-DCS | WA2927623 | BR Unit 1 B15 cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Jan 2020 | 2020-01-17 13:05:11 | 2020-01-17 14:15:00 | Fail | Attended site to replace the faulty cell call point in Unit 1 B15. Tested it ok after replacement. Please order one cell call point landscape type back to Hakea stock.
MSA-DTAG | WA2926693 | ground front windows-Appears someone has attempted to break in and multiple damages to window | Perth Children's Court | GMP-BR-HO | Building | Windows (BU) | O'Brien Glass With Care | 0 | CLOSE | 16 Jan 2020 | 2020-01-16 11:51:42 | 2020-02-17 14:15:00 | Fail | job completed - Reglazed & re-tinted
MSA-DTAG | WA2927869 | Lift - Some wiring is causing the lift to randomly fault, | Perth Children's Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 16 Jan 2020 | 2020-01-23 17:00:00 | 2020-01-17 12:00:00 | Pass | No costs associated with this work order
MSA-DTWD | WA2927354 | E Block, SK3 the upright double door fridge door seals are broken and falling off in places | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 2 | CLOSE | 16 Jan 2020 | 2020-01-21 17:00:00 | 2020-03-30 15:42:00 | Fail | Inspected door seals on all two door skope fridges serving E block. All fridge seals in good condition. Left supplied door seals in plant room onsite for future replacement.
MSA-DCS | WA2941812 | Unit 1, PA System is not working | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jan 2020 | 2020-01-18 09:51:01 | 2020-05-13 09:49:00 | Fail | this job will be completed under WA2989473
MSA-DCS | WA2942026 | Medical Suite cavity sliding doors inoperable | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jan 2020 | 2020-01-24 17:00:00 | 2020-04-17 09:30:00 | Fail | attended 17/4/20 to complete the repairs to the sliding track and doors as per our BRAF. Another company has replaced the track only and the doors are operable.
MSA-DFES | WA2962227 | Retrospective WO - Cleaner to attend Baldivis FS being used as Incident Control for recent fire. | DFES Baldivis | GMP-BR | Cleaning | Cleaning (CL) | CLEANDUSTRIAL CLEANING SERVICE | 3 | CLOSE | 17 Jan 2020 | 2020-01-24 17:00:00 | 2020-01-25 13:00:00 | Fail | Job completed Sunday 12th of January 2020. See attached email PDF
MSA-DTAG | WA2941686 | Custody Technician required for the inteface testing of mechanical services -see notes | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 17 Jan 2020 | 2020-01-24 17:00:00 | 2020-01-19 12:30:00 | Pass | During testing found changes had been made to mechanical shut offs need further investigation from installer of panel.
MSA-DTWD | WA2942119 | Admin BLD 832 - Various fluro’s faulty | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 17 Jan 2020 | 2020-01-22 17:00:00 | 2020-01-31 15:20:00 | Fail | job completed - replaced faulty fluros
MSA-DTWD | WA2942400 | T Block, level 2 , Male staff toilets, partially blocked, filling up and not draining completing | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Jan 2020 | 2020-01-22 17:00:00 | 2020-04-20 15:00:00 | Fail | replaced junction, re-routed branch
MSA-DTWD | WA2942445 | BLD 851, Freezer room - Faulty Freezer | Muresk Institute | GMP-BR | Refrigeration | Freezers (RE) | CDA Air & Solar | 3 | CLOSE | 17 Jan 2020 | 2020-01-24 17:00:00 | 2020-02-18 13:20:00 | Fail | 17/02/20 - Job Attendance (up to and including first half hour of labour) to check operation of faulty freezer. Our Tech replaced condenser fan motors. Tightened all flares/fittings and topped up with refrigerant
MSA-DCS | WA3082641 | Roof repair works to kitchen | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Main Kitchen | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 Jan 2020 | 2020-01-24 17:00:00 | 2020-04-15 08:44:00 | Fail | located leak and repaired
MSA-DCS | WA3082645 | Roof repair works to medical centre | Boronia Pre-release-AJ14 - Health and Education Centre | SPA-BR | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 Jan 2020 | 2020-01-24 17:00:00 | 2020-04-15 08:46:00 | Fail | located leak and repaired
MSA-DCS | WA2959606 | Unit 1, B & D Kitchen- Vinyl floor is lifting in several areas | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jan 2020 | 2020-01-28 17:00:00 | 2020-09-08 12:30:00 | Fail | damaged section of flooring replaced
MSA-DCS | WA2962311 | Education PDA sensor fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 20 Jan 2020 | 2020-01-20 13:30:19 | 2020-02-07 12:00:00 | Fail | Attended site. Checked report fault with MDAS. Found Transponder in EDU/W/S offline due to faulty Moxa adaptor. Supplied and replaced Moxa Nport device in Workshop. Reset the MDAS system. Tested operation.
MSA-DCS | WA2971213 | unit 8 house 5 and 8 corner doors in the kitchens are falling off-see notes | Bandyup Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Schlager Construction Group | 3 | CLOSE | 20 Jan 2020 | 2020-01-28 17:00:00 | 2020-02-14 14:30:00 | Fail | Supplied and installed new hinges to kitchen cabinets. Works carried out in units as directed by Steve Branson.
MSA-DCS | WA2971289 | Gatehouse, east - key to lock on anti ram device faulty/need to gain entry to avoid damage to | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 20 Jan 2020 | 2020-01-20 17:22:42 | 2020-06-01 13:00:00 | Fail | Installed new lock
MSA-DTAG | WA2959486 | Fire system check with Australian HVAC – please attend at 07.30am Thursday 23 January 2020 | Rockingham Justice Complex-Main Building-Ground Floor | GMP-BR-HO | Fire Protection Services | Smoke and Heat Detection (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 20 Jan 2020 | 2020-01-28 17:00:00 | 2020-01-23 11:36:00 | Pass | TECHNICIAN ATTENDED SITE, UNABLE TO GAIN ACCESS AT PRE-ARRANGED TIME, FINALLY GAINED ACCESS TO PROCEED WITH TESTING OF FIRE SIGNALS, BUT WAS ADVISED TO CANCEL TESTING AS THE VEHICLE HAD ARRIVED FOR COURT CUSTODY.
MSA-DCA | WA2972316 | internal Car operating panel inside lift car is bulging out, won’t click back into place-see notes | Swan Bell Tower-Main Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 2 | CLOSE | 21 Jan 2020 | 2020-01-24 17:00:00 | 2020-04-21 14:40:00 | Fail | Job completed - REPLACED CAR OPERATING PANEL AND CEILING LIGHTS
MSA-DCS | WA2972702 | unit 1 control air con not working | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 21 Jan 2020 | 2020-01-24 17:00:00 | 2020-07-30 14:06:00 | Fail | COMPLETED
MSA-DCS | WA2972710 | Cell call system is down | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Jan 2020 | 2020-01-21 19:54:06 | 2020-01-24 09:30:00 | Fail | Completed 100% cell call check. Most tested to YARD OFFICE some left to divert to GATEHOUSE. All ok except for BLOCK 3 CELL 2. New job required to repair.
MSA-MRWA | WA2972057 | L7 747 Light out please replace. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 21 Jan 2020 | 2020-01-22 17:00:00 | 2020-01-21 10:00:00 | Pass | Put light back in for the new occupant
MSA-DCS | WA2975449 | Entry control - the door entry door touch screen is starting to fail. | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Jan 2020 | 2020-01-22 14:34:27 | 2020-01-28 12:45:00 | Fail | Attended site and collected parts, replaced gatehouse monitor with new ELO touchscreen monitor from Hakea site spares. All replaced and tested ok. Job complete
MSA-DCS | WA2975454 | Entry control - Air con not working | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 22 Jan 2020 | 2020-01-23 10:37:15 | 2020-02-25 15:51:00 | Fail | COMPLETED
MSA-DCS | WA2975544 | Sewage plant – settlement dam over flowing | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | WATERCON - DO NOT USE********* | 1 | CLOSE | 22 Jan 2020 | 2020-01-23 10:50:16 | 2020-01-22 15:00:00 | Pass | Removed blockage
MSA-DCA | WA2976819 | throughout buildiing Several Emergency lights are non-functional on the Nexus system -see notes | State Theatre Centre (Heath Ledger Theatre)-Main Building | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 23 Jan 2020 | 2020-01-24 17:00:00 | 2020-03-10 10:00:00 | Fail | Arrived on site and spoke with graham about the nexus system then proceeded to go through the faults, Graham had informed me that in the middle of a performance the emergency light fittings underwent a automatic test, he came and stopped shut off the test half way through. We need to re run a test between 12-7am, to properly identify which fittings have a fault, then we can look into replacing those fittings. The nexus system currently has version 4.2.3, with the latest version being 4.3.1. With the latest version required to program these test I called up ABB and had the file emailed to me, we downloaded the file to a USB and went to update the system. The PC that has the nexus system on it is currently running an old version of windows, that can’t run the program to update the nexus system. I spoke to graham about this who informed me that they are currently in talk of upgrading every windows pc in the building. I am waiting for his call on the next step. The computer that has the
MSA-DCA | WA2977535 | Lift emergency phone not operating | DO NOT USE - TO BE DECOMMISSIONED Collection & Research Centre Welshpool-Harry Butler Centre-Ground Floor - Lift - PFM ID 011 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 23 Jan 2020 | 2020-01-29 17:00:00 | 2020-01-24 13:30:00 | Pass | No costs associated with this work order
MSA-DCS | WA2977054 | health turning circle driveway main retaining wall has a large cracked | Bandyup Prison | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | Schlager Construction Group | 2 | CLOSE | 23 Jan 2020 | 2020-01-29 17:00:00 | 2020-06-26 11:30:00 | Fail | Carried out repairs to the turning circle driveway retaining wall as per quotation.
MSA-DCS | WA2977061 | salon main air con not working roof mounted evap to main salon | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 23 Jan 2020 | 2020-01-29 17:00:00 | 2020-05-19 08:11:00 | Fail | Arrived to site and gained access to roof safely.Replaced Flexible connection which had perished from sun damage.Replaced parts as per BRAF.Works now completed.Duct layout on roof is showing signs of age with rust taking starting to take over from the inside out.Quoting for reverse cycle system to be installed to the area as it currently has no means of heating.
MSA-DCS | WA2977266 | Unit 10, SO & Wing office- Carpet is damaged SITE COSTED | Hakea Prison | WSM-BR-SITE | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Jan 2020 | 2020-01-31 17:00:00 | 2020-04-02 18:30:00 | Fail | Office was not emptied out as arranged and required for job to proceed. Prison to report job in the future when they can allow access. Closing with costs to date as advised by Grant Byrne.
MSA-DCS | WA2977276 | East side walkway, from video link to unit 6/7 entrance gate- repair holes in concrete | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Concreting (PR) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Jan 2020 | 2020-01-31 17:00:00 | 2020-09-22 14:45:00 | Fail | ATTENDED 30/01 - TO ASSESS AND MEASURE UP JOB/ORDER MATERIALSSITE BEING DIFFICULT WITH GAINING ACCESSSITE EVENTUALLY TOLD US TO CANCEL JOB - NO FURTHER REPAIRS/ACTION TAKEN
MSA-DCS | WA2977550 | Unit 6 Cell 8, 13 & 16 viewing hatch covers are broken | Bandyup Prison | GMP-BR- HO | Carpentry | Materials (CA) | Schlager Construction Group | 2 | CLOSE | 23 Jan 2020 | 2020-01-29 17:00:00 | 2020-03-30 15:30:00 | Fail | Attended site and measured cell door viewing panels to be replaced.Fabricated new viewing panels.Attended site and installed new cell door viewing panels.
MSA-DTWD | WA2976916 | U block, eastside, outside of U017 - 2x uneven areas of paving outside. | Balga Campus | GMP-BR | Paving & Roadworks | Paving (PR) | M Construction (WA) | 2 | CLOSE | 23 Jan 2020 | 2020-01-29 17:00:00 | 2020-05-06 08:37:00 | Fail | Job complete
MSA-DTWD | WA2977544 | BLD 825 room 5 Faulty Smoke alarm | Muresk Institute | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 23 Jan 2020 | 2020-01-29 17:00:00 | 2020-01-24 15:30:00 | Pass | Replaced smoke alarm
MSA-DTWD | WA2977559 | BLD 851 freezer room Temperature fault | Muresk Institute | GMP-BR | Refrigeration | Freezers (RE) | CDA Air & Solar | 2 | CLOSE | 23 Jan 2020 | 2020-01-29 17:00:00 | 2020-02-18 13:14:00 | Fail | 17/02/20 - Job Attendance (up to and including first half hour of labour) to check operation of faulty freezer. Our Tech replaced condenser fan motors. Tightened all flares/fittings and topped up with refrigerant
MSA-DTWD | WA2978712 | A Block, 3 x Awnings ripped and damaged | Fremantle Campus (formerly WA Maritime) | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 24 Jan 2020 | 2020-02-03 17:00:00 | 2020-03-19 13:33:00 | Fail | Supplied and installed new awnings
MSA-DTWD | WA2978843 | BLD 823 Hallway - faulty smoke alarm | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 24 Jan 2020 | 2020-01-30 17:00:00 | 2020-01-24 16:30:00 | Pass | Job completed - Replaced smoke alarm
MSA-DTWD | WA2978889 | Lift F20 store room L1 doors are not closing-Please attend Tuesday | West One Services | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 2 | CLOSE | 24 Jan 2020 | 2020-01-30 17:00:00 | 2020-02-07 10:15:00 | Fail | Upon arrival at site, the technician performed the following:DOORS/ENTRANCES - HANGER ROLLERS - COMPONENT REPLACED
MSA-DCS | WA2979837 | Kaartdijin Mia - early detection unit on the roof of learning centre damaged | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Jan 2020 | 2020-01-28 12:10:01 | 2020-03-13 14:50:00 | Fail | No further works req from Seme
MSA-DCS | WA2979842 | Kaartdijin Mia - razor wire and supports damaged on learning centre roof, needs repairs | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 28 Jan 2020 | 2020-01-28 12:21:25 | 2020-03-13 16:00:00 | Fail | 28/01/20Workshop loaded truck.Personnel inspected & assessed damage on site.Works needs to be planned with security. Was not authorised to start work on day work order was issued.12/03/20 to 13/03/20Removed razor wire off roof. Removed detection off roof. Repaired holes in roof with silicone. Secured new support cages with huck rivets every 250mm.Installed 3 rows of razor wire in a tringle formation.Demob from site.
MSA-DCS | WA2980289 | BR - Front gate, random search blue light us not working properly | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Jan 2020 | 2020-01-29 09:49:56 | 2020-02-04 16:29:00 | Fail | Investigated random search alarm and found occasionally it won't reset. Will investigate programming.
MSA-DTAG | WA2980066 | Sat camera's down no visual in DMJC control room-L4 cannot open any doors | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 28 Jan 2020 | 2020-01-28 12:57:26 | 2020-03-27 10:00:00 | Fail | Repairs to camera's
MSA-DCA | WA2981923 | Humidity alarms as per below | Art Gallery of WA - James St-Administration Block (Block A)-Level One-AB1.04A - Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 29 Jan 2020 | 2020-01-30 17:00:00 | 2020-02-28 10:55:00 | Fail | See logs.
MSA-DCS | WA2981981 | Admin- Hole in wall in video link phone booth | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jan 2020 | 2020-02-03 17:00:00 | 2020-07-14 14:50:00 | Fail | PATCH UP HOLE WITH ALUMIN PLATE
MSA-DCS | WA2982133 | Unit 2, B & D Day Room- Floor tiles have large bubble | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 Jan 2020 | 2020-02-05 17:00:00 | 2020-06-30 12:30:00 | Fail | DAMAGED FLOORING REMOVED / REPLACED
MSA-DCS | WA2982176 | Laundry, Water fountain is not getting cold | Hakea Prison | WSM-BR-SITE | Refrigeration | Chiller (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 29 Jan 2020 | 2020-02-03 17:00:00 | 2020-03-05 15:30:00 | Fail | Water cooler replaced. All ok
MSA-DCS | WA2982207 | Camera 048 & 049 PTZ north fuzzy & no zoom | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jan 2020 | 2020-01-30 10:41:13 | 2020-03-25 15:14:00 | Fail | Camera 49 type : analog palco ptz
MSA-DCS | WA2982542 | western side of training centre fire mains doors broken hinges | Hakea Prison | SPA-GR | Building | Fire Door (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 Jan 2020 | 2020-01-30 12:55:40 | 2020-03-25 14:00:00 | Fail | repaired door and frame
MSA-DCS | WA2982825 | Inner Perimeter - Zone IDF-F1 in fault | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Jan 2020 | 2020-02-03 17:00:00 | 2020-03-26 08:46:00 | Fail | Zone F1 roof / fence detection not being reinstated as per site instructionNo further works by SEME
MSA-DTAG | WA2982261 | L4 comms room Security Switch has failed Please procure and install new switch-see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 29 Jan 2020 | 2020-01-29 14:52:25 | 2020-05-04 18:00:00 | Fail | job completed - Restarted Cisco switch and got network up and running.
MSA-DTWD | WA2982120 | L Block, Cool Rooms not getting down to temperature | Murdoch Campus | GMP-BR | Refrigeration | Coolroom (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 29 Jan 2020 | 2020-02-03 17:00:00 | 2020-03-09 14:29:00 | Fail | FOUND UNIT SHORT CYCLING, SYSTEM IS SHORT REFRIGERRANT. ISLOATED AND PERFORMED A LEAK TEST WITH NITOGREN. FOUND SMALL LEAK ON TX VALVE FLARE NUT. ALSO SOE SEAGE OF OIL UNDER THE SHAFT SEAL AS THE UNIT IS 20 YEARS OLD AND ON R22 IT IS RECOMMENDED THAT WE REPLACE THE UNIT. BRAF TO BE SUBMITTED.
MSA-DTWD | WA2982139 | E block, ET13 - split system A/C is leaking water may be icing up | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 29 Jan 2020 | 2020-02-03 17:00:00 | 2020-03-26 12:54:00 | Fail | ATTENDED SITE, FOUND A/C LEAKING WATER. FOUND DRAIN TRAY AND DRAIN TRAY INSULATION FAULTY. INDOOR FAN COIL UNIT DRIP TRAY REQUIRES REPLACING OR THE INDOOR TO BE REPLACED IF INSULATION WORN. PRICE TO BE SUBMITTED. SIMON PRICING UP PARTS
MSA-DTWD | WA2982406 | sth block server room Hire of temporary server room a/c for 01 to 29th Feb 2020 | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 29 Jan 2020 | 2020-02-05 17:00:00 | 2020-02-29 17:00:00 | Fail | WO was raised for portable cooler hire for the month of February
MSA-DCS | WA2983367 | Unit 6, Cell C2- cistern is faulty | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Jan 2020 | 2020-01-31 07:54:25 | 2020-01-31 10:00:00 | Fail | COMPLETED
MSA-DCS | WA2984610 | Transponders are down education are & Visits area - Commication failure | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 30 Jan 2020 | 2020-01-30 18:55:59 | 2020-02-07 18:00:00 | Fail | Removed defected Moxa unit and installed new. Programmed and tested. Issue still apparent. Installednew transponder and tested. Issue still apparent. Re-installed old transponder. Factory reset Moxa and programmedagain.Rebooted nPort hub and tested. Unit online and functioning correctly. Unsure why unit would not take settings first timearound.
MSA-DTAG | WA2983731 | Interview room 3.1 - Digital door handle slides off – grub screw thread is worn | Central Law Courts-Main Building-Level 3 | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 30 Jan 2020 | 2020-01-31 17:00:00 | 2020-01-30 13:00:00 | Pass | repairs to lock
MSA-DTAG | WA2984279 | Level 3 – Female public toilet is blocked. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Jan 2020 | 2020-01-31 17:00:00 | 2020-01-31 11:00:00 | Pass | Complete
MSA-DTAG | WA2984616 | CCTV Room - Moinitor 4 has failed | Supreme Court-Supreme Court Building-Basement | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 30 Jan 2020 | 2020-01-31 17:00:00 | 2020-04-09 08:00:00 | Fail | new work station installed
MSA-DTWD | WA2983683 | H Block, Creche H2- Air Con is not working | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 30 Jan 2020 | 2020-02-04 17:00:00 | 2020-02-24 16:30:00 | Fail | Completed by contractor
MSA-DTWD | WA2983757 | Nursey back door is not latching closed | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 30 Jan 2020 | 2020-02-04 17:00:00 | 2020-02-03 09:05:00 | Pass | Replaced faulty lock
MSA-DTWD | WA2983855 | L Block, Ground- Lift is not working | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 30 Jan 2020 | 2020-02-04 17:00:00 | 2020-01-31 12:00:00 | Pass | Not chargeable
MSA-DTWD | WA2984535 | U block Repair brick paving on the east end of U Block | Balga Campus | GMP-BR | Paving & Roadworks | Paving (PR) | M Construction (WA) | 3 | CLOSE | 30 Jan 2020 | 2020-02-06 17:00:00 | 2020-05-06 08:41:00 | Fail | Job complete
MSA-MRWA | WA2984590 | Basement carpark-Multiple lights out within the carpark area, please replace as required. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | CLOSE | 30 Jan 2020 | 2020-02-06 17:00:00 | 2020-02-06 11:30:00 | Pass | Replaced multiple lights in car park and bike area
MSA-DFES | WA2985886 | Applied Training Ground Replace or repair cracked drain lid cover near boom gate-see notes | FESA RHQ - Forrestfield | GMP-BR | Building | Steel Work (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 31 Jan 2020 | 2020-02-07 17:00:00 | 2020-05-01 13:40:00 | Fail | Works are now completed - New cover is installed
MSA-DCS | WA2989473 | Gate control PA system is not working | Albany Regional Prison-Gatehouse | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Feb 2020 | 2020-02-05 17:00:00 | 2020-08-19 19:45:00 | Fail | PA in all the units works correctly.Obsolete equipments in unit Education gatehouse and unit 2.No PA all call from gate house as built in panel has failed, old maxprp system.
MSA-DCS | WA2989906 | unit 2 cell C4 key stuck in lock | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 03 Feb 2020 | 2020-02-03 11:50:52 | 2020-02-03 11:10:00 | Pass | job completed - replaced lock
MSA-DCS | WA2989916 | Security Area- Visits room camera NE requires to be re connected. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Feb 2020 | 2020-02-05 17:00:00 | 2020-02-13 09:30:00 | Fail | Replaced failed a PTZ Camera, configured settings for operation and confirmed video and recording.
MSA-DCS | WA2990744 | Old control / sallyport office-2 x light switches damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Feb 2020 | 2020-02-10 17:00:00 | 2020-02-11 15:50:00 | Fail | Control for the old sallyport lights was on the computer in the old control room. Now that the computer has been moved to the new control room there is no local control of the lights. As it is controlled by the computer it may be prudent get SEME to fit new control switches for the lights as they will have to interact with the computer system.
MSA-DCS | WA2991007 | Entire site - has no water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 03 Feb 2020 | 2020-02-03 20:42:29 | 2020-02-04 04:00:00 | Fail | 3/2/20 - investigated cause of fault. Reset Vsd controller which had an overheating alarm. Bought system back up to operating pressure. Checked water supply in units. Recommended to Chris (AHS), that Helwig elec or similar would be required for further investigation.4/2/20 - Vsd controller overheated again due to exhaust fan in Vsd faulty. Temp fan set up to cool unit until Helwig elec can repair. Pump sequence change to reduce load on Vsd with help of Helwig elec. Dave from Helwig said he is going to rectify the elec issue.
MSA-DFES | WA2990971 | Engine Room Front Door for light tanker will not close | CFRS Claremont | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 03 Feb 2020 | 2020-02-04 17:00:00 | 2020-02-04 12:00:00 | Pass | bi-fold door 1 & 2 safety edge strip keeps activating when comes down try to adjust but no success. So technician took bump edge strips out of use so doors can be secured. Quotation for high safety beams was submitted.
MSA-DTAG | WA2990666 | Level 2A- Water dripping through Registry ceiling space | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 03 Feb 2020 | 2020-02-06 17:00:00 | 2020-02-03 14:30:00 | Pass | Techs to return to change pipe and couplers also fittings to fix leak
MSA-DTWD | WA2990798 | A Block, Female Toilet is leaking on floor | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Feb 2020 | 2020-02-06 17:00:00 | 2020-04-16 12:30:00 | Fail | Complete
MSA-DTWD | WA2990802 | A & C Block - Chillers have gone out | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 0 | CLOSE | 03 Feb 2020 | 2020-02-03 17:22:03 | 2020-02-05 16:00:00 | Fail | Arrived on site, Found chillers running but had a fault earlier in the day for the dp switch meaning there was air in the system Found the water inket turned off , cant find out why this was turned offBled system and running well
MSA-DCS | WA2991303 | Unit 8, Cell B6- Vinyl has split and metal flooring | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 04 Feb 2020 | 2020-02-07 17:00:00 | 2020-05-29 09:45:00 | Fail | Closing with costs to date, LVM being issued to complete repairs
MSA-DCS | WA2991307 | Unit 9, Cell C13- vinyl is damaged | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 Feb 2020 | 2020-02-11 17:00:00 | 2020-09-07 14:35:00 | Fail | replaced damaged vinyl
MSA-DCS | WA2991309 | Unit 9, Cell D5- vinyl damaged | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 Feb 2020 | 2020-02-11 17:00:00 | 2020-07-17 12:38:00 | Fail | UPLIFT AREAS X4 SUPPLIED AND INSTALLED NEW VINYL
MSA-DCS | WA2991583 | Gym- light on pole in front of gym damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Feb 2020 | 2020-02-07 17:00:00 | 2020-03-24 17:00:00 | Fail | Replaced damaged pole light outside gym
MSA-DCS | WA2992033 | Unit 4 - C Wing Grille - Lock bottom screw is stripped out | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Feb 2020 | 2020-02-05 12:52:48 | 2020-02-05 10:30:00 | Pass | modified lock box to secure lock correctly.
MSA-DCS | WA2993771 | Unit 4 - lock has fallen out of Medication trolley | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Feb 2020 | 2020-02-05 16:31:49 | 2020-02-05 11:45:00 | Pass | Job completed - serviced padlock
MSA-DTAG | WA2993588 | Registry/AC Room HPWU unit 3 faulting | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 04 Feb 2020 | 2020-02-07 17:00:00 | 2020-03-23 12:00:00 | Fail | Attend site. Access roof and confirm unit isolation. Disconnect wiring to presdure transmitter. Unscrew transmitter from suction pipe. Schrader depressor appeared to be in good condition with no leaks. Fit new transmitter to suction pipe and tighten. Check for leaks, no leaks found. Deisolate and check pressure on unit display. Connect guages to confirm correct pressure. Pressure confirmed to be ok. Check operation of unit, working ok.
MSA-DTWD | WA2991832 | Block 8, toilets faulty exhaust fans | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 1 | CLOSE | 04 Feb 2020 | 2020-02-05 17:00:00 | 2020-04-20 08:00:00 | Fail | Found to be a BMS issue. IT department working on it.
MSA-DTWD | WA2992848 | D block level G entrance foyer FCU 2 in fault no airconditioning | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 04 Feb 2020 | 2020-02-05 17:00:00 | 2020-04-14 09:00:00 | Fail | Attended site, set up barricades and completed jsa, acccessed ceiling and found fan to be running but slowly and motor was very hot, needs replacing , quote submitted. 30.3.20: Attended site. Gained access to FCU 2. Removed faulty fan motor from fan deck. Installed new motor and capacitor to fan deck. Installed fan deck into FCU 2. Re energised power supply to unit. Checked system operation. Fault still present on BMS. Checked flow switch. Flow switch closed. Tried to reset fault. Fault still present. Unit enabled and running. Will see if fault clears with proper start sequence from BMS in the morning. If not may be a fault with BMS controller.
MSA-DTWD | WA2993586 | E & S Block- Aircon to E105A Theaterrte and S121 not working | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 04 Feb 2020 | 2020-02-07 17:00:00 | 2020-03-26 10:55:00 | Fail | Portable units removed from site
MSA-DTWD | WA2993716 | T,U & V Block- sewerage pump controller in alarm | Rockingham Campus | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 04 Feb 2020 | 2020-02-05 17:00:00 | 2020-02-08 16:00:00 | Fail | replaced faulty probe
MSA-DTWD | WA2993719 | U Block - Air cons in U009, U010 and U017 are all blowing hot air | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 04 Feb 2020 | 2020-02-07 17:00:00 | 2020-03-24 13:00:00 | Fail | Attended site, set up boom lift to lift motors up and down,fitted new motors and all parts to appropriate systems. Replaced motor,belt and water solinoid on 0081875.replaced motor and belt on 00821503.replaced float valve on 00594306.replaced pads on 00594308.replaced water pump on u2/ec7.tested all systems and left operational
MSA-DCA | WA2995028 | Fire Hose reel near lunchroom in warehouse is leaking water. | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Lunchroom | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Critical Fire Protection & Training | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 17:00:00 | 2020-02-06 12:34:00 | Pass | Fire hose reel near lunchroom in warehouse is leaking waterstaff have attempted to release and reset nozzle however leak remainsFire hose reel needed to be replaced with new
MSA-DCS | WA2994206 | education GUTTER LEAKING WATER ON TO RAMP | Karnet Prison Farm | GMP-BR- HO | Roofing | Guttering (RF) | AFD Contracting | 3 | CLOSE | 05 Feb 2020 | 2020-02-11 17:00:00 | 2020-05-05 13:00:00 | Fail | 05/05/20Re rivet and seal gutter over education
MSA-DCS | WA2994311 | unit 4 D4 vinyl is damaged | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 05 Feb 2020 | 2020-02-12 17:00:00 | 2020-10-12 10:30:00 | Fail | new flooring in stalled
MSA-DCS | WA2994519 | Unit 13, B & D wing - Vesda Fire units in constant fault in B/D wing between cells 01/02 & 13/14 | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 09:52:59 | 2020-06-05 20:32:08 | Fail
MSA-DCS | WA2994614 | Yeed B wing lock to fire hose cpboard faulty (YCO) unable to open | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 05 Feb 2020 | 2020-02-10 17:00:00 | 2020-02-20 09:30:00 | Fail | Job completed - open cupboard door alarm read with was obstructing door relocate switch
MSA-DCS | WA2994827 | Workshop area - MDIS transponer 6 is offline and requires repair. | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 05 Feb 2020 | 2020-02-10 17:00:00 | 2020-02-24 17:00:00 | Fail | Investigated fault, replaced with site spare fiber modem, still not communicating, replaced Transponder with new Transponder, site spare used. All replaced and tested ok for correct operation, tested duress buttons with 1 x technician in the control room. All duress buttons tested and showing correct locations. Job complete
MSA-DCS | WA2994829 | MSS unit P.E expanders are offline. | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 05 Feb 2020 | 2020-02-10 17:00:00 | 2020-02-24 16:00:00 | Fail | Attended site and investigated fault. Found expanders all offline. Reset power and still had expanders offline. Installed new 16 in out board, reprogrammed board and powered up. Retested for correct operation and all tested ok. Job complete
MSA-DCS | WA2995029 | gate house zone 3 omni trax im constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 14:28:44 | 2020-04-29 07:54:00 | Fail | Investigated fence, found cable reading infinite resistance, this indicates a cable fault. Temporarily modified hardware to restore limited function. Requires splice kits and cable replacement.28/4. L.Walkerden M Cavanagh Found broken coupler ,rectified , checked cable resistance , walk tested and confirmed ok
MSA-DCS | WA2995030 | gate house zone 9 omni trax constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 14:31:25 | 2020-02-14 17:45:00 | Fail | Attended site.Found damaged splice kit on outer microphonics in zone 9.Replaced with new (supplied by SEME) and checked EOL - 1MOhm.Conducted test.All back to normal and operational
MSA-DCS | WA2995034 | zone 10 IM constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 14:33:47 | 2020-04-29 07:59:00 | Fail | Investigated fence, found resistance fluctuating between 53 and 56K ohms, this indicates a cable fault. Requires splice kits and cable replacement.28/04/20. L Walkerden M Cavanagh found broken connector after walking perimeter , rectified , tested and verified with control office. Tested ok
MSA-DFES | WA2995086 | The wall between the bathroom shower and bedroom 8 appears to have substantial water damage | CFRS Perth- Perth FS-Accommodation | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 05 Feb 2020 | 2020-02-10 17:00:00 | 2020-04-08 12:00:00 | Fail | Remove old silicone from tiles and re silicone, patch and reapint wall and skirting
MSA-DTAG | WA2995078 | Air flow is low in JSO office – please check DD3.43 & DD 3.42 | Central Law Courts-Main Building-Level 3 | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 05 Feb 2020 | 2020-02-10 17:00:00 | 2020-04-01 16:00:00 | Fail | Attend site with icon logic. Carry out controller replacement. Reprogram new controller and commission operatiom
MSA-DTWD | WA2994370 | ground Tic controller faulty not running all the stations and has a broken door cover | Joondalup Kendrew Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 17:00:00 | 2020-02-18 09:00:00 | Fail | Attended site and replaced faulty door hinge. Went to install irrigation controller, however not suitable due to number of solenoids per station.Job cancelled by Sean McGrath.
MSA-DTWD | WA2994455 | C Block, Room CG06- Broken window | Carlisle Campus | GMP-BR | Glazing | Window Glass (GL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 05 Feb 2020 | 2020-02-10 17:00:00 | 2020-03-25 14:00:00 | Fail | Replaced damaged window pane
MSA-DTWD | WA2994562 | C Block, Room CF3- Door Lock is faulty | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Locksmith (SE) | GRONBEK SECURITY | 2 | CLOSE | 05 Feb 2020 | 2020-02-10 17:00:00 | 2020-02-19 12:00:00 | Fail | Remove and replace cylinder - C BLock, Room CF3.
MSA-DTWD | WA2994590 | D block D206 noisy fan motor | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | Precise Air Group | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 17:00:00 | 2020-03-20 16:00:00 | Fail | Picked up required parts,attended site and set up barricades, isolated hx2 and tagged out. Removed ceiling tiles to access motor,removed faulty motor and replaced with new,wired motor into system and tested.cleaned up work site and checked bms system for correct operation
MSA-MRWA | WA2994575 | L7 Corridor near 729 Emergency light out, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 17:00:00 | 2020-02-06 09:45:00 | Pass | Replaced globe with new
MSA-MRWA | WA2995082 | Level 6, Room 6.103- Install monitor arms | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 1 | CLOSE | 05 Feb 2020 | 2020-02-06 17:00:00 | 2020-02-07 14:31:00 | Fail | Fit arms to desk
MSA-DCS | WA2995844 | Unit 2, A wing yard door - door needs repairing, wooden door damage near the lock affecting the lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 06 Feb 2020 | 2020-02-07 11:01:33 | 2020-02-26 13:15:00 | Fail | Job completed - Attend site, measure and quote replacement door. Return to site supply and install replacement door as quoted.
MSA-DCS | WA2995857 | Laundry - Number 3 washing machine has a noisy baring | Hakea Prison | SPA-BR | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 06 Feb 2020 | 2020-02-07 11:06:28 | 2020-05-22 11:55:00 | Fail | Work completed as per BRAF
MSA-DCS | WA2996099 | Boiler house - #2 compressor not running. | Hakea Prison | GMP-BR- HO | Building | General Building (BU) | CLEVELAND COMPRESSED AIR SERVICES | 2 | CLOSE | 06 Feb 2020 | 2020-02-11 17:00:00 | 2020-02-13 15:00:00 | Fail | Supply repairs on Atlas Copco LE75-10UV Piston compressor Boiler house - #2 compressor not runningInvestigate on 14/2/20
MSA-DCS | WA2996128 | ISU, C Wing, Cell C01- Cell Call not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Feb 2020 | 2020-02-11 17:00:00 | 2020-03-26 09:00:00 | Fail | Rectified and fixed cell call ISU C1, job completed.
MSA-DFES | WA2996324 | Station Officers Office - Water leaking through ceiling adjacent to air conditioner outlet | CFRS Vincent | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 06 Feb 2020 | 2020-02-11 17:00:00 | 2020-05-01 16:45:00 | Fail | Sanded and painted ceiling after aircon issues was fixed
MSA-DTAG | WA2995325 | Lift 3 can travel to the basement without swiping ID card/security issue - see notes | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 06 Feb 2020 | 2020-02-10 17:00:00 | 2020-02-06 15:26:00 | Pass | Security not working. Found JKBL key switch not wired correctly, re wired and tested. Working correctly
MSA-DTAG | WA2995459 | Court One and Lunch room-The air-conditioning unit appears to not be cooling -see notes | Joondalup Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 06 Feb 2020 | 2020-02-11 17:00:00 | 2020-04-18 12:30:00 | Fail | Works completed.
MSA-DTWD | WA2995831 | L2 lift area switch board cupboard lock broken | West One Services | GMP-BR | Security | Locksmith (SE) | DIAMOND LOCK AND KEY | 0 | FLDCOMP | 06 Feb 2020 | 2020-02-06 14:56:37 | 2020-02-06 11:45:00 | Pass | Date of Attendance: 06/02/20Locksmith completed the following :Attended site as requested. Opened electrical cupboard. Latch had too much load on it because doors were not closing properly. Doors rubbing on carpet and rebated doors not joining correctly in the middle. Need a carpenter to trim the doors and re-hang.
MSA-MRWA | WA2995525 | Lvl 7, Room 721- Lights flickering please remdiate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 06 Feb 2020 | 2020-02-07 17:00:00 | 2020-02-07 10:55:00 | Pass | Replaced globe with new
MSA-MRWA | WA2996306 | Access control not arming | Materials Engineering Branch | GMP-BR | Security | Access Control (SE) | Siemens Ltd | 1 | CLOSE | 06 Feb 2020 | 2020-02-07 17:00:00 | 2020-02-07 13:15:00 | Pass | Removed the door point from the alarm system so it cant cause a problem when the alarm is signed.
MSA-DCA | WA2997122 | Lift number 5 - stuck on ground floor - doors open no occupants | State Library of WA-Main Building-Ground Floor-GF15 - Van Dock | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 07 Feb 2020 | 2020-02-07 14:53:10 | 2020-02-07 12:00:00 | Pass | Not charegable
MSA-DCS | WA2996639 | Unit 2 cell D5 damaged vinyl | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Feb 2020 | 2020-02-13 17:00:00 | 2020-05-22 10:00:00 | Fail | Found the repairs have been completed on a different job number
MSA-DCS | WA2996643 | Unit 2 cell D7 damaged vinyl | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Feb 2020 | 2020-02-13 17:00:00 | 2020-09-07 14:58:00 | Fail | UPLIFTED THEN REPLACED DAMAGED VINYL AREAS
MSA-DCS | WA2996645 | Unit 2 cell D12 damaged vinyl | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Feb 2020 | 2020-02-13 17:00:00 | 2020-11-11 14:30:00 | Fail | DAMAGED SECTION OF FLOOR UPLIFTED/ REPLACED
MSA-DCS | WA2996652 | Unit 2 D wing passage day room vinyl damaged | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Feb 2020 | 2020-02-13 17:00:00 | 2020-10-08 13:24:00 | Fail | SUPPLY AND INSTALLED NEW VINYL FLOORING TO AREA X3 - REPAIRED CONCRETE
MSA-DCS | WA2997278 | kitchen rationale oven door has been smashed by trolley | Casuarina Prison | SPA-BR | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 07 Feb 2020 | 2020-02-08 11:49:32 | 2020-03-11 10:00:00 | Fail | Replace Broken Door on Rational oven no 1
MSA-DCS | WA2997427 | sewerage plant allun pump not working | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | WATERCON - DO NOT USE********* | 1 | CLOSE | 07 Feb 2020 | 2020-02-08 13:47:13 | 2020-02-08 15:00:00 | Fail | Watercon employee attended site 08/02/2020 - Priority 1Replaced dosing pump with spare pump in stock. Set up dosing plant and tested - all okay.
MSA-DTAG | WA2997237 | Entry Foyer - Buzzing sound for 15 seconds every half an hour emanating from ceiling above the doors | Armadale Courthouse-Main Building-Ground Floor | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 07 Feb 2020 | 2020-02-12 17:00:00 | 2020-05-27 14:30:00 | Fail | Found battery back up dead causing door to alarm, replaced dead battery’s and checked over unit, found track wheels heavily worn and require replacement, quote to replace 4x standard track wheels, 2x techs required for safe works. Braf being raisedReturned 27/5 - Replaced x4 track wheels as per work order, adjusted door gap to suit.
MSA-DTAG | WA2997499 | Main entrance - Technician required to attend Saturday 8 Feb from 07.00am until approx 16.30pm | Central Law Courts-Main Building | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 07 Feb 2020 | 2020-02-12 17:00:00 | 2020-02-08 14:00:00 | Pass | Isolations and alarms for mech service testing
MSA-DTWD | WA2996838 | F41 check AC is cooling properly | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 07 Feb 2020 | 2020-02-12 17:00:00 | 2020-02-24 16:30:00 | Fail | Install Completed by contractor
MSA-DTWD | WA2996841 | J block check 2 evaps are working properly | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 07 Feb 2020 | 2020-02-12 17:00:00 | 2020-03-16 14:19:00 | Fail | ATTENDED SITE AND SIGNED IN. COMPLETED SAFETY CHECK AND ACCESSED UNIT. FOUND UNIT HAS FAULTY WATER PUMP AND REQUIRES NEW PADS. BRAF TO BE SUBMITTEDTRAVELED TO WHOLESALERS AND COLLECTED PARTS . TRAVELED TO SITE AND SIGNED IN AT ADMINISTRATION. LOCATED EVAP COOLERON J BLOCK AND COMPLETED QUOTED WORKS AS PER SCHEDULE. DISPOSED OF OLD PARTS AT THE TIP. ASSISTED BY GREG OTTIVIANO.ASSISTED ANDY
MSA-DTWD | WA2997469 | Plant Room 1, Water Tower- recirculation pump has failed | West One Services | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 07 Feb 2020 | 2020-02-12 17:00:00 | 2020-03-24 11:27:00 | Fail | Arrived on site, inspected pump, pump siezed, quoted replacement for pump Arrived on site, completed jsa and safety, removed fittings from pump , replaced pump , tested and running well
MSA-DCS | WA2997596 | fire alarm node 3 M1-12-industries SPK LPSW-valve is faulty | Casuarina Prison-Industries | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 08 Feb 2020 | 2020-02-08 09:55:50 | 2020-03-12 13:02:00 | Fail | Casuarina Prison.Called for low pressure alarm, found 2x with low pressure, 1 @ 1000kpa and 1 @ 925kpa.Jacked both system back up to 1200kpa. Unable to clear low pressure alarm on FIP. Pressure switch will need to be replaced.Revisit required.Client signed uptick on phone.04-03-20Arrived on siteInvestigated low pressure switchAlso pumped up sprinkler system pressure and tried to reset but was unable , then went to change out pressure switch but was told we hadrun out of time , have had to leave as we found with low pressure still in alarm , will need to return to site at another date to complete repair12/3/20Attended site and fitted two new low pressure switches to old boiler house valve set adjusted and tested ok.
MSA-DCS | WA2997786 | Unit 12 - Cell B10 - Cell door is sticking and hard to open | Melaleuca Prison | GMP-BR- HO | Carpentry | Materials (CA) | Schlager Construction Group | 2 | CLOSE | 08 Feb 2020 | 2020-02-12 17:00:00 | 2020-02-25 11:30:00 | Fail | 13/02/20ttended site and removed damaged mortice lock cell 10 door that needed replacing.14/02/20Picked up new mortice lock from Barnett Architectural Hardware contacted prison for access told to contact bookings. Access booked for 25/02/2020.25/02/2020Re attended site to fit new mortice lock and on inspection noticed it had all ready been replaced by another contractor.
MSA-DCS | WA2997788 | Unit 11 - A & B wing - Toilet roll holder has come off | Melaleuca Prison | GMP-BR- HO | Carpentry | Materials (CA) | Schlager Construction Group | 2 | CLOSE | 08 Feb 2020 | 2020-02-12 17:00:00 | 2020-07-01 12:30:00 | Fail | Removed damaged toilet roll holder from wall.Carry out repairs to toilet roll holder.Refit toilet roll holder to wall.
MSA-DCS | WA2997854 | Perimeter detection- PE beam not detecting | Roebourne Regional Prison | WSM-BR-RC | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Feb 2020 | 2020-02-09 14:21:11 | 2020-04-07 14:49:00 | Fail | Zone 2 both sets have had the bracket realigned Zone 3 beam TX has had the stack replaced Zone 4 beam top hat and tamper switch have been replaced Zone 5 beam stacks have had the brackets realigned Zone 7 beams stacks have had the brackets realigned Zone 8 beams stacks have had the brackets realignedZone 13 beam stack has been replaced Zone 14 beam stack has been replaced Zone 15 beam stack has been replacedZone 16&17 beam stacks have had the bracket realigned Both beam sets in Zone 18 have had the stacks replacedZone 19 beam stack has been replaced Zone 17 PE has been realigned and working correctly Zone 22 Pe beam has had the tamper replacedZone 13 TX has be repairedZone 4 TX has had the tamper replaced
MSA-DCS | WA2997857 | half of the Cameras at the main gate not working | Roebourne Regional Prison | WSM-BR-RC | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Feb 2020 | 2020-02-09 14:31:15 | 2020-03-22 10:32:00 | Fail | Works CompleteRe-cable and replaced Fixed camera 9 and 11 with IP and required network hardwareRe-cable and replaced PTZ camera 23 with IP and required network hardware
MSA-DCS | WA2997989 | unit 1 A14 - cell door locked | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 1 | CLOSE | 09 Feb 2020 | 2020-02-10 18:47:26 | 2020-02-10 12:45:00 | Pass | Job completedd - serviced lock
MSA-DCS | WA2998863 | Ground floor lift - when you press the lift for the ground floor it doesn’t register for the ground | East Perth | GMP-BR- HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 10 Feb 2020 | 2020-02-10 11:02:35 | 2020-02-10 08:30:00 | Pass | Not chargeable
MSA-DCS | WA2998865 | Gatehouse - All systems loss in the control room | Roebourne Regional Prison | WSM-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Feb 2020 | 2020-02-10 14:59:07 | 2020-03-20 11:44:00 | Fail | Works CompleteSupply and install replacement Stratus Server for Security Management SystemSupply and install new UPS for Servertest and confirm correct operation
MSA-DCS | WA2998990 | CCU - cell H2 camera has black screen night. | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Feb 2020 | 2020-02-11 07:58:29 | 2020-03-13 16:30:00 | Fail | Found IR illuminator in PFM stores. Tested ok. Modified to fit camera housing in cell H2. Installed and tested by covering the cell windows with mattresses to simulate nighttime. Tested ok.
MSA-DCS | WA2999001 | Unit 9, A & B wing offices - replace floor coverings, damaged. | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Feb 2020 | 2020-02-17 17:00:00 | 2020-03-31 02:00:00 | Fail | replaced carpet tiles
MSA-DCS | WA2999007 | Unit 10, SO office - replace floor coverings in SITE COST | Hakea Prison | WSM-BR-SITE | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Feb 2020 | 2020-02-17 17:00:00 | 2020-04-01 19:45:00 | Fail | Office was not emptied out as arranged and required for job to proceed. Prison to report job in the future when they can allow access. Closing with costs to date as advised by Grant Byrne.
MSA-DCS | WA2999047 | BR-unit 6 safe cell C2 night camera not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Feb 2020 | 2020-02-11 08:18:29 | 2020-03-18 15:30:00 | Fail | Advice unit 6 officer that safecell C2 is old analog with infra red illuminator camera, to have a better quality of video/image and works better with Digital LCD monitor it requires upgrading.
MSA-DCS | WA2999089 | Visits Area SW PTZ camera pan and tilt function not operational. | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Feb 2020 | 2020-02-13 17:00:00 | 2020-02-13 14:30:00 | Pass | Southwest visits camera replaced for new, setup supply, programmed and replaced recording schedule, tested both image and recording footage all good. No further action required
MSA-DCS | WA2999102 | Bakery - Workshop-seals to the proover are damaged | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 10 Feb 2020 | 2020-02-17 17:00:00 | 2020-04-21 16:30:00 | Fail | 10/02/20 - Called as requested to the proover door seals u/s. Measured up for new door seals. 26/3/20 - Replaced seals on door, Prisoners have removed aluminium strip on one door and bent the other.17/4/20 - Replaced seals on remaining door.The bolts that hold the left hand door are missing and loose. Need to tighten and install.22/4/20 - Installed bolts in rail and siliconed.
MSA-DCS | WA2999206 | Outcare - Front door not closing properly/jamming | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 10 Feb 2020 | 2020-02-13 17:00:00 | 2020-03-23 09:30:00 | Fail | CLOSER ADJUSTED & RESET
MSA-DCS | WA2999481 | Unit 4, C4 - main door locks are jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 10 Feb 2020 | 2020-02-11 10:11:24 | 2020-02-10 14:30:00 | Pass | Job completed - Serviced cell lock
MSA-DCS | WA2999707 | Kitchen- Vegetable processor has exposed wires & not working | Melaleuca Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Feb 2020 | 2020-02-11 09:48:03 | 2020-04-09 13:35:00 | Fail | 11/02/2020 - Called as requested to the food processor not working and wires exposed. Stripped unit down to tested cable all ok assembled and placed exposed wires inside the unit temporarily until a new cable can be spied and fitted. Tested the unit working ok. Left operational and safe.09/04/2020 - Replaced mains cable tested- all good
MSA-DCS | WA3000035 | kitchen northern kettle lid lifter needs to be repaired | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Feb 2020 | 2020-02-11 13:06:59 | 2020-03-12 16:30:00 | Fail | 11/02/2020Called as requested to the kettle lid requires assembly. Removed from site for workshop repairs and parts. 21/02/2020Returned to site with lid and fitted to the unit, hinge sling assembly required.12/03/2020Returned to site was unable to fit the hinge remove ,return to the workshop welded new hinge return to site fitted to hinge sets tested all working okay.
MSA-DFES | WA2999572 | Level 1, kitchen - Air con Drain blocked and leaking into cavity and internal brickwork | CFRS Welshpool | GMP-BR | Air Conditioning | Materials (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 10 Feb 2020 | 2020-02-17 17:00:00 | 2020-03-30 15:53:00 | Fail | Unit isolated. Need to replace drain
MSA-DFES | WA2999731 | yard Faulty retic.-see additional notes | CFRS Claremont | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 10 Feb 2020 | 2020-02-13 17:00:00 | 2020-02-28 08:00:00 | Fail | Investigate retic not workingBRAF was done as Extra retic parts required
MSA-DTAG | WA3001110 | Cell 1 TV not working | Rockingham Justice Complex | GMP-BR-HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 3 | CLOSE | 10 Feb 2020 | 2020-02-17 17:00:00 | 2020-04-30 10:00:00 | Fail | Replaced new TV in cell
MSA-DTWD | WA2999221 | L3 AMEP sth wall-Number of network ports not working-see notes | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 10 Feb 2020 | 2020-02-17 17:00:00 | 2020-03-10 12:30:00 | Fail | Located both data cables and labelled correctly. Tested outlets shown up with cable breaks 20-30m into run . Will have to do braf for repairs Attended site and signed in. Ran 2x new data cables to AMEP office as by braf. Tested, labeled and all working fine. Job complete.
MSA-DTWD | WA2999606 | Room 133N- Chiller showing fault | Perth Campus B4 | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 10 Feb 2020 | 2020-02-13 17:00:00 | 2020-02-12 14:15:00 | Pass | As per instructed by Programmed, we do not have approval to proceed with further works @ Perth Campus
MSA-DTWD | WA2999621 | B block, room B2214 - Daiken Split sytem blowing hot air, fault code U4 | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 10 Feb 2020 | 2020-02-13 17:00:00 | 2020-05-11 12:00:00 | Fail | Found several condenser PCBs and fan have failed. BRAF send for approval. There is a 2 week wait on parts. If condenser fan blades required this is not available until end of MarchReplaced PCBsand found unit out of refrigerant. Located leak on inner condenser coil. Client asked for quote to replace unit. Awaiting approval.FM decided that unit replacement not to go ahead.
MSA-DTWD | WA2999939 | ground 14Ab air con will not turn on-Precise on site | Perth Campus B3 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 10 Feb 2020 | 2020-02-13 17:00:00 | 2020-04-08 16:00:00 | Fail | NotesAccessed building via fm. Test ran ducted split units lhand rh sides. Found lh unit indr fan operating and testrun shows outdr unit cooling and ok.Test ran rh unit to show no operation. Found indr faninnop and no outdr operation. Able to rectify wiringfault and indr fan now running. Outdr unit still failsupon cooling call. Outdr unit shows burnt wiring andfaulty controller/pcb arrangement to not bring on compand fans. Unit req new control wiring to be reconfiguredby eliminating over complicated and outdated board. Willengage electrical subc.19/2/20Isolated and gained ceiling space access. Located 2 x head units. Removed assoc covers and tested fan mtrs, ok.Isolated outdr unit and inspected control wiring. Found activate switch and 24v power supply to outdr unit faulty. Rectified and also checked outdr fan mtrs, comp and all assoc wiring. Test ran with new wiring conf, unit operating and cooling as desired. 2nd unit inspected and found unit req thermostat to be install
MSA-DTWD | WA3001335 | L2 D213 room too hot | Perth Campus B4 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 10 Feb 2020 | 2020-02-17 17:00:00 | 2020-04-03 10:45:00 | Fail | solated and gained ceiling space access. Located 2xhead units. Removed assoc covers and tested fanmtrs,ok.Isolated outdr unit and inspected control wiring.Foundactivate switch and 24v power supply to outdrunitfaulty. Rectified and also checked outdr fan mtrs,compand all assoc wiring. Test ran with new wiring conf,unitoperating and cooling as desired. 2nd unit inspectedandfound unit req thermostat to be installed intocontrolcircuit. Adapted wiring to test components and testedok.Will raise DAS for wiring circuit change.
MSA-MRWA | WA2999454 | West end stairwell Fluro lights out please remediate. | Traffic Operations Centre | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 10 Feb 2020 | 2020-02-11 17:00:00 | 2020-02-10 12:25:00 | Pass | Replaced with new tubes. Back in working order
MSA-DCA | WA3002777 | Lift 5 One display screen not working | State Library of WA | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 11 Feb 2020 | 2020-02-18 17:00:00 | 2020-02-12 08:30:00 | Pass | In car RHS screen gone off line, rebooted screen back and tested.
MSA-DCS | WA3002265 | Unit 4, Control Room camera display is not working | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Feb 2020 | 2020-02-12 09:34:06 | 2020-04-21 16:56:00 | Fail | Setup dual screens from duplicated to extended. Program in salvos for both monitors. Now they can view double the amount of cameras and operate screens independently.
MSA-DCS | WA3002310 | Manual selective button for cameras not working | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Feb 2020 | 2020-02-11 17:58:42 | 2020-04-23 19:00:00 | Fail | Job Complete as now is functioning
MSA-DCS | WA3002771 | ISU B02 Roller shutter to cell is not operating - (everything is on suspecting motor issue) | Banksia Hill Detention Centre | GMP-BR- HO | Building | Roller Shutters (BU) | UNIVERSAL DOORS | 2 | CLOSE | 11 Feb 2020 | 2020-02-14 17:00:00 | 2020-03-26 15:00:00 | Fail | REINSTALLED ROLLER SHUTTER WITH NEW MOTOR, REFIT & REWELDED SECURITY SCREEN, RECONNECT MOTOR, RESET LIMITS, CHECKED OPERATION, ALL OK
MSA-DFES | WA3002880 | Gym, cornice in corner south west of ceiling has been eaten by rats | CFRS Joondalup | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 11 Feb 2020 | 2020-02-18 17:00:00 | 2020-02-18 15:00:00 | Pass | COMPLETED
MSA-DTWD | WA3002178 | Block 8 - 1st Floor Plant room - 1 air handling unit is leaking a lot of water | Thornlie Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Equans Mechanical Services Australia | 0 | CLOSE | 11 Feb 2020 | 2020-02-11 13:07:59 | 2020-02-13 15:49:00 | Fail | Actual onsite Start time 08.45. Water isolated. Unit back on. Waiting for plumber to attend and rectify issue with drains before repairs to unit coil carried out.
MSA-DCA | WA3004874 | Roof- compressor unit is faulty | King Street Arts Centre-Main Building-External Area | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 12 Feb 2020 | 2020-02-13 17:00:00 | 2020-03-24 15:38:00 | Fail | Replaced compressor on ac21 as per quote. Found system has a gas leak when pressure testing. Returned another day.Accessed unit and found system has dropped pressure.Removed nitrogen and split pipework.Pressurized indoor and outdoor circuit and leak checked both sides.Found indoor side is dropping pressure.Found leak on indoor schraeder valve.Replaced seal and checked pressure.Found both sides held pressure.Reconnected pipework and evacuated system.Found unit held vacuum.Charged with r22 refrigerant.Checked operation of system and found unit operating correctly.
MSA-DCS | WA3004116 | Jeelia, B & C wing Laundry - Doors to laundry have dropped affecting lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 12 Feb 2020 | 2020-02-14 17:00:00 | 2020-02-21 08:30:00 | Fail | Adjusted Strike
MSA-DCS | WA3004160 | Unit 3, C & D wing showers - wall panels are coming away from the wall | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 12 Feb 2020 | 2020-02-14 17:00:00 | 2020-05-01 14:15:00 | Fail | RE FIXED WALL PANELS
MSA-DCS | WA3004170 | Unit 1, B & D - Floor bubbling on landing in front of B/D entry door | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 12 Feb 2020 | 2020-02-18 17:00:00 | 2020-09-08 10:30:00 | Fail | damaged section of flooring replaced
MSA-DCS | WA3004200 | Unit 2, Entry Air lock, right hand side - door frame into the unit is loose | Bandyup Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 2 | CLOSE | 12 Feb 2020 | 2020-02-17 17:00:00 | 2020-03-30 10:00:00 | Fail | Attended site and carried out repairs to airlock entry door frame, reinforced using aluminium angle and additional fixings.Supplied and installed new Dorma TS93G hydraulic closer.Supplied and installed new Raven adjustable door seals.
MSA-DCS | WA3004234 | Unit 9, cell A3,A4, A15 - medical hatches can be kicked open, lock problem | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 12 Feb 2020 | 2020-02-13 08:21:21 | 2020-02-12 15:30:00 | Pass | Job completed - hatches and replace on lock
MSA-DCS | WA3004238 | Unit 10, C12 medical hatch, can be kicked open, lock problem | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 12 Feb 2020 | 2020-02-13 08:23:00 | 2020-06-24 15:30:00 | Fail | Replaced medical hatch
MSA-DCS | WA3004456 | Crisis Care unit, common room door- lock is working on one side but not the other | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 12 Feb 2020 | 2020-02-12 13:41:29 | 2020-02-12 14:00:00 | Fail | Serviced door lock
MSA-DCS | WA3004593 | Unit 2, A wing - wing grill silenoid sticking/repair/replace/A wing | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 12 Feb 2020 | 2020-02-13 11:27:53 | 2020-02-21 09:45:00 | Fail | No completion notes
MSA-DCS | WA3004672 | Crisis care, front door - electronic lock is playing up | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 12 Feb 2020 | 2020-02-13 12:32:58 | 2020-02-12 15:00:00 | Pass | adjusted door handle to ensure door closes and locks correctly.
MSA-DCS | WA3004692 | Unit 5 C Wing double door fridge is not cooling | Hakea Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 12 Feb 2020 | 2020-02-17 17:00:00 | 2020-03-16 14:36:00 | Fail | Fridge has been replaced. Operating correctly at time of departure.
MSA-DCS | WA3004694 | Replace defective padlocks (x2) and keys (x3) | Riverbank | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 12 Feb 2020 | 2020-02-17 17:00:00 | 2020-02-13 09:45:00 | Pass | Job Completed - keys cut
MSA-DCS | WA3004745 | Visits Area - PA system not working in visits room | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Feb 2020 | 2020-02-19 17:00:00 | 2020-03-23 15:53:00 | Fail | Works Related to construction handed over to Project manager - no further works by SEME
MSA-DFES | WA3004802 | Please check if the 'Fire Station' sign is working | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 12 Feb 2020 | 2020-02-19 17:00:00 | 2020-03-27 15:15:00 | Fail | BRAF was declined, job signed off.
MSA-DTAG | WA3004494 | Lift 1 - Out of Service. Doors were opening and closing and alarm was sounding. | Central Law Courts-Main Building-Level 3 | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 12 Feb 2020 | 2020-02-13 17:00:00 | 2020-02-12 13:22:00 | Pass | Doors would fully close than reopen on lvl 3 and than timeout. Found right hand landing door tight in certain spots, would not self close. Cleaned track and backed off upthrusts. Rollers to be replaced, obr created. Tested and returned to service.
MSA-DTAG | WA3004854 | Lvl 3,Court 37,Water leaking through the ceiling has caused part of the ceiling / tiles to collapse | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 12 Feb 2020 | 2020-02-13 17:00:00 | 2020-03-19 09:00:00 | Fail | Pipe work removed and replace with new pipe.Checked after refilling for leaks
MSA-DTWD | WA3004241 | Staff female disabled toilet flexi hose on basins are rusted & leaking | Jandakot Campus - Hangar | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 12 Feb 2020 | 2020-02-13 17:00:00 | 2020-04-02 18:28:00 | Fail | Job to be signed off new job to be raised once an isolation valve can be installed
MSA-DTWD | WA3004775 | L Block Storeroom- Ceiling panels need repairing | Balga Campus | GMP-BR | Building | Ceiling (BU) | M Construction (WA) | 3 | CLOSE | 12 Feb 2020 | 2020-02-19 17:00:00 | 2020-03-30 13:55:00 | Fail | Job complete
MSA-MRWA | WA3004650 | AGI Shed - Clean up area as per email sent | Materials Engineering Branch | GMP-BR | Cleaning | Cleaning (CL) | MR - Handyperson - PFM | 2 | CLOSE | 12 Feb 2020 | 2020-02-17 17:00:00 | 2020-02-14 14:28:00 | Pass | Job was assessed returning later date to complete
MSA-DCA | WA3006409 | AC 2 water leak | Shipwreck Galleries-Main Building-Level 1-Dutch Wreck Gallery | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 13 Feb 2020 | 2020-02-14 17:00:00 | 2020-02-18 16:30:00 | Fail | Attended site. FCU2A system leaking water. Applied tests and checks, isolated system and made area safe due to excessive water and limited access due to gallery being occupied. Rerurned to site the following day. Removed and replaced condensate pump, insulated chilled water and hearing water valves. Re ran and configured 5/8 drain, re- insulted copper pipework, re ran and configured 3/8 sub drains for chilled and heating water drip emergency trays and insulated copper pipework. Siliconed and sealed areas of drain tray with in FCU. Due to the constant wear and tear of the gallery FCUS a spare condensate pump was purchased and has been left in the BMS room as a critical spare for FCU2A/B Dutch Gallery FCU systems. Tested operation. System operating correctly with no leaks present.
MSA-DCS | WA3006366 | Unit 3 house 1 and 2 Entry intercom not audible | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Feb 2020 | 2020-02-20 17:00:00 | 2020-02-27 10:00:00 | Fail | Replaced unit 3 house 2 cell call with new cell call. Replaced and all tested ok. Job complete , house 1 completed on separate job
MSA-DCS | WA3006689 | Unit 2 - A Wing-Vent in A Wing shower missing. | Casuarina Prison | GMP-BR- HO | Building | Steel Work (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 13 Feb 2020 | 2020-02-18 17:00:00 | 2020-02-24 12:00:00 | Fail | COMPLETE - NEW VENT INSTALLED
MSA-DCS | WA3006699 | Unit 2, B & D Day Room- Floor vinyl in front of oven is bubbling | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Feb 2020 | 2020-02-20 17:00:00 | 2020-06-30 13:30:00 | Fail | DAMAGED VINYL REMOVED / REPLACED
MSA-DFES | WA3005993 | front door no1 vols engine room door will not close | CFRS Rockingham | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 13 Feb 2020 | 2020-02-14 17:00:00 | 2020-02-13 15:23:00 | Pass | DOOR WAS STUCK UPHAD TO ADJUST PE BEAMSRE WIRE CONTROL CONNECTIONSRE PROGRAMME THE DOOR AND LIMITS AMD TESTLEFT WORKING
MSA-DFES | WA3006779 | ground Rear Perimeter fence has sheet missing.-photo's to follow in email | VFRS Bassendean | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Feb 2020 | 2020-02-18 17:00:00 | 2020-02-17 09:00:00 | Pass | Repaired timber rail and reattached loose sheeting
MSA-DTAG | WA3006283 | Custody - hot water urn not heating and tap dripping | Rockingham Justice Complex | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 13 Feb 2020 | 2020-02-14 17:00:00 | 2020-02-14 11:55:00 | Pass | Attended to fix leaking tap. Also machine wasn’t getting hot. Tap is broken and needs replacing but the bigger concern is the wiring and board are burnt out after removing cover. System is hard wired. Needs to be replaced. INSTALLED NEW CAPEX ASSET - ZIP ECONOBOIL 5L BWU REWORKED SPACE REMOVED OLD TO TIP
MSA-DTAG | WA3006328 | basement custody office-Screen displaying CCTV footage keeps turning on and off | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Feb 2020 | 2020-02-14 17:00:00 | 2020-02-13 17:00:00 | Pass | Attended site checked and found CCTV multiplex is faulty and keep rebooting itself, monitor itself is ok. Back to office source part and back to site to replace and tested it ok after replacement. VIDEOART VT3058 X 1.
MSA-DTAG | WA3006706 | Bio Clean required. Urine on sallyport floor – Accused known as being HIV positive | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 13 Feb 2020 | 2020-02-14 17:00:00 | 2020-02-14 07:30:00 | Pass | Bio Clean
MSA-DTAG | WA3006840 | Custody Centre, Cell 4- Bio Clean required, details below | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 13 Feb 2020 | 2020-02-14 17:00:00 | 2020-03-14 21:30:00 | Fail | Job completed by cleaner as per work order
MSA-DTWD | WA3006187 | Room E2 demountable – EVAP keeps tripping out | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 13 Feb 2020 | 2020-02-18 17:00:00 | 2020-03-05 13:00:00 | Fail | found electrical breaker trippped, disconnect the motor. found faulty. requires a new motor and soleniod. parts ordered, to return
MSA-DTWD | WA3006347 | Level 3, Room B328 Fashion- Leaking tap | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 13 Feb 2020 | 2020-02-20 17:00:00 | 2020-02-18 17:00:00 | Pass | replaced tap set and spout
MSA-DTWD | WA3006494 | Block 3- 19Ab Tap water leaking constantly | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 13 Feb 2020 | 2020-02-20 17:00:00 | 2020-02-18 17:15:00 | Pass | inspected, work completed across other work orders
MSA-DCS | WA3012452 | Unit 3, A & C - floor near oven bubbling, also small bubble inside wing door | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 Feb 2020 | 2020-02-20 17:00:00 | 2020-09-29 13:00:00 | Fail | FLOOR REPAIRS COMPLETED
MSA-DCS | WA3013010 | east oval single grille gate near water fountain lock is faulty hard to operate | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 14 Feb 2020 | 2020-02-15 11:39:00 | 2020-02-14 14:30:00 | Pass | Serviced lock
MSA-DCS | WA3013176 | unit 2, A wing, day room - in the corner is damaged ceiling | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 Feb 2020 | 2020-02-19 17:00:00 | 2020-05-25 10:52:00 | Fail | roof leak located and rectified, ceiling patched, prison painted.
MSA-DTAG | WA3013000 | Level 3 - Lift No.1 is stuck opening and closing on Level 3 and making loud noises | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 14 Feb 2020 | 2020-02-17 17:00:00 | 2020-02-14 14:50:00 | Pass | Lift On JRV lvl3 when arrived to site. Found doors cycling open/closed. T5 not making intermittently. Found rear LH car door roller cracked. Replaced & tested. Doors functioning correctly. All ok. Lift in service.
MSA-DTWD | WA3012989 | P Block, 3 x Air Con units stolen | Midland Campus | GMP-BR-RC | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 14 Feb 2020 | 2020-02-17 17:00:00 | 2020-04-08 16:00:00 | Fail | Accessed P block. Obtained indoor unit details. Measured room floor areas. Processed information onto Precise Air. Isolated power supplies to outdoor isolators on western wall.
MSA-DTWD | WA3013016 | E block restaurant/kitchen tap has come loose from its mount | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Feb 2020 | 2020-02-19 17:00:00 | 2020-02-14 14:30:00 | Pass | No completion notes
MSA-DTWD | WA3013400 | A block upstairs A52 We have programming issues with the BMS & new controller-see notes | Midland Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 14 Feb 2020 | 2020-02-19 17:00:00 | 2020-03-09 14:57:00 | Fail | Michael Otter (as per clients WO description) attended site and identified that there were BMS programming issues. Rectified these programming issues and checked operation. Equipment running as per normal.
MSA-MRWA | WA3013072 | L7 room 747 Inspect chairs repair and report. | Don Aitken Centre MRWA Head Office | GMP-BR | Furniture | Domestic Furniture (FU) | MR - Handyperson - PFM | 2 | CLOSE | 14 Feb 2020 | 2020-02-19 17:00:00 | 2020-02-18 11:00:00 | Pass | damaged chairs removed for repair
MSA-DCS | WA3026202 | Roebourne Regional Prison Work Camp-One circle cell call hand set not working in unit 1 | Roebourne Regional Prison Work Camp | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Feb 2020 | 2020-02-15 16:30:34 | 2020-02-28 11:30:00 | Fail | Removed and replaced cell call handset. Tested ok. Parts used:Austco CI-OH Officer station handset.
MSA-DCS | WA3026239 | Unit 12 B10 has no lock | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 1 | CLOSE | 15 Feb 2020 | 2020-02-16 11:02:05 | 2020-02-18 10:45:00 | Fail | replaced lock and cylinder escutcheon.
MSA-DCS | WA3030671 | Unit 4 - House 5 - off line no cell call | West Kimberley Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Feb 2020 | 2020-02-16 22:51:44 | 2020-03-05 10:30:00 | Fail | Replaced unit 4 house 5 with new APC UPS. Site stock used. All replaced and tested ok. Job complete
MSA-DCA | WA3054817 | external area - Main water leak | Short Street Theatre-Main Building-External Area | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 17 Feb 2020 | 2020-02-17 13:01:49 | 2020-02-17 14:02:00 | Fail | Expose burst pipe Make safe Back fill and relay pavers
MSA-DCS | WA3054389 | Obs post 7, window has a crack | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Feb 2020 | 2020-02-21 17:00:00 | 2020-05-13 15:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3054430 | Jeelia, Cell A4- cell door missing screws and has dropped on lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 17 Feb 2020 | 2020-02-21 17:00:00 | 2020-02-21 09:15:00 | Pass | Replaced hinge on cell door.
MSA-DCS | WA3054488 | Unit 1, Cell C5- medical hatch is getting stuck in lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 17 Feb 2020 | 2020-02-18 07:37:24 | 2020-02-18 09:45:00 | Fail | Serviced hatch lock
MSA-DCS | WA3054493 | Unit 2, C Wing yard grill- auto closer is broken | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | AAA Ability Locksmiths | 1 | CLOSE | 17 Feb 2020 | 2020-02-18 07:39:21 | 2020-02-19 13:45:00 | Fail | Replaced door closer.
MSA-DCS | WA3054599 | CCU (11) - camera to cell D4 is blurry. Prisoner banged the cover of the camera, cracked it | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Feb 2020 | 2020-02-18 08:09:43 | 2020-04-14 07:53:00 | Fail | Job complete under WA3176444
MSA-DCS | WA3055157 | kitchen - Brat Pan not tilting | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 17 Feb 2020 | 2020-02-20 17:00:00 | 2020-03-19 15:00:00 | Fail | 20/2/20Arrived on site was told the unit would not tilt. Tested the the transformer, resistor, capacitor, motor, switch, all tested fine, did find some loose connections which I tightened up, unit is tilting but externals of the switch are broken, recommend replacing tilt switchWhile on site was asked to look at Waldorf bratt pan, was told it has intermittent problems with pilot igniting, found nothing as was working while on site. Was told when issue is happening they can light by an gas igniter but the sparker does not work and there is no ticking noise. Also leveled up the unit.19/03/20 Called as required to fit part order fitted tested all working ok now.
MSA-DCS | WA3055478 | Gardens - pump shed VSD faulty | Karnet Prison Farm | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Feb 2020 | 2020-02-24 17:00:00 | 2020-04-06 13:00:00 | Fail | Investigate garden pump VSD. Found faulty pump. Requires removal to quote on repairs.Remove pump so job can be quoted.Collect repaired pump.Replace gardens pump.
MSA-DCS | WA3055588 | unit 4 C10 damaged vinyl | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Feb 2020 | 2020-02-24 17:00:00 | 2020-07-17 12:39:00 | Fail | SUPPLY AND INSTALL NEW VINYL
MSA-DCS | WA3055716 | Unit 3, B wing shower block window - Damaged window slide, metal strip is protruding from frame. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Feb 2020 | 2020-02-24 17:00:00 | 2020-02-24 13:30:00 | Pass | complete - spiral balances renewed
MSA-DCS | WA3055721 | Medical Centre - numerous roof internal particle board tiles are damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Feb 2020 | 2020-02-24 17:00:00 | 2020-07-08 09:48:00 | Fail | JOB TO BE COMPLETED ON SOURCE #WA3425706 - ONLY LABOUR HAS BEEN CHARGED
MSA-DTAG | WA3055087 | Ground level, Court 3 Magistrate Entrance - Raised floor is pulling away from walls and sinking | Perth Children's Court | GMP-BR-HO | Flooring | Timber (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Feb 2020 | 2020-02-24 17:00:00 | 2020-05-21 13:56:00 | Fail | removed white ant damaged timber flooring, installed new framework and flooring ready for carpet.
MSA-DTWD | WA3054766 | Downstairs workshop - bi fold door, manual chain has broken | Kwinana Automotive Centre | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 17 Feb 2020 | 2020-02-20 17:00:00 | 2020-02-19 15:17:00 | Pass | Haul chain added to motor to facilitate operation if no power to door.This is the only site in Western Australia we’re staff will not signProgram paperwork
MSA-DTWD | WA3055036 | E block, E33.1 cool room - Irregular Nosie | Bentley Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 17 Feb 2020 | 2020-02-20 17:00:00 | 2020-04-23 16:00:00 | Fail | Found no unusual noises as reported. Carried out full inspection of system. Cleaned coils.Reinspected when on site. All appears ok.
MSA-DTWD | WA3055305 | Horticulture Shed, east side of shed- Sliding doors not operating correctly | Midland Campus | GMP-BR | Building | Automatic Doors (BU) | AWB Co. | 2 | CLOSE | 17 Feb 2020 | 2020-02-20 17:00:00 | 2020-03-12 14:45:00 | Fail | 12.03.20 - ATTENDED SITE, SUPPLY & INSTALLED ONE (1) NEW SLIDING DOORTRACK & FOUR (4) CARRIAGES ON THE SLIDING DOOR LOCATED AT THEHORTICULTURE SHED AS QUOTED
MSA-DTWD | WA3055608 | D Block, Room D3- Air con leaking water in room | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 17 Feb 2020 | 2020-02-20 17:00:00 | 2020-02-20 16:30:00 | Pass | Found Condensation Drain blockage.Clear the blockage now not leaking all Good
MSA-DCS | WA3069994 | Gatehouse - EBI 3 is not working- no signal | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Feb 2020 | 2020-02-18 10:31:08 | 2020-02-18 17:45:00 | Fail | Sourced parts, attended site and repaired PSU and network faults with EBI Server.Monitored for correct operation and tested OK.Job CompleteParts used (SEME Stock):1 x Power Supply ModuleConsumables
MSA-DCS | WA3070156 | Gym, Overhead light above the playing area fails to start | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Feb 2020 | 2020-02-25 17:00:00 | 2020-03-24 14:00:00 | Fail | Checked gym lights, ordered parts, picked up cherry picker. Repaired faulty lights and tested.
MSA-DCS | WA3070632 | gate control senstar memory No8 nearly full | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Feb 2020 | 2020-02-25 17:00:00 | 2020-04-23 08:00:00 | Fail | Old Senstar system decommissioned and fault is now non issue.
MSA-DCS | WA3070763 | control room, PTZ 65 showing no input-SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Feb 2020 | 2020-02-25 17:00:00 | 2020-02-28 14:30:00 | Fail | On investigation at Equipment Cabinet Camera was found to be operating correctly, reset fibre modem and confirmed on Indigo system that video feed from camera was operating correctly.
MSA-DCS | WA3071090 | unit 2 B wing grille lock top screw is stripped and will not slam shut | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 18 Feb 2020 | 2020-02-19 14:02:11 | 2020-02-19 12:15:00 | Pass | Job completed - repaired grille and replace fixings
MSA-DCS | WA3071281 | unit 1 cell C8, cell call system not working at all-was pressure cleaned | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Feb 2020 | 2020-02-19 15:24:06 | 2020-03-27 09:48:00 | Fail | job completed under wa3168779
MSA-DFES | WA3071003 | Engine bay non slip flooring is peeling up/off in several locations | CFRS Fremantle | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 18 Feb 2020 | 2020-02-25 17:00:00 | 2020-02-25 12:30:00 | Pass | BRAF declined and directed by Brendan to close off with costs to date.
MSA-DTAG | WA3070544 | Level 4, St Georges Terrace end- Female WC leaking | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Feb 2020 | 2020-02-21 17:00:00 | 2020-04-28 08:15:00 | Fail | Complete
MSA-DTAG | WA3070726 | L24 kitchen Reader has faulted again for the kitchen and locks people in | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 18 Feb 2020 | 2020-02-21 17:00:00 | 2020-04-17 16:00:00 | Fail | job completed - Removed reader and installed new
MSA-DTAG | WA3070741 | Contractors Accessing Celing Space And Staff-rodent droppings in ceiling space potential pest infest | Joondalup Courthouse | GMP-BR-HO | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 18 Feb 2020 | 2020-02-21 17:00:00 | 2020-02-20 08:30:00 | Pass | rodent baiting to external areas including 7 new rat boxes installed and loaded with bait
MSA-DTAG | WA3071209 | Security Office- HPWU unit 3 failed | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 18 Feb 2020 | 2020-02-21 17:00:00 | 2020-04-08 10:30:00 | Fail | Gas leak has been repaired and unit is now working as normal.
MSA-DTAG | WA3071298 | courtroom 2 ants in court | Rockingham Justice Complex | GMP-BR-HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 18 Feb 2020 | 2020-02-25 17:00:00 | 2020-02-24 09:50:00 | Pass | Ant treatment applied to court room 2
MSA-DTWD | WA3070624 | BLD 822A- lights faulty | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 18 Feb 2020 | 2020-02-21 17:00:00 | 2020-02-26 14:00:00 | Fail | Replaced Faulty 10amp HRC fuse, 3 x 150 Watt lamps
MSA-DTWD | WA3070627 | BLD 822, Flat C Kitchen- Faulty power point | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 18 Feb 2020 | 2020-02-21 17:00:00 | 2020-02-26 11:30:00 | Fail | Installed 1x power point RCD
MSA-DTWD | WA3070832 | BLD 840- Various lights faulty | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 18 Feb 2020 | 2020-02-21 17:00:00 | 2020-02-20 09:00:00 | Pass | replaced downlights
MSA-MRWA | WA3070357 | Toilet, Light out in bathroom please replace | Traffic Operations Centre | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | CLOSE | 18 Feb 2020 | 2020-02-19 17:00:00 | 2020-02-18 11:07:00 | Pass | Replaced globe with new
MSA-DCS | WA3071633 | Unit 2, Control Room door is not closing properly | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 Feb 2020 | 2020-02-20 07:02:56 | 2020-02-19 14:30:00 | Pass | Serviced control room lock
MSA-DCS | WA3071865 | Gatehouse, Key watcher - faulty not working as it should | Wooroloo Prison Farm | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Feb 2020 | 2020-02-19 12:26:02 | 2020-02-21 14:00:00 | Fail | Replaced circuit board on Keywatcher box 3, programmed system, tested all boxes, checked software- all ok
MSA-DCS | WA3071921 | Canteen - freezer faulty, incorrect temperatures | Wooroloo Prison Farm | GMP-BR- HO | Refrigeration | Freezers (RE) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 19 Feb 2020 | 2020-02-24 17:00:00 | 2020-03-09 09:00:00 | Fail | Fridge running high temp.Leak found on evaporation loop.Rectified.Please see work logs for further.
MSA-DCS | WA3072727 | Kitchen - dishwasher not heating water | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 19 Feb 2020 | 2020-02-20 12:56:47 | 2020-04-17 17:30:00 | Fail | 21/02/20 - Called as requested to the dishwasher not working, checked the dishwasher. Fitted o/t & rinse tank thermostat, tested all ok.22/02/20 - Called as requested to the dishwasher not working again. Found the internal circuit breaker tripped due to the wash elements blown. Will require 3 x wash tank elements. 17/04/20 - Replaced parts as per previous visit reconnected contactor and set temp on thermostat new elements drawing between 18-19 amps - all good.
MSA-DCS | WA3072745 | SOG Pod- Keyboard is damaged on built in desk | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Feb 2020 | 2020-02-26 17:00:00 | 2020-02-27 10:30:00 | Fail | Removed faulty keyboard and installed replacement. Tested and confirmed correct operation of new keyboard.
MSA-DCS | WA3072878 | BR- Camera 52 picture quality is poor | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Feb 2020 | 2020-02-19 18:35:56 | 2020-05-08 15:35:00 | Fail | Investigated faults, repaired ,mulitple comminucation faults, reprogrammed camera and tested ok.Job Complete
MSA-DCS | WA3072880 | BR- Camera 91 picture is poor in zoom mode | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Feb 2020 | 2020-02-19 18:37:41 | 2020-03-18 14:30:00 | Fail | Camera 91 newly installed AXIS IP PTZ camera, advice officer on site that wind loading will affect the image when zooming the camera to maximum of 600 meters ( shaky image ).Zone 8 to 15 external is also covered by 8 fixed cameras.
MSA-DCS | WA3072951 | Control room - sennet network, Coms fault. Inter detection fence. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Feb 2020 | 2020-02-19 19:30:16 | 2020-03-12 17:45:00 | Fail | Investigated multiple faults after lightning strike. Investigated perimeter detection and repaired multiple faults, restored communication systems and perimeter detection function.
MSA-DFES | WA3072987 | Ground level, Hanger Roller door from Car park into Hanger - Electronic roller door not working. | DFES Rescue Helicopter Base | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 19 Feb 2020 | 2020-02-24 17:00:00 | 2020-03-25 10:00:00 | Fail | Client explained that door has been leaking oil for a period of time and seems to be struggling tooperate door. I have submitted a quote for motor to be replaced/upgraded.Followed up on BRAF approval for the 26th Parts hold up till 25th March
MSA-DTWD | WA3072383 | Damaged water pipe located near bike racks | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 19 Feb 2020 | 2020-02-26 17:00:00 | 2020-03-25 16:19:00 | Fail | Investigate sand loss , repair and re fill and tidy
MSA-DTWD | WA3072446 | Damaged perimeter fence due to weather. 6 -8 meters of temporary fencing required ASAP | Thornlie Campus | GMP-BR-RC | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 19 Feb 2020 | 2020-02-20 17:00:00 | 2020-05-06 14:00:00 | Fail | Please note works were only completed last week by another contractor. We have had the job open for an extended period while we have waited for direction from site to proceed with works or that the temp fence we hired out was no longer required.
MSA-MRWA | WA3072066 | Southern side of building - Please test electrical pit for ACM and report. | Don Aitken Centre MRWA Head Office-Main Building-Ground Floor | GMP-BR | Electrical | General Electrical (EL) | Environmental Site Services | 1 | CLOSE | 19 Feb 2020 | 2020-02-20 17:00:00 | 2020-02-21 17:00:00 | Fail | Please see attached lab analysis results
MSA-DCS | WA3073874 | Unit 4, Cell D11- Window does not stay open when opened | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Feb 2020 | 2020-02-26 17:00:00 | 2020-07-08 13:15:00 | Fail | SPIRAL BALANCES RENEWED
MSA-DCS | WA3073880 | Unit 1, Cell C16- Door viewing window is smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 20 Feb 2020 | 2020-02-21 07:41:55 | 2020-04-01 14:30:00 | Fail | door has been replaced
MSA-DCS | WA3073901 | Jeelia, B Wing- Laundry door out of alignment affecting lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 20 Feb 2020 | 2020-02-26 17:00:00 | 2020-02-21 11:15:00 | Pass | Adjusted hinges and realign door to ensure correct locking.
MSA-DCS | WA3073915 | Education, Old Canteen - Front door hard to lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 20 Feb 2020 | 2020-02-26 17:00:00 | 2020-02-21 10:30:00 | Pass | Adjusted strike and lock.
MSA-DCS | WA3073922 | Control, Gatehouse - multiple faults reported by control officer- more info below | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Feb 2020 | 2020-02-25 17:00:00 | 2020-03-26 13:27:00 | Fail | Investigated multiple faults, replaced faulty network switch which resolved Channel 26, Controller 27 & 28.Replaced faulty Hard Drive on Server.Tested OK.Job CompleteParts used (SEME Stock):1 x Network Switch1 x Hard DriveSundries
MSA-DCS | WA3073965 | Unit 9, C & D control room door- has electronic lock problem | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Feb 2020 | 2020-02-21 08:15:32 | 2020-02-20 12:30:00 | Pass | Job completed- replaced electric strike.
MSA-DCS | WA3073971 | Main prison perimeter – microwave on zone C2 is faulty | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 Feb 2020 | 2020-02-27 17:00:00 | 2020-03-13 15:13:00 | Fail | Zone tested and reports run and confirm functional since alignment check. Critical spare microwave set left onsite
MSA-DCS | WA3074059 | Laundry, stairwell door - Broken Key in the lock. | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 20 Feb 2020 | 2020-02-20 12:50:49 | 2020-02-20 11:30:00 | Pass | Job completed - remove broken key from cylinder, return broken key to security
MSA-DCS | WA3074206 | Eyre, Cell A3- Personal lock fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 20 Feb 2020 | 2020-02-25 17:00:00 | 2020-03-09 09:00:00 | Fail | supplied & installed replacement cylinder.
MSA-DCS | WA3074338 | Offices & lunch area - ant infestation | Warminda Hostel | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 20 Feb 2020 | 2020-02-21 10:46:48 | 2020-02-20 14:20:00 | Pass | Ant treatment with Termidor applied to affected areas
MSA-DCS | WA3074484 | staff room - door lock completely failed | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 20 Feb 2020 | 2020-02-20 15:27:25 | 2020-02-20 16:00:00 | Fail | job completed - replaced faulty lock
MSA-DCS | WA3074506 | Bakery - Oven door is broken | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 20 Feb 2020 | 2020-02-27 17:00:00 | 2020-04-07 15:00:00 | Fail | Fit oven door back onto oven, welding bottom door hinge back into position.
MSA-DCS | WA3074566 | POD AC faulty, not working | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 20 Feb 2020 | 2020-02-21 12:13:15 | 2020-02-20 19:00:00 | Pass | Arrived to site and found control A/C flashing F3 fault.Checked over indoor unit and duct work.Very high ambient temps recorded in roof space.Pipes feeding indoor temps not improving.Checked over outdoor unit and found pools of oil in lower base pan.Gas leak evident.Began pressure test procedures.Located split discharge pipe due to compressor which has been replaced at some stage has no mounting bolts which has cause the pipe to fracture under constant vibrations.Advised prison hot works required to repair pipe and need fire panel isolated.Pipe repaired.Pressure tested.Passed.Evacuated system of contaminates.Recharged to name plate specifications.Powered up unit.Watched temps improve.All working okay.
MSA-DCS | WA3074619 | Damaged plasterboard ceiling to Reception (inside roller door) adjoining video link | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Feb 2020 | 2020-02-27 17:00:00 | 2020-09-21 11:40:00 | Fail | ASSESSED ONLY - CLOSING JOB COST TO DATEBRAF EMAILED 31/08 - NO APPROVAL AS @ 21/09/2020
MSA-DCS | WA3074754 | Healthcare - Receptionists door - lock is faulty | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Feb 2020 | 2020-02-21 14:19:31 | 2020-02-21 12:00:00 | Pass | Repaired lock
MSA-DCS | WA3074759 | Social Visits holding cell handles on both doors are loose | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Feb 2020 | 2020-02-21 14:22:51 | 2020-02-21 12:15:00 | Pass | Inspected broken handles - beyond repair. Require replacement parts. DOJ Locksmith to source parts. Job closed off as per advice from DOJ Locksmith
MSA-DTAG | WA3074711 | Coroners Office - Aircon does not appear to be working in two offices – rooms are too warm. | Central Law Courts-Main Building-Level 11 | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 20 Feb 2020 | 2020-02-25 17:00:00 | 2020-04-01 12:00:00 | Fail | Attend site. Access lev 11 and check temperature issues on north east offices. Found offices to be warm. Access bms and check duel duct box operation. Found box serving this area not operation correctly. Adjust setpoints to test and found box to be working in opposite. As i rise the setpoint i find the cooling damper to open. As i lower the setpoint i find the heating damper to open. Icon logic have dialed in remotely and rectified this issue. Test operation of DD box. Now working ok.
MSA-DTAG | WA3074922 | Level 10, Front counter - the supplementary air con in the Banksia waiting room as it is still very | Westralia Square | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 20 Feb 2020 | 2020-02-25 17:00:00 | 2020-07-15 16:30:00 | Fail | Luke Robson (15/07/2020)Arrived on site remove ceiling panels, duct work and Grills to access. Reinstalled unit, control and power wiring. Connected ductwork, reinstalled ceiling panels and Grills. Tested unit, all working as it should with no faults. Cleaned and vacuumed area.
MSA-DTWD | WA3074057 | T Block, Cafeteria- walk in freezer has gone into fault | Murdoch Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 0 | CLOSE | 20 Feb 2020 | 2020-02-20 12:50:18 | 2020-02-20 14:00:00 | Fail | Attended site and signed in, found the evaporator coil iced up on the freezer room. Isolated and defrosted, ran the system ran test ran . Gas pressure ok , defrost cycle working all heaters ok . The door to the room is being left ajar during the day which allows hot air to get in and cause icing up . Will quote to fit door alarm.
MSA-DTWD | WA3074427 | Main workshop door - eletrical fault doors wont close | Kwinana Automotive Centre | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 20 Feb 2020 | 2020-02-20 15:11:07 | 2020-02-21 15:56:00 | Fail | 20/2/20 - Attended site but requires lifter to gain access.21/2/20 - Door is working very well, no faults found
MSA-DTWD | WA3074478 | Q Block, G/Floor- Room Q001A & Q001B the large sliding doors will not lock | Joondalup McLarty Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 2 | CLOSE | 20 Feb 2020 | 2020-02-25 17:00:00 | 2020-02-25 07:15:00 | Pass | Dang Nguyen (24/02/2020) - Work NoteAttend site to investigate fault with on doors Q001 A, B, found the magnets to be at fault. Will require a revisitDang Nguyen (25/02/2020) - Work NoteAttend site to rectify faults on Q001 A, B doors not locking. Cables are ok, magnet plates are out of alignment because door frames are out by a bit. Best resolution would be to install mini maglocks. Q001 A door is locked by temperamental due to frame. Barry will fix frame first
MSA-DTWD | WA3074832 | N Block, Room N28- Delivery Pipe on Unit A is damaged- see further notes below | Midland Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 20 Feb 2020 | 2020-02-25 17:00:00 | 2020-04-09 16:40:00 | Fail | Arrived onsite. Gained access to N block. Confirmed multi head system had lost charge to one circuit only. Isolated circuit A. Took relevant information for repair. Sent information through to PAG. Picked up materials for repair.Arrived onsite. Isolated and locked out power supply to multi system. Found both lines to outdoor unit had been severed. Repaired refrigerant lines. Pressure tested system. Evacuated system and charged with R22. Test ran system. Circuit A compressor not running. Checked all compressor associated components. All ok. Compressor quite hot. Suspect compressor is electrically seized. Fujitsu have informed me that parts are no longer available for this unit due to age. Will consult with FM for outcome.8.4.20: Arrived onsite with 2 x split systems and installation materials. Recovered refrigerant from existing multi head system. Removed old units from building. Mounted indoor units, pipe covers and wall brackets. Will return to site tomorrow to finish installation
MSA-DTWD | WA3074840 | T Block, ground floor, room T008, T009, T010 - have faulty door locks, difficult to lock the rooms | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 1 | CLOSE | 20 Feb 2020 | 2020-02-21 17:00:00 | 2020-04-21 12:00:00 | Fail | Job completed - have had restricted key system from another locksmith allowing us to work on this key system, work out how doors have been keyed & numbered discuss with site how to move froward with repair and key system
MSA-DTWD | WA3074896 | external, ground level - graffiti around outside of building | Perth Campus B1 | GMP-BR | Building | External Walls (BU) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 20 Feb 2020 | 2020-02-27 17:00:00 | 2020-02-28 14:50:00 | Fail | REMOVE AND PAINT OVER GRAFFITI LOCATED EXTERNAL GROUND LEVEL OUTSIDE
MSA-DCS | WA3075796 | Unit 2 Control Room- Transponders faulty in the following locations | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Feb 2020 | 2020-02-22 11:39:13 | 2020-02-28 09:30:00 | Fail | Used the PC map to help locate the faults in the field. 2.7.2 - located in the female recreation area behind the donga. Found receiver PCB to be water damaged. Dried and cleaned the inside of the enclosure. Replaced the PCB with a site spare. Tested ok. 4.2.6 - located near the sores loading dock. Found receiver PCB to be water damaged and the cover damaged. Replaced receiver PCB with a site spare. Removed security bolts and replaced with self tapper screws. Tested ok. 4.6.1 - receiver lid had been been pulled off damaging the nut surrounds. Removed all the security bolts and nuts. Replaced with self tapper screws. Tested ok. No faults remain on the MDAS system. Parts used:Consumables2 x receivers replaced with new
MSA-DCS | WA3076060 | Unit 7, Cell H12 - key can not poen the main lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 21 Feb 2020 | 2020-02-22 14:33:22 | 2020-02-21 16:15:00 | Pass | Job completed - service lock and replace fixings
MSA-DCS | WA3076083 | Control Room- Camera 20 - no night vision | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-12 09:00:00 | Fail | Camera replaced and configured
MSA-DCS | WA3076136 | Pre Release Unit - MDAS receiver post is rusted out - Zone 7 & 11 | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 21 Feb 2020 | 2020-02-28 17:00:00 | 2020-04-16 14:30:00 | Fail | MDAS conduits rerouted to new position and new post installed and concreted in. Reterminate and commissioned.
MSA-DCS | WA3076213 | CCTV Camera's have gone down. | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Feb 2020 | 2020-02-21 23:03:24 | 2020-02-24 12:09:00 | Fail | Investigated cause of failure, found that DVM software develops a fault and crashes after exactly 497 days of continuous operation on all camera servers. Repaired software faults and modified to automatically restart servers if this reoccures. Recommend restarting camera servers in a controlled manner once a year.Tested OKJob Complete
MSA-DCS | WA3258151 | ***Invoice purposes only**** - Unit 2, control room - P E Beam 12 & 17 constanting alarming. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Feb 2020 | 2020-02-22 11:47:52 | 2020-04-30 11:03:00 | Fail | Cyclone related to be completed under WA29977854
MSA-DTAG | WA3075568 | Cathedral - Intercom system went off, giving beep sound. | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 21 Feb 2020 | 2020-02-24 17:00:00 | 2020-02-21 16:00:00 | Pass | Found modules offline in SAT Building. Rebooted and tested
MSA-DTWD | WA3075217 | Theatres L2 & L3- Broken seats | Perth Campus B2 | GMP-BR | Furniture | Indoor Furniture (FU) | AWB Co. | 3 | CLOSE | 21 Feb 2020 | 2020-02-27 17:00:00 | 2020-06-09 12:30:00 | Fail | Theatres L2 & L3- Broken seats - Carried out repairs as per BRAF
MSA-DTWD | WA3075650 | Rooms 208,209.212 & 214 - Air con not working | Kwinana Automotive Centre | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 21 Feb 2020 | 2020-02-24 17:00:00 | 2020-05-22 16:00:00 | Fail | Works completed as per BRAF
MSA-DTWD | WA3076017 | E block, Skills Kitchen 3- 2 ovens and 1 fryer not working | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 21 Feb 2020 | 2020-02-26 17:00:00 | 2020-03-11 13:30:00 | Fail | 24/02/20204 ovens not working, two with leaks and others low pressure/ pilots going out.04/03/2020Replaced thermocouple on blueseal oven11/03/2020Fixed gas leak in fryer, moved 2 ranges, replaced thermocouple then tested and adjusted gas pressure
MSA-DTWD | WA3076084 | Block 7 - north east side of canteen - Evap air con is leaking | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 21 Feb 2020 | 2020-02-28 17:00:00 | 2020-05-04 13:00:00 | Fail | Travelled to site signed in. Carried out removal and installationof a new Evap unit on block 7 as per reported Braf
MSA-MRWA | WA3075578 | Western courtyard entry - Door not releasing please investigate and remediate | Materials Engineering Branch | GMP-BR | Security | Security Management System (SE) | Siemens Ltd | 1 | CLOSE | 21 Feb 2020 | 2020-02-24 17:00:00 | 2020-02-21 13:50:00 | Pass | the magnetic lock on the door is not fitted well and 'drags' on the frame, thereby resulting in the door not closing properly by itself
MSA-MRWA | WA3075912 | Level 5, Room 549 - remove fluro above desk | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | COMP | 21 Feb 2020 | 2020-02-26 17:00:00 | 2020-02-26 10:14:00 | Pass | Removed light above desk
MSA-DCS | WA3076288 | Cell call 521 not working | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Feb 2020 | 2020-02-23 09:16:02 | 2020-03-05 17:29:00 | Fail | Sourced CI-CC from Seme stockInstalled into cell and tested, loud and clear.Checked audio recordings and confirmed loud and clear
MSA-DFES | WA3076297 | Sliding gate to the carpark is not closing properly and its faulty | CFRS Perth- Perth FS-Car park | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 22 Feb 2020 | 2020-02-22 13:22:13 | 2020-02-22 11:45:00 | Pass | Damaged PE Beams, Replaced during visit to get operational
MSA-DCS | WA3076605 | pit 3,4 the security temper alarm is going off | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-23 10:10:00 | Fail | See job notes, tamper replaced operating correctly.
MSA-DCA | WA3078174 | Volunteers Office- Split AC unit leaking | A Shed, Victoria Quay, Fremantle-A-Shed-Ground Floor-Office - West | GMP-BR | Air Conditioning | Ducted Split System (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 24 Feb 2020 | 2020-03-03 17:00:00 | 2020-02-29 16:30:00 | Pass | Attended site 25-2-20. VSO office split AC leaking water. Applied tests and checks to find condensate pump U/S. Removed and replaced pump and carried out tests and checks. Investigation found inline OA fan system faulty and not operating correctly allowing fresh air ingress to applicable split AC offices. Removed and replaced inline fan and fan blade. Tested operation. System operating correctly with no leaks present.
MSA-DCS | WA3077645 | Gatehouse - internal secure lobby door - tongue on lock is falling out | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 24 Feb 2020 | 2020-02-24 12:59:09 | 2020-02-24 10:00:00 | Pass | repairs to lock
MSA-DCS | WA3077972 | Control rooms - command to change views is not working | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Feb 2020 | 2020-02-25 10:45:26 | 2020-02-24 16:11:00 | Pass | Attended site, reprogrammed views to displays and tested OK.Job Complete
MSA-DCS | WA3078332 | PTZ37 camera, is stuck and wont move | Boronia Pre-release | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Feb 2020 | 2020-02-24 17:49:59 | 2020-02-24 15:38:00 | Pass | Attended Boronia, found camera with fibre loss indication, site indicated they had a lightning strike and all monitors went black but system restored itself. Reset field modem and tested camera image restored, checked pan tilt and zoom functions all ok. No further action is required. job recalled 11/3/20 reattended site, found modem faulty, replaced S732DVT-EST1
MSA-DCS | WA3078358 | Unit 1, Cell C16- Cell door is broken | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 1 | CLOSE | 24 Feb 2020 | 2020-02-25 14:06:20 | 2020-02-25 11:45:00 | Pass | Cell door require replacement door. BRAF declined as works given to another contractor.
MSA-DCS | WA3078506 | Cell 32- Cell call is not working | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Feb 2020 | 2020-02-27 17:00:00 | 2020-04-08 16:00:00 | Fail | 8/4/2020removed faulty cell call and repaired faulty componets.reinstalled and testedCell Call was left onsite as spare
MSA-DCS | WA3078530 | Albany Regional Prison-Gatehouse - Extender from upstairs not working to connect to monitor 3 | Albany Regional Prison-Gatehouse | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Feb 2020 | 2020-02-27 17:00:00 | 2020-04-23 09:00:00 | Fail | Secure loose connection
MSA-DTAG | WA3077550 | Court Room 3 - Please inspect flooring for White ants | Perth Children's Court | GMP-BR-HO | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 24 Feb 2020 | 2020-02-25 17:00:00 | 2020-02-25 14:15:00 | Pass | Attended and fixed a bait box in the passageway in stud wall where termites were present.Will monitor bait box at end of next week. this may be monitored regularly for 6 months.High Tech Pest Control has provided a Quote for treatment to Niall Dwyerwhich has been approved. We will use BRA form to adjust the price of the work orderas instructed by Niall.9/3/20- termites are active in bait box.Sentricon(R) Allways Active installed around outside of courthouse Monitoring to continue4/5/20 Termite activity in bait box now ceased. No activity in IGS outside. Continuing to monitor.
MSA-DTWD | WA3077742 | E Block, E37 walk in freezer is icing up | Bentley Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 24 Feb 2020 | 2020-02-25 17:00:00 | 2020-03-24 10:30:00 | Fail | Returned to site with Askin Sub contractor for freezer door heater. Isolated and disconnected. Sub contractor identified brakage in New heater cables. Repaired. Once pannels back in place reconnected electrically and tested. Heater operation confirmed.
MSA-DTWD | WA3078017 | T Block footpath- sewerage pump controller light flashing | Murdoch Campus | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 24 Feb 2020 | 2020-02-25 17:00:00 | 2020-04-11 17:00:00 | Fail | replaced transducer
MSA-DTWD | WA3078094 | Campus Grounds- Possible ammonia leak | Carlisle Campus | GMP-BR | Refrigeration | Refrigerators (RE) | ACME INTERNATIONAL REFRIGERATION ENGINEERS PTY LTD | 0 | CLOSE | 24 Feb 2020 | 2020-02-24 15:37:57 | 2020-03-11 11:29:00 | Fail | Reason for call:Ammonia leak on cool room pm valveService details::Got call about ammonia leak,drove to site and spoke to Glen,got inside and checked around forammonia leak,found ammonia leaking thru top spindle of suction pm valve,isolated ammonia valvesand tagged out,pumped out all ammonia from evaporator and suction pm valve,ran extraction fan toremove ammonia from area,pm valve will need to be replaced,will send thru quote to replace at
MSA-DTWD | WA3078336 | A block Cygnet building, Room 2.05 &2.06- air con not working & burning smell | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 24 Feb 2020 | 2020-02-25 17:00:00 | 2020-03-03 12:00:00 | Fail | Attended site and signed in, air-conditioning system number 4 was faulty and had a burning smell. Found the drain pan had flooded and could of caused some water to splash onto the evaporator motor . Found some insulation had fallen off and blocked the drain , unblocked and made sure no other insulation was going to fall.The system has four thermostat that serve four seperate rooms , thermostat four was faulty. Drove to suppliers and picked up a new one, returned and fitted , test ran all ok.
MSA-DTWD | WA3078396 | J Block - Evaps not cooling | Rockingham Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 24 Feb 2020 | 2020-02-27 17:00:00 | 2020-03-03 08:00:00 | Fail | Travelled to site signed in. Located Evaporative units located in J block. Found that fans were spinning backwards. Reversed phases to change direction. Possibly due to new isolator install. Pads on one unit heavily sagging causing water to leak out of unit. Belt is worn and requires replacement. A pump is required on the other unit. A braf will be created. Existing Braf has already been submitted for repairs, Awaiting on Campus for approval for repairs.
MSA-DTWD | WA3078423 | T Block - 2nd Floor - Air Con is leaking east end near window | Murdoch Campus | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 24 Feb 2020 | 2020-02-25 17:00:00 | 2020-04-04 13:00:00 | Fail | Works completed as per BRAF
MSA-DTWD | WA3078428 | E block, Skills kitchen 1- Tap on 3rd bench on right hand side in kitchen is faulty | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Feb 2020 | 2020-02-27 17:00:00 | 2020-02-25 15:30:00 | Pass | COMPLETED
MSA-DTWD | WA3078451 | Car park roller gate back of 30Ab - has broken remote for control 610158 | Perth Campus B2 | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 24 Feb 2020 | 2020-03-03 17:00:00 | 2020-04-03 10:32:00 | Fail | Attended site and in Inspected gate and found that site would like 2x additional remotes for the gate, one to replace the broken one and one as a spare. See pictures attached for remotes that are required.Returned 3/4/20 - Coded new gate remotes. Tested ok.
MSA-MRWA | WA3077835 | Level 3 - 3.101 Pick up sit stand desk at reception deliver and install. | Don Aitken Centre MRWA Head Office | GMP-BR | Furniture | Office Furniture (FU) | MR - Handyperson - PFM | 1 | COMP | 24 Feb 2020 | 2020-02-25 17:00:00 | 2020-02-25 15:23:00 | Pass | Installed desk
MSA-MRWA | WA3078011 | Level 8 Outside male toilet in hallway - Light flickering, please remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 24 Feb 2020 | 2020-02-25 17:00:00 | 2020-02-24 15:21:00 | Pass | Replaced flashing globes
MSA-MRWA | WA3078370 | Mechanical Plant, Secondary Chilled Water Loop not operational please attend & remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Refrigeration | Refrigerators (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 24 Feb 2020 | 2020-02-25 17:00:00 | 2020-02-24 16:30:00 | Pass | ACCESSED SITE AND SHOWN BMS IN ALARM. SECONDARY CHILLED WATER LOOP NOT OPERATING. ACCESSED ROOFTOP PLANT FOUNDWATER PUMPS AND COOLING TOWERS ISOLATED. REINSTATED POWER AND TEST RAN ALL EQUIPMENT. BMS NOW SHOWING SYSTEM STATUS AND COOLING CALL ACTIVE.
MSA-DCS | WA3078774 | Unit 10 B10 medical hatch lock can be opened without keys | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 25 Feb 2020 | 2020-03-03 17:00:00 | 2020-07-15 14:00:00 | Fail | Supplied and fitted replacement hatch and lock.
MSA-DCS | WA3078877 | Camera 167 & PTZ 172- not working in external zone 17 | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Feb 2020 | 2020-02-25 11:54:56 | 2020-03-12 14:30:00 | Fail | Cameras appear to have been affected by a power outage. Power supplies tested ok. Reset power to both cameras. Image and all PTZ functions tested ok. Parts used :Consumables
MSA-DCS | WA3078888 | Unit 14, A & C Dayroom kitchen- stainless steel drawers tracks need replacing | Casuarina Prison | GMP-BR- HO | Furniture | Office Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 25 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-27 11:00:00 | Fail | DRAWER RUNNERS REPLACED
MSA-DCS | WA3079003 | Social visits room - Camera 7 not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Feb 2020 | 2020-02-26 08:40:28 | 2020-03-18 10:30:00 | Fail | Configured and installed repaired indigo ptz ip dome camera. Job completed.
MSA-DCS | WA3079135 | Entry to carpark light pillar has fallen over | Boronia Pre-release-External Area-Ground Floor-Visitor Car Park | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-26 14:00:00 | Fail | Replaced damaged bollard after sourcing replacement.
MSA-DCS | WA3079309 | Industries Admin- small leak coming from the urn | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-19 15:04:00 | Fail | Pick up unit from a supplier, remove old unit, install new unit and calibrate
MSA-DCS | WA3079690 | Kitchen- Fridge not cooling | Banksia Hill Detention Centre | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-23 15:00:00 | Fail | Carriedout the pressure test found the leak in charging valve, replaced shreded core . Vacuumised the system and charged the refrigerant.
MSA-DCS | WA3079741 | Bulk stores offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Feb 2020 | 2020-03-04 17:00:00 | 2020-02-25 16:00:00 | Pass | Replaced and programmed new network switch as switch was faulty. Planet network switch used. All replaced, programmed and tested ok. Job complete, site stock used. Requires replacement to replace site stock.
MSA-DCS | WA3079823 | Unit 1, B & D Wing- dog runs has damaged mesh | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-05-19 15:30:00 | Fail | 04/03/20Job inspected.Areas require welding.Needs to be carried out on a lock down day.19/05/20Installed 358 mesh to Unit 1 main yard
MSA-DCS | WA3079851 | Unit 3, A & C- Outside black fence falling over | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-05-19 15:30:00 | Fail | 04/03/20Inspected and have measured up for work. May require BRAF.19/05/20Installed 2 x end posts to Unit 3
MSA-DCS | WA3079925 | CCTV control panel is not functioning | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-31 16:10:00 | Fail | Attended aite, investigated hardware and repaired software operating system fault on door control computer in control room.Tested OKJob Complete
MSA-DTWD | WA3078939 | L Block, Lift 3 is not operationing correctly | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 25 Feb 2020 | 2020-02-26 17:00:00 | 2020-02-25 12:30:00 | Pass | Not charegable
MSA-DTWD | WA3079014 | S Block, S4 fume cupboard (S7) sink is leaking | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-02-27 20:15:00 | Pass | sealed hole in sink
MSA-DTWD | WA3079026 | S Block, Store room S3/1 fume cupboard float level faulty | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-02-27 14:30:00 | Pass | replaced float valve
MSA-DTWD | WA3079195 | Between J005 & J006- Wooden decking is damaged | Balga Campus | GMP-BR | Flooring | Timber (FL) | AWB Co. | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-04-14 16:00:00 | Fail | Carried out works to decking as per BRAF
MSA-DTWD | WA3079646 | Lvl 4,Plant room- grundfos pump not reticulating hot water | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 25 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-11 17:00:00 | Fail | replaced check valve, function to be monitored
MSA-DTWD | WA3079651 | Lvl 1, Room D111- Leaking Oxygen Regulator | Perth Campus B4 | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 25 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-26 14:00:00 | Fail | repaired leak on compressed air reg, replaced oxygen reg
MSA-DTWD | WA3079712 | G Block, Drains in laundry are blocked | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-04-24 10:00:00 | Fail | repaired drain as found when floor cut
MSA-DTWD | WA3079713 | A Block Staff lunch room - Wall mounted urn is providing hot water | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 25 Feb 2020 | 2020-02-26 17:00:00 | 2020-02-26 11:22:00 | Pass | Reconnected water
MSA-DTWD | WA3079714 | B Block, Lvl 4, cleaners store- drains are blocked | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-02-26 11:30:00 | Pass | cleared waste pipe to stack
MSA-DTWD | WA3079722 | G Block Air con software not communicating with plant | Rockingham Campus | GMP-BR | Air Conditioning | Package (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-05-19 15:27:00 | Fail | Visit 1 Checked over Block G AHU, found it to start on each occasion, time scheduling is all OK.Unable to replicate reported fault of AHU not starting in the morning.Found HWP VSD offline, tested LAN > OK.Tested VSD network interface > faulty.HWP VSD to be replaced. Visit 2 Supply, install and commission one (1) new ABB ACH-580 IP54 1.1kW VSD to replace existing ACH-550 as per quote, Visit 3 completed Upgrade of obsolete EC-BOS-6 with new EC-BOS-8 web controller as per BRAF.
MSA-DTWD | WA3079806 | V Block workshop wash trough taps are staying on | Rockingham Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-19 14:30:00 | Fail | replaced 2x taps, repaired 1
MSA-DTWD | WA3079917 | Lvl3, Staff Room- Air Con is too hot | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 25 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-25 11:00:00 | Fail | Accessed plant area and unit supplying staffroom.Checked airflow fan speed settings,ok and still adequate.Replaced ra filters with new and ensured temps and airflow in room not affected. Rectified insulation deteriorantion in return air plenumn and adjusted fresh air inlet to suit. Returned unit to service
MSA-DTWD | WA3079948 | E Block, E75 kitchen- 4x taps are loose | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-05 21:00:00 | Fail | repaired various fixtures through e74 and e75
MSA-DCA | WA5676713 | RETROSPECTIVE WORK ORDER-Lift - stuck on level 2, doors closed. | PICA-Main Building | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | COMPFIN | 26 Feb 2020 | 2020-02-27 17:00:00 | 2020-02-26 15:17:00 | Pass | Lift1 PICA-MRL :Lift stopped on top floor due to power outage , reset main processor and tested , couldn't duplicate fault left lift running
MSA-DCA | WA6001146 | RETROSPECTIVE DO NOT ATTEND-Lift 1 stopped - INV PURPOSE ONLY | PICA-Main Building | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | COMPFIN | 26 Feb 2020 | 2020-02-26 17:00:00 | 2020-02-26 15:17:00 | Pass | Lift stopped on top floor due to power outage , reset main processor and tested , couldn't duplicate fault left lift running
MSA-DCS | WA3080174 | Gatehouse - Camera's 50, 65, 66, 67, 68, 117 have no picture | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 07:20:11 | 2020-03-30 13:17:00 | Fail | Investigated and repaired multiple cameras, found multi-channel analog fibre modem had failed. Parts are no longer manufactured so I installed a stand alone 4 channel encoder locally in admissions to allow recording and viewing locally and in gatehouse on DVM. These cameras will be available on video wall when digital upgrade project is complete.Job Complete
MSA-DCS | WA3080316 | Hakea Training Demountable - possibility of unstable ground due to rabbit burrows | Hakea Prison | GMP-BR- HO | Building | Foundations (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 Feb 2020 | 2020-03-03 17:00:00 | 2020-03-05 14:45:00 | Fail | No approval to proceed.
MSA-DCS | WA3080832 | Security unit (unit 4) - Microwave PPE number 4 in fault | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 11:55:00 | 2020-04-20 12:01:00 | Fail | Job has been completed and PE beams are operational
MSA-DCS | WA3081065 | Cell call MPU constant buzzing | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 Feb 2020 | 2020-03-05 17:00:00 | 2020-02-26 13:00:00 | Pass | Replaced cell call due to water damage/condensation issue in unit. All replaced and tested ok. Job complete. Site spare used.
MSA-DCS | WA3081070 | Freeze frame not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 Feb 2020 | 2020-03-05 17:00:00 | 2020-05-26 22:45:00 | Fail | Installed second monitor, KVM and wireless keyboard and mouse combo
MSA-DCS | WA3081120 | Unit 1B, Camera 6 is offline | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Feb 2020 | 2020-02-26 17:28:01 | 2020-03-19 09:00:00 | Fail | Replaced unit 1 with 2 x new Planet network switches and 4 x SFP ports. All programmed and tested ok. Cameras working ok with constant Ping. Job complete
MSA-DCS | WA3081131 | Unit 12- A B wing office door- keys are getting jammed | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 13:35:46 | 2020-02-27 11:20:00 | Pass | Job completed - Attend site, inspect door lock require replacement cylinder, return and replace cylinder
MSA-DCS | WA3081176 | Control Room - Master computer screen not working (main display for perimeter security) | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Feb 2020 | 2020-02-26 18:00:55 | 2020-03-13 12:30:00 | Fail | Discrepancy between EBI workstation 4 and the more detailed maps on other workstations. Checked through programming and maps. Tested ok from the field to the control room.
MSA-DCS | WA3081203 | Unit 8 A & B Wing control door - time delay to lock door too long | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Feb 2020 | 2020-03-03 17:00:00 | 2020-03-16 08:30:00 | Fail | Rectified and fixed electronic lock time delay, job completed.
MSA-DCS | WA3081212 | Unit 4, J Block, Main kitchen drain blocked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 14:32:16 | 2020-03-03 15:15:00 | Fail | Cleared blockages to kitchen sinks and 1 x wc pan
MSA-DCS | WA3081269 | Genator control box - warning light showing high fault | Wooroloo Prison Farm | GMP-BR- HO | Security | Access Control (SE) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 15:13:21 | 2020-02-27 12:00:00 | Pass | Unable to find wiring diagram, advise site contact to seek a n electrical contractor with access to wiring information.
MSA-DCS | WA3081331 | Unit 11 - A B wing office door, not closing properly. | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 16:39:25 | 2020-02-28 11:30:00 | Fail | Job completed - Attend site, temporarily secure door, additional parts required. Return to site supply and install replacement mortice lock andstrike.
MSA-DCS | WA3081335 | Hakea-Melaleuca Prison unit 12 GRD level pod office door B wing, officer key snapped in lock | Melaleuca Prison | GMP-BR- HO | Carpentry | Materials (CA) | AAA Ability Locksmiths | 0 | CLOSE | 26 Feb 2020 | 2020-02-26 21:13:42 | 2020-02-26 19:00:00 | Pass | removed broken key from lock.
MSA-DTAG | WA3080246 | Custody corridor- Ceiling haas caved in due to storm damaged | Joondalup Courthouse | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 26 Feb 2020 | 2020-02-26 11:59:48 | 2020-03-07 08:30:00 | Fail | COMPLETE - WATER DAMAGE REPAIRED
MSA-DTAG | WA3080674 | Ground floor, Lift 9 - lift is out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 17:00:00 | 2020-02-26 14:32:00 | Pass | Apparently doors cycling level 3 no faults in error log for the day. Checked over every floor landing doors all free and makingelectrical contact. Checked car doors all ok. Tested lift at all floors unable to fault. Cleaned light rays
MSA-DTAG | WA3081074 | Lift No.1 has “dropped” / jolted while a staff member was inside | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 26 Feb 2020 | 2020-03-03 17:00:00 | 2020-02-27 11:45:00 | Pass | Not charegable
MSA-DTWD | WA3080241 | A Block Level 4 Stairwell ceiling damage near A401 | Leederville Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 26 Feb 2020 | 2020-02-26 17:00:00 | 2020-03-11 11:00:00 | Fail | As per BRAF
MSA-DTWD | WA3080245 | C Block has multiple roof leaks | Carlisle Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 17:00:00 | 2020-05-12 15:30:00 | Fail | Works completed and new box gutter is installed - See photos attached
MSA-DTWD | WA3080289 | Block 3, heavy plant store has water from evap air con into store room | Thornlie Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 26 Feb 2020 | 2020-03-03 17:00:00 | 2020-05-19 16:30:00 | Fail | Works completed as per BRAF
MSA-DTWD | WA3080318 | Isolate power in various locations on campus - due to storm | Balga Campus | GMP-BR-RC | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 26 Feb 2020 | 2020-02-26 12:36:15 | 2020-03-24 10:53:00 | Fail | Attended site. Wired up new pole light onto pole. Installed pole onto rag bolts and levelled. Tested and reset timeclock to correct time. Cleaned up site. Job completed .**Risk Cover Claim No: 20110884-1******
MSA-DTWD | WA3080520 | BLD 834, Switchboard- faulty RCDS | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 26 Feb 2020 | 2020-03-03 17:00:00 | 2020-05-07 15:06:41 | Fail | Replaced RCD 16amp
MSA-DTWD | WA3080768 | H Block Creche - has an ant infestation on the patio | Rockingham Campus | GMP-BR | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 26 Feb 2020 | 2020-02-27 17:00:00 | 2020-02-28 13:35:00 | Fail | Ant infestation on the patio. Sprayed patio area for infestation of ant nest. 5 litres of Termidor used.
MSA-DTWD | WA3080781 | Canteen - cockroach & mouse infestation | Rockingham Campus | GMP-BR | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 26 Feb 2020 | 2020-03-03 17:00:00 | 2020-02-28 14:10:00 | Pass | Canteen cockroach and mouse infestation.Carried out cockroach & mouse treatment and baiting - all work completed.
MSA-DTWD | WA3080838 | Q block, Ground floor- 3 Door frames to wards are damaged | Joondalup McLarty Campus | GMP-BR | Building | Doors (BU) | M Construction (WA) | 2 | CLOSE | 26 Feb 2020 | 2020-03-03 17:00:00 | 2020-05-15 07:38:00 | Fail | Job complete
MSA-DTWD | WA3081308 | Level 2, Room A206- Blinds Broken | Perth Campus B5 | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 26 Feb 2020 | 2020-03-05 17:00:00 | 2020-03-09 10:00:00 | Fail | repaired broken blinds
MSA-MRWA | WA3080413 | Level 5 - Room 537 - remediate squeaky door | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 1 | COMP | 26 Feb 2020 | 2020-02-27 17:00:00 | 2020-02-27 15:09:00 | Pass | Lubricated hinges to make quiet
MSA-MRWA | WA3081282 | Level 3, Chiller Plant Room - Check operation of Afterhours cooling Call | Traffic Operations Centre | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 26 Feb 2020 | 2020-03-03 17:00:00 | 2020-02-27 16:30:00 | Pass | Will provide quote to install run light next to push button.
MSA-MRWA | WA3365694 | Retrospective PO, please do not attend - secondary chilled water loop control not working | Don Aitken Centre MRWA Head Office | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 26 Feb 2020 | 2020-02-28 17:00:00 | 2020-06-11 15:14:00 | Fail | COMPLETEDRefer to work order WA3078370
MSA-DCA | WA3082074 | Main public Lift - Lift is making loud grinding noise when moving between ground and level 1 | Maritime Museum Victoria Quay-Main Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 17:00:00 | 2020-02-27 13:30:00 | Pass | job completed - the technician performed the following - HYDRAULIC RAM/CYLINDER - HYD SEALS - COMPONENT NOISY CORRECTED
MSA-DCS | WA3081681 | Crisis care control room carpet damaged | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Feb 2020 | 2020-03-05 17:00:00 | 2020-08-12 10:07:00 | Fail | DAMAGED CARPET WAS REMOVED/UPLIFTED ONLY ON THIS JOB - NEW CARPET INSTALLED ON JOB #WA3413552
MSA-DCS | WA3081682 | Unit 10 Cell A5 tiles damaged on floor near bed | Hakea Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Feb 2020 | 2020-03-05 17:00:00 | 2021-02-18 10:34:00 | Fail | BUNK BEDS REMOVED FOR FLOOR/VINYL REPAIR THAN REPLACEDTILING WILL BE COMPLETED ON #WA3279530
MSA-DCS | WA3081735 | Unit 3 B Wing cleaning cupboard door needs repair - rotted at the base | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Feb 2020 | 2020-03-05 17:00:00 | 2020-03-25 13:30:00 | Fail | NEW DOOR INSTALLED
MSA-DCS | WA3081762 | Front gate - cashiers office - air con is not running | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 08:01:17 | 2020-03-12 15:15:00 | Fail | Replaced control and sensor. All operational.
MSA-DCS | WA3081857 | Education 1-Panel saw not operating correctly suspect bearing or motor issue due to loud noise. | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Power Tools (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 27 Feb 2020 | 2020-03-06 17:00:00 | 2020-03-04 13:30:00 | Pass | Job completed - Panel saw motor faulty. Check motor & controls. Dismantle & repair wiring on contactor. Assemble & test.
MSA-DCS | WA3081935 | CCU (11), D4 - Camera needs cleaning | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Feb 2020 | 2020-03-06 17:00:00 | 2020-04-14 07:56:00 | Fail | Job complete under WA3176444
MSA-DCS | WA3082000 | Unit 14, A & C oven outlet/overflow hose blocked | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-23 09:25:00 | Fail | Hose Breaking away on inside & blocking up, cut off bad end and refitted. Returned with new hose & replaced.
MSA-DCS | WA3082046 | MPU wing, Store room door - defective door handle requiring replacement. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 27 Feb 2020 | 2020-03-06 17:00:00 | 2020-04-10 11:30:00 | Fail | Job completed - replace mortise lock, cam and internal handle
MSA-DCS | WA3082062 | Unit 7, A wing, Laundry - Light is flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-05-15 09:30:00 | Fail | Investigated faulty lights in unit 7. Ordered replacement emergency power pack. Rewired supplied light, installed and tested.
MSA-DCS | WA3082523 | pharmacy, located in stores area outside the prison - roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 11:41:36 | 2020-05-05 16:46:00 | Fail | located leak and rectified
MSA-DCS | WA3082553 | Vege prep ,potato rumbler ,rubber doorflaps is damaged | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-02-27 13:00:00 | Pass | Installed new seal
MSA-DCS | WA3082677 | Gym, Basket ball court - Roof leaks in gym | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Concrete Roof Construction (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-08-12 10:02:00 | Fail | REPAIRS TO AIR VENTS ALONG LENGTH OF ROOF AND POLY CANS FLASHING'S
MSA-DCS | WA3082703 | Salon- Roof leak | Bandyup Prison | GMP-BR- HO | Roofing | Tiled Roofing (RF) | Schlager Construction Group | 3 | CLOSE | 27 Feb 2020 | 2020-03-06 17:00:00 | 2020-03-16 16:00:00 | Fail | Attended site and carried out repairs to the roof area to stop water penetrating and damaging ceilings.
MSA-DCS | WA3082726 | Everpure filtered hot and cold water tap not dispensing hot water. Filter indicator light flashing | Nyandi Training Academy-Pilbara Wing | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-16 13:25:00 | Fail | DIAGNOSED ISSUES WITH VERY OLD UNDERSINK BWU - CANNOT BE REPAIRED - ADVISED AND QUOTED FOR NEW CAPEX ASSET REPLACEMENT - BILLI QUADRA COMPACT LCH UNIT INSTALLED SERIAL NUMBER R126100741LCH REMOVED OLD SYSTEM TO TIP PROG SN A40183998A
MSA-DCS | WA3082731 | Check high gas pressure reading | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 13:46:03 | 2020-03-03 11:00:00 | Fail | Test gas supply pressure. Gas supply is 7.2 kPa. An OPSO valve is required to be installed.
MSA-DCS | WA3082775 | Interview room 3 - Door (public side) does not latch shut | Mandurah | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 27 Feb 2020 | 2020-03-06 17:00:00 | 2020-03-03 11:10:00 | Pass | Job completed - Attend site repair and adjust strike plate to Interview room 3 door for correct operation
MSA-DCS | WA3082778 | Demountable Training Room 5 - entry door not closing due to hinges. Door dropping at top hinge area | Nyandi Training Academy-Staff Training Transportable 5 | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-27 13:15:00 | Fail | Attended site and carried out measurements for door replacement.Carried out modifications to door frame to strengthen so new block door can be installed.Supplied and installed new 1060mm x 2160mm x 35mm external block door.Sealed and applied 2 coats of gloss paint to new door.Repainted door frame and archives colour to match existing.
MSA-DCS | WA3082786 | EC2 – IP41.02.05 Microwave tamper | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Feb 2020 | 2020-03-06 17:00:00 | 2020-05-22 20:09:00 | Fail | Replaced with Senstar MPS4100 from site stock
MSA-DCS | WA3082789 | Unit 1, Cell C9- cell call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 14:40:51 | 2020-02-27 17:45:00 | Pass | Tested cell call in unit 1, cell 9- faulty device.Replaced cell call unit, tested- all ok.Used 1x CI-CC/270/120- replacement to go to site stock
MSA-DCS | WA3082804 | Expander 46:01 Offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Feb 2020 | 2020-03-06 17:00:00 | 2020-02-28 20:00:00 | Pass | Installed new gallagher 8 input expander as expander was faulty and dropped offline. All replaced programmed and tested ok. Job complete. 1x 8 input expander used site stock
MSA-DCS | WA3082899 | Hakea Prison-Main Gatehouse Control - no cameras activating - alarms activating | Hakea Prison-Main Gatehouse | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Feb 2020 | 2020-02-27 22:19:28 | 2020-02-27 22:45:00 | Fail | Issue with EBI and senstar integration, found senstar operating correctly indicating correct alarms found EBI responding, reset workstation for video wall with no change, changed EBI over to slave and indicated operating correctly, reset EBI server 1 and brought back online, switched back to master and tested now operating correctly. No further action is required system fully restored.
MSA-DCS | WA3082910 | Lenard, Turner, Murchison - No cell call systems working. | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Feb 2020 | 2020-02-28 00:55:20 | 2020-03-19 11:45:00 | Fail | Replaced cell call backup batteries in Lenard and Muchison, tested all ok after replacement. 12V 26 Ah X 2
MSA-DCS | WA3082917 | Fire alarm won't reset - Unit Lenard | Banksia Hill Detention Centre-Gatehouse | SPA-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 27 Feb 2020 | 2020-02-28 01:56:54 | 2020-04-01 12:32:00 | Fail | Banksia hill network issues caused by lighting strikeOn site 11pm till 2amAttended site to continue investigation after lighting strike found 7 nodes offline and network faults.After investigation managed to get network online and most nodes back online apart from node 11 Lenard and node 5 education which both requires parts (see below). Node 9 Lenard is online but only 50% of detection is working due to parts required see below. Notified site on state of fire system when left sitelendard unit offline node 11 - this requires a new simplex 4100 PSU site has been notified that the unit is offline to the fire system.Banksia eduction node 5 is offline and site notified - requires a new simplex network card kit and 2 network media cards it a older style network card installed at the moment which will need to upgraded to the newer one. Will need to confirm if we need the motherboard for this one with Shaun Scudds or we can just replace the older card with the newer style with the me
MSA-DCS | WA3082920 | 9 cameras malfunctioning due to lightning strike | Banksia Hill Detention Centre | WSM-BR-RC | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Feb 2020 | 2020-02-28 02:46:47 | 2020-06-24 15:20:00 | Fail | Multiple faults after lightning storm. Replaced multiple parts on duress and CCTV system, replaced faulty perimeter cameras. Unable to source some analog hardware as it is now obsolete.Separate project in progress to upgrade analog system to digital.Job Complete
MSA-DCS | WA3082921 | Fire Panel Fault cannot reset. | Karnet Prison Farm | SPA-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 27 Feb 2020 | 2020-02-28 03:00:13 | 2020-02-28 18:00:00 | Fail | Complete
MSA-DFES | WA3082817 | Strategy governance area -roof water leak & water marks above Shelley Staff desk | DFES Cockburn Emergency Services Complex-Main Building-Level 2 | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-20 14:00:00 | Fail | Carried out repairs, sealed joins in rainhead
MSA-DTAG | WA3082873 | Jury room to court 2 (near 217) - ceiling leaking, water entry possilby from the roof. | Supreme Court-Supreme Court Building-Level 1 | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 17:00:00 | 2020-04-15 08:50:00 | Fail | located leak and repaired
MSA-DTWD | WA3082546 | E block. LSK- Prover not working. Possible element issue | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-11 16:30:00 | Fail | 28/02/20Arrived on site, found the internal c/b had tripped and the float valve sticking, fixed float valve and reset c/b and it tripped. Found the on/off selector switch was sticking on, contact had fused together, Broke it free and switch is operating properly again, Tested elements and the wet element is faulty not drawing current09/03/20Returned to site to fit the element, found there isn't a nut for the new element and had to use the old nut which broke. I also had to replace the float ball and float valve. I fitted a new water tap in the line too as other one didn't work. Currently the prover is still out of service, due to not having a nut.Will need to return with a nut.11/03/20 Returned to site to fit nut to element Tested unit Test ok
MSA-DTWD | WA3082577 | D block. Ground floor access toilet door not locking | Joondalup Kendrew Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-05-08 17:05:00 | Fail | Inspected door and found motor had over heated and controller not working on ditek unit also found mag lock failing on privacy kit. Recommend upgrade to ed100 with slide Chanel and full privacy kit with mini mag lock. Existing unit is normally only spect for domestic use. Braf raised and approvedAttended 8/5/20 - Completed works as per quote.
MSA-DTWD | WA3082651 | Remove and make safe broken branches in gum trees on Oxford St & Richmond St | Leederville Campus | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | SPECIALISED TREE LOPPING | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-07 11:30:00 | Fail | No completion notes
MSA-DTWD | WA3082706 | C Block C101 & C107 ceiling tiles are dislodged | Balga Campus | GMP-BR | Building | Ceiling (BU) | M Construction (WA) | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-30 14:40:00 | Fail | Job complete
MSA-DTWD | WA3082768 | Walkway- U and V blocks gutters damaged from storm | Joondalup McLarty Campus | GMP-BR | Roofing | Guttering (RF) | M Construction (WA) | 3 | CLOSE | 27 Feb 2020 | 2020-03-06 17:00:00 | 2020-03-23 14:02:00 | Fail | Job complete gutter was existing stock contractor had from another job
MSA-DTWD | WA3082811 | Fire Panel reported an earth fault | West One Services | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-04 09:00:00 | Fail | Found panel earth fault was non existantant after reset .Looked at bell strobe,cards, could not see visual carosion.
MSA-MRWA | WA3082638 | ground floor, female & male toilets, door closer - closing to fast, hydraulics not working | Heavy Vehicle Services | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-02-28 10:15:00 | Pass | Installed 2 x new door closers
MSA-MRWA | WA3082676 | Not able to arm alarm, please see Tina Mcdermott- see notes below | Office and Warehouse-Malaga | GMP-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Feb 2020 | 2020-02-28 17:00:00 | 2020-03-24 09:30:00 | Fail | Job completed - installed part on zone 33, wire and test. All ok
MSA-MRWA | WA3082857 | Inspect and clean ceiling vents in the male and female bathrooms | Materials Engineering Branch | GMP-BR | Cleaning | Cleaning (CL) | MR - Handyperson - PFM | 2 | COMP | 27 Feb 2020 | 2020-03-04 17:00:00 | 2020-03-04 10:01:00 | Pass | Cleaned all the vents in male and female toilets
MSA-DCA | WA3083351 | Water through large front windows | King Street Arts Centre-Main Building-Level 1-Meeting Room 1 | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-03-05 15:30:00 | Pass | Located suspected leak and sealed with roofing silicone
MSA-DCA | WA3083577 | Directors office, Room 2.37- water ingress into window | State Library of WA-Main Building-Level 2-2.7 - Storage Room | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 28 Feb 2020 | 2020-03-03 17:00:00 | 2020-03-03 14:45:00 | Pass | Directed by Reese Whitney to close off job and quote works as access to the roof was going to be costly
MSA-DCS | WA3082926 | Camera malfunctions + DGP Unit Leonard B & C Wings - Faults. | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Feb 2020 | 2020-02-29 02:41:03 | 2020-02-28 19:00:00 | Pass | Completed see job notes for details
MSA-DCS | WA3083134 | Alarm on main cell call system is not working | Karnet Prison Farm | GMP-BR-RC | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Feb 2020 | 2020-02-28 11:01:24 | 2020-06-11 20:13:00 | Fail | Installed 2 full duplex cell calls and Cat6 cable back to gatehouse from MPC cells.Connected to system and confirmed correct operation
MSA-DCS | WA3083166 | potable main water pumps keep tripping rcd | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Feb 2020 | 2020-03-06 17:00:00 | 2020-03-17 15:00:00 | Fail | Investigate potable water pumps. Motor c/b’s require replacement. Requires quoteSource parts. Replace motor c/b’s and auxiliary contacts for potable water pumps
MSA-DCS | WA3083286 | Unit 9 Sale A2 the main lock is faulty | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 1 | CLOSE | 28 Feb 2020 | 2020-02-29 07:43:09 | 2020-02-28 12:30:00 | Pass | JOb completed - service lock on cell.
MSA-DCS | WA3083292 | Unit 6 A wing day room roof leaking near the fridge | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Feb 2020 | 2020-03-04 17:00:00 | 2020-05-05 16:53:00 | Fail | located leak and rectified
MSA-DCS | WA3083375 | Unit 4, J Block, Cell L4- roof leak | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-06-12 13:09:00 | Fail | located leak and rectified
MSA-DCS | WA3083378 | Education, Store room- ceiling is damaged due to water leak | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Schlager Construction Group | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-06-26 11:00:00 | Fail | Attended site and carried out repairs to the damaged vent in ceiling.
MSA-DCS | WA3083380 | Program room behind salon- Roof leak | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-05-27 15:00:00 | Fail | REPLACED SHEETING AND SEALED ROOF PENETRATIONS - GENERAL MAINTENACE
MSA-DCS | WA3083442 | CCu, Office - DVR locked up/ frozen. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-03-04 10:30:00 | Pass | Job complete
MSA-DCS | WA3083450 | Fire Pumps are running. | Karnet Prison Farm | GMP-BR-RC | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 28 Feb 2020 | 2020-02-28 13:00:33 | 2020-04-17 09:38:00 | Fail | Callout to pump running after lightning strike – pump had been turned off by site as water spraying from pump. Pressure relief valve blow off pump, requires replacement. Charger Card and Power supply board with water damage. Parts ordered and installed, pump batteries found to be flat and replaced.
MSA-DCS | WA3083496 | INF(10)- Air Con control panel has a fault unable to turn vents off in cells | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-04-03 16:37:00 | Fail | Investigated faults, repaired multiple data network faults and tested OK.Job Complete
MSA-DCS | WA3083591 | Visits, Camera 7 is not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Feb 2020 | 2020-02-29 10:13:13 | 2020-03-13 16:30:00 | Fail | Duplicate job. Work to be completed under work order WA3079003 SEME #90220388.
MSA-DCS | WA3083884 | Tamper alarm fault- error code listed below | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Feb 2020 | 2020-02-29 12:04:32 | 2020-03-28 14:39:00 | Fail | Attended site- investigated tamper alarm- identified perimeter network fault for entire perimeter. Checked equipment in field- accessed and inspected all Field Processors and traced Fault to failed power supply to data modems - restores power supply to modems and checked Field Processors- communications restored- recommend further works to install redundant power supply to data modems in field.Perimeter system functioning correctlyFurther works to be quoted - No claim related to these works - please close work order
MSA-DCS | WA3083937 | Gallagher system is not responding | Karnet Prison Farm | GMP-BR-RC | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-03-11 14:17:00 | Fail | replaced kvm extender for cardax system at front desk. all tested , all ok
MSA-DCS | WA3083940 | Camera monitor 2 not functioning | Karnet Prison Farm | GMP-BR-RC | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-02-28 17:40:00 | Pass | Replaced KVM with site spare.Installed 5vdc power supply, all indigo monitors are operational
MSA-DCS | WA3083958 | Gatehouse - Gate intercoms are not working. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Feb 2020 | 2020-02-29 12:41:24 | 2020-04-08 18:22:00 | Fail | Replaced intercom base station and intercom,Tested all intercom connected to station,Loud and clear
MSA-DCS | WA3084189 | Monitors in control room is down for camera | Boronia Pre-release-AH19 - Administration, Education Senior Officers and Programs | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Feb 2020 | 2020-02-29 01:48:52 | 2020-02-29 08:15:00 | Fail | Re-connected all equipment, monitors are all ok
MSA-DFES | WA3084109 | Behind the in built office space - investigation for where leaks are coming from | Metropolitan VFRS | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-03-17 11:41:00 | Fail | Cleared leaves from box gutter and modifed outlet. Sealed with silicone
MSA-DFES | WA3084112 | PPC room internal and external wall - Please check the back wall in relation to stop flooding | Metropolitan VFRS | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-04-09 16:00:00 | Fail | Strip drainage system is now unblocked, bottom of shed wall sheeting has been replaced and all is now in reasonable condition. See before and after photos
MSA-DFES | WA3084156 | Boom gate is not closing and it is producing a high pitched noise from the control box outside | FESA RHQ - Forrestfield | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-06-24 15:30:00 | Fail | Technician attended the site of WA Emergency Services Academy boom gate on 03/03/2020. Following full test and inspection of gate components identified was electrical damage possibly from lightning. Needs new main board and swipe card board.24/06/2020. Technician removed faulty boom gate and installed brand new unit set up boom gate. Ok, however access system causing issue so technician left an "out of service" tag on the boom gate for access to be repaired. Full test and inspection of gate components completed prior to leaving site.
MSA-DFES | WA3084164 | Small colour bond fence southern end of FF carpark, post has rusted at the bottom | VFRS Mandurah | GMP-BR | Building | Steel Work (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-03-04 12:00:00 | Pass | Replaced rusted post and panel with new
MSA-DTAG | WA3083362 | Camera & duress system is down due to lighting | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 28 Feb 2020 | 2020-02-28 12:25:49 | 2020-03-06 14:00:00 | Fail | Replaced battery banks to suit UPS previously replaced. On reboot 1 x Display Port to HDMI failed.Replaced lead. Tested UPS & commissioned
MSA-DTAG | WA3083662 | Access panel to be cut in to custody strip search area. Location has been marked out | Joondalup Courthouse | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-03-21 10:00:00 | Fail | CEILING REMOVED & REPLACED TO ALLOW FOR AIR CON UNIT REPAIRS
MSA-DTWD | WA3083449 | F Block, F3- store room box gutter leaking | Murdoch Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-04-02 13:45:00 | Fail | Removed rusted box gutter and water damaged supporting ply. Replaced with new
MSA-DTWD | WA3083851 | E Block, E29- Denlab split system is not working | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-04-02 11:30:00 | Fail | Awaiting electrician to replace isolator and check wiringRetuned to site. Investigated and found inverter PCB and condenser fan motor have failed, also isolator needs replacing. Ordered and picked up parts. Return to site. Replaced PCB, fan motor and wall isolator. Removed lockout. Started unit and checked operation. All ok
MSA-DTWD | WA3083861 | J Block, Room J4- 079 alarm fault | Bentley Campus | GMP-BR | Security | Monitoring (SE) | CONNECT SECURITY SYSTEMS | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-04-03 10:00:00 | Fail | Replaced battery
MSA-DTWD | WA3083929 | C block, level 1, room C112 - Water Leaks from corner of room | East Perth Campus | GMP-BR | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Feb 2020 | 2020-03-09 17:00:00 | 2020-05-15 10:09:00 | Fail | located leak and rectified
MSA-DTWD | WA3083979 | Campus carpark lights are tripping out | Rockingham Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-05-11 16:06:00 | Fail | Attended site and signed in. Located main switchboards and override the carpark lighting. Found 2 circuits not working. W2 and R6. Isolated and went investigating for fault. Many poles blocked access by over grown trees, and bushes grown around them. Dug bases of poles to access the connections. Tested and eliminated fault pole to pole. Found 2 faults exist. 1 is main feed which requires more time to investigate the pathway lights could be at fault. And 1 feed into carpark lighting junction box. Isolated faulty cables and tagged. Can not energise circuit as fault still exists. Need to braf a estimate to continue investigation. Left isolated. Drew plan of what’s been tested. Notified staff of findings and what’s to go forward. Job complete
MSA-DTWD | WA3084041 | Damaged/leaking hot water tap in staffroom | Armadale Campus - 40 Commerce Ave | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-03-18 14:00:00 | Fail | Replaced urn tap
MSA-DTWD | WA3084046 | level 1, left 3 - Basement button not working properly - intermit | Perth Campus B2 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-02-28 16:00:00 | Pass | Lift running when arrived, error FC Timed out errors due to power outages , customer ask so requested to replaced in car Basementbutton to green as other side, carried out a reset and tested operation of lift.
MSA-DTWD | WA3084091 | A Block - Alarm panel keeps beeping | Balga Campus | GMP-BR | Security | Monitoring (SE) | Casa Security Pty Ltd | 0 | CLOSE | 28 Feb 2020 | 2020-02-28 18:49:56 | 2020-02-28 16:15:00 | Pass | Cleared faults
MSA-DTWD | WA3084158 | L Block Lift not working again. | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 28 Feb 2020 | 2020-03-05 17:00:00 | 2020-03-02 12:30:00 | Pass | Not chargeable
MSA-MRWA | WA3083603 | Room 710 - Flickering light please replace. | Don Aitken Centre MRWA Head Office-Main Building-Seventh Floor | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 28 Feb 2020 | 2020-03-03 17:00:00 | 2020-03-03 08:54:00 | Pass | Removed globe noticed one of the tombstones is loose and the starter has swollen and corroded will send to awb to remediate. Not urgent
MSA-MRWA | WA3084137 | Level 2, Real Time Traffic Operations - Operable wall has failed, please attend and open. | Road Network Operation Centre (RNOC) | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 28 Feb 2020 | 2020-03-03 17:00:00 | 2020-02-28 19:16:00 | Pass | Inspected door and found roll pin had come out of locking drive bar. Removed front plate and refitted roll pin. Will require a return To site with 2 techs to refit tie bars have left fixings taped to door pic attached have left fixings on site pic attachedBrendan has cancelled the return visit and notified us that it is not required therefore this job is completed
MSA-DCA | WA3084337 | Plant room - VSD on HAU 10 needs to be reset as board room is without AC | Maritime Museum Victoria Quay | GMP-BR | Air Conditioning | Ducted Split System (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 29 Feb 2020 | 2020-02-29 18:43:13 | 2020-02-29 19:00:00 | Fail | Accessed building and met with client. Checked AHU.Standby mode.Checked BMS.Found no enable to run.Schedule created for new slot for tonight's extra function.System started a running in auto mode.Advised client.
MSA-DCS | WA3084253 | Unit1 cell 2.11 call isn't working | Roebourne Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Feb 2020 | 2020-03-01 09:33:30 | 2020-03-05 13:59:00 | Fail | Sourced spare CI-CC from Seme stock Travelled to site and replaced, tested cell call and recordings, confirmed operational
MSA-DCS | WA3084275 | UNIT 1- CELL B4- Lock is faulty. | Hakea Prison-Unit 1 | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 29 Feb 2020 | 2020-02-29 13:51:53 | 2020-02-29 12:00:00 | Pass | Job completed - Attend site after hours, service and repair lock.
MSA-DCS | WA3084320 | Camera PT 5 not working, | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Feb 2020 | 2020-03-01 13:14:13 | 2020-03-10 11:00:00 | Fail | 10/03/2020 confirmed no picture on incoming equipment in Gatehouse. Attended EC10 on perimeter. Powered up camera, and confirmed start-up sequence. Confirmed good camera image and PTZ functionality from cabinet. Restored modem connection and confirmed they had video and PTZ functionality. Reset Camera Preset locations.
MSA-DCS | WA3088630 | Hakea-Melaleuca Prison - Unit 11 - Cell D3 - Floor lining is lifting up and having problems | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Feb 2020 | 2020-03-05 17:00:00 | 2020-12-01 10:30:00 | Fail | DAMAGED SECTION OF FLOORING REMOVED & REPLACED WITH NEW VINYL.
MSA-DTWD | WA3084318 | BALGACAMPUS-BLOCKC,D and E, Security alarms, Damage to the cable | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | Casa Security Pty Ltd | 0 | CLOSE | 29 Feb 2020 | 2020-02-29 17:24:46 | 2020-03-12 13:06:00 | Fail | Repaired damaged cable
MSA-DCS | WA3086285 | UNIT 3- All PIR sensors are constanly activating. | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Mar 2020 | 2020-03-02 08:23:57 | 2020-03-05 21:00:00 | Fail | Checked the Unit PIR map on EBI. Most of the PIR icons were flashing green as if they had been in alarm but the alarm had not been acknowledged. There were no alarms that had not been acknowledged. PIRs for U2 cell 8 and U3 cell 13 would activate as soon as the areas were armed. Walked around all units with a copy of the EBI map to check the physical condition of the PIRs. Could not find any that had been damaged. Map is inaccurate compared to what is located out in the field. Replaced faulty U3 cell 13 PIR. Tested ok. Returned later in the evening to observe one of the nightly walk tests. All tested ok except for U2 cell 8. Shutdown, restarted and resynchronised the servers. The fault with the PIR graphic has been rectified. U2 PIR to be repaired under another work order number. Parts used:Interlogix EV116AM PIR x 4 (1 used, 3 left on site as spare)Consumables
MSA-DCS | WA3086288 | Unit 2-Cell 9 PIR activating. | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Mar 2020 | 2020-03-02 08:35:38 | 2020-05-01 07:56:00 | Fail | 30/4 Performed cable tests and found issue at PIR / conduit possibly caused by verminRe terminatedTested ok
MSA-DCS | WA3086431 | the camera number 4 not working on top of the building | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Mar 2020 | 2020-03-02 18:18:43 | 2020-04-23 09:52:00 | Fail | Focus is fine but camera over rotates on PTZ command. Tovresolve this camera settings were reprogrammed to a lower PTZ speed so it will not over rotate on the slow network
MSA-DCS | WA3086433 | ISU kitchen door lock is broken | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 2 | CLOSE | 01 Mar 2020 | 2020-03-05 17:00:00 | 2020-03-09 11:00:00 | Fail | supplied and install replacement lock, handles and cylinder
MSA-DFES | WA3086318 | Duncraig FS-Main Building- Dorm 1- The aircon is leaking water onto the carpet | CFRS Duncraig-Main Building | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 01 Mar 2020 | 2020-03-03 17:00:00 | 2020-03-18 14:00:00 | Fail | Removed pipe duct, Removed old flexible drain, Change drain entry from right to left hand side Ran new drain in new 20mm rigid pic, Replaced pipe cover, Patched hole in the gyprock, Tested drainCleaned up area
MSA-DFES | WA3086330 | Sub indicator board - system 2 alarm hasn't been reset. | DFES Regional Office - Belmont | GMP-BR | Building | Materials (BU) | Critical Fire Protection & Training | 1 | CLOSE | 01 Mar 2020 | 2020-03-03 17:00:00 | 2020-03-03 09:50:00 | Pass | As per work logAttended site from call out receivedNo access on attendingMade several phone call and still no accessCharge for call outNo signature slip available as no access was available.
MSA-DCA | WA3087905 | Retrospecitive work order do not attend-chiller water system comming as fault on system | Collection and Research Centre Welshpool-Bulk Wet Store-Ground Floor-Plant Room | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 02 Mar 2020 | 2020-03-03 17:00:00 | 2020-03-03 16:30:00 | Pass | Attended site Monday 2/3/20 1200pm for an after-hours call out.Temperature through out building of HBC to be warm. Applied tests and checks to find CH2 in fault. Reset chiller and monitored operation. Investigation found fault present with BMS system not allowing correct control over Bypass valve. Reset global of BMS controls system and monitored operation. Left site 2/3/20 1400pm.
MSA-DCS | WA3087455 | the reception door doesn't lock properly | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 1 | CLOSE | 02 Mar 2020 | 2020-03-03 20:38:33 | 2020-03-03 15:00:00 | Pass | Job completed - Attend site, repair lock.
MSA-DFES | WA3087379 | Welshpool FS- engine roller door fallen off | CFRS Welshpool | GMP-BR | Carpentry | Materials (CA) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 02 Mar 2020 | 2020-03-03 17:00:00 | 2020-03-02 17:45:00 | Pass | Technician attended the site of 380 Welshpool Rd, Welshpool, WA to the Engine bay door 2 exit A40352193G on 02/03/2020. Following a full test and inspection of door components found fault to be panel window on front exit door blown off by wind. Technician has put window back on as temporary measure. Panel will need replacing to prevent reoccurrence. Also rear door to bay 3 is missing 2 windows and panel is damaged.2 quotes were submitted.
MSA-DCA | WA3087975 | Basement, Sewer pump in continuous alarm | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 1 | GMP-BR | Plumbing & Drainage | Sewage Treatment Plant (PD) | Ballantyne Plumbing Gas & Electrical | 2 | CLOSE | 03 Mar 2020 | 2020-03-06 17:00:00 | 2020-03-03 15:51:00 | Pass | Cleaned sensor and hosed out pit and tested both pumps on auto and manual and all good
MSA-DCA | WA3088905 | Fault on AC in Admin office – New Museum Area | Collection and Research Centre Welshpool-Administration and Library Building-Level One-Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 03 Mar 2020 | 2020-03-06 17:00:00 | 2020-03-09 10:00:00 | Fail | Attended site. Admin AC system upstairs adjacent staircase not operating correctly. Applied tests and checks to find system short of refrigerant. Raised BRA for applicable repairs. Carried out repairs to AC system as per approved BRA. Pressure tested system to locate refrigerant leak on condenser coil. Braised and repaired leak, re-pressure tested system to 3500kpa. Evacuated and charged system with 10.5kg R410a. Carried our testsand checks. System operating correctly.
MSA-DCS | WA3087831 | Jeelia,C wing - numerous cells in C Wing have lost tv reception | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Sapio Pty Ltd | 2 | CLOSE | 03 Mar 2020 | 2020-03-06 17:00:00 | 2020-03-13 11:00:00 | Fail | Job completd - Replaced wall plates and aerial leads in all cells & common area. All TVs now display clear image on all channels.
MSA-DCS | WA3087865 | Unit 14 - A Wing-hole in the ceiling looks like it could be water damage. | Casuarina Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Mar 2020 | 2020-03-10 17:00:00 | 2020-05-28 10:30:00 | Fail | NO VISIBLE DAMAGE FOUND UPON INSPECTION
MSA-DCS | WA3087915 | Unit 1 - Court Yard-broken welds on B&D yard fence | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 2 | CLOSE | 03 Mar 2020 | 2020-03-06 17:00:00 | 2020-05-12 14:30:00 | Fail | 04/03/20Inspected fence.Requires 2 x securifor fence panels 2100 high.BRAF required.05/05/20Welding on mesh panels. To complete following Tuesday due to inclement weather.12/05/20Complete
MSA-DCS | WA3087940 | Unit 2, C wing, shower - middle shower recess - hot water tap spinning around and not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-04 12:00:00 | Pass | Replace missing split Pins in cold water spindle in plumbing duct cleaners store
MSA-DCS | WA3087955 | pre-release unit - Security system drops offline, serval times a day. a couple minutes each time. | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Mar 2020 | 2020-03-03 17:24:40 | 2020-03-12 10:00:00 | Fail | Run activity report and confirm network timeouts are no longer an issue. Gallagher 600 + 8H module delivered to site and stored as critical spare if this issue occurs again.
MSA-DCS | WA3087959 | pre-release unit - JACQUES Intercom fault alarms | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Mar 2020 | 2020-03-03 17:26:37 | 2020-03-24 16:23:00 | Fail | Server Upgraded and relocated to MED comms room. New data cabling installed between server rack and communications rack. Program, test and commission and verify HLI all ok.
MSA-DCS | WA3087970 | Unit 4 - A & C-A/C wing door bouncing off the latch when shutting from when the door is open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 03 Mar 2020 | 2020-03-06 17:00:00 | 2020-03-20 14:00:00 | Fail | On site replace door closer mounting and body screws andreplace slide arm
MSA-DCS | WA3087981 | gardens cucumber shed wet wall panels require repairs falling out | Karnet Prison Farm | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-09 13:45:00 | Pass | wall is of evap air con filters - job for air con company
MSA-DCS | WA3088874 | Gardens green house RCD keeps tripping | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-16 12:00:00 | Fail | Investigate gardens greenhouse rcd. Tripping caused by faulty pump. Requires quote.Source replacement pump. Install new pump.
MSA-DCS | WA3089005 | Industries mechanics compressor faulty | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CLEVELAND COMPRESSED AIR SERVICES | 2 | CLOSE | 03 Mar 2020 | 2020-03-06 17:00:00 | 2020-05-22 12:39:00 | Fail | Installed new pump onto frame, removed fittings from faulty pump and installed onto new pump.
MSA-DCS | WA3089011 | industries compressor not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CLEVELAND COMPRESSED AIR SERVICES | 1 | CLOSE | 03 Mar 2020 | 2020-03-04 14:10:19 | 2020-03-04 11:15:00 | Pass | On inspection I checked the safety switches on the doors, they are working fine.After further investigation I came to the conclusion that the controller is the issue. Sometimes I could get it to start by pressing in theemergency stop, resetting the fault then holding down stop and start together. The compressor would start 70% of the time. I left thecompressor running
MSA-DCS | WA3089039 | Camera 226 not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Mar 2020 | 2020-03-10 17:00:00 | 2020-04-25 17:00:00 | Fail | Attended site and replaced camera 226 with new wisenet camera. All replaced focused and tested ok. Job complete . Seme stock used
MSA-DCS | WA3089070 | Carpentry - aircon not working in the office | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 03 Mar 2020 | 2020-03-04 14:54:25 | 2020-04-21 16:00:00 | Fail | Obsolete cassette unit replaced for new as per BRAF extension.
MSA-DCS | WA3089106 | D1 Internal - Perimeter alarm constantly beeping and also not working | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Mar 2020 | 2020-03-04 15:48:47 | 2020-03-08 11:00:00 | Fail | D1 Internal Repaired by project technician
MSA-DCS | WA3089116 | perimiter fence PE beam 5 is constant alarm | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Mar 2020 | 2020-03-04 00:06:46 | 2020-03-05 14:20:00 | Fail | Cyclone related, will be completed under WA2997854
MSA-DCS | WA3089138 | MDAS fault listed below | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Mar 2020 | 2020-03-04 16:26:44 | 2020-03-05 14:04:00 | Fail | Sourced emergency spare parts - transponder - tamper switch - enclosure and receiver Arrived onsite to find no faults present on system. Checked logs to find no faults, tested system and checked all TR.Officers advised cabinets may have been opened.All cabinets are locked
MSA-DCS | WA3089568 | Jeelia, A wing Laundry - dry not working (suspect broken belt) | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 3 | CLOSE | 03 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-20 10:00:00 | Fail | Attend site - machine needs to be taken to workshop for repairs. Supply & fit Drive Belt & Support RollersComplete work in workshop - return machine to site.
MSA-DFES | WA3088356 | receptlion area carpets wet following roof collaps-need blowers to dry carpets | DFES Regional Office - Belmont | GMP-BR | Flooring | Carpet (FL) | AWB Co. | 1 | CLOSE | 03 Mar 2020 | 2020-03-04 17:00:00 | 2020-03-04 08:30:00 | Pass | SUPPLY ONLY DEHUMIDIFIERS TO SITE
MSA-DFES | WA3089108 | Engine room door airkey for 2.4UT not working | CFRS Canning Vale | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 03 Mar 2020 | 2020-03-06 17:00:00 | 2020-03-12 09:00:00 | Fail | no charge to follow only battery issue and job closed on our end and battery replaced
MSA-DFES | WA3089111 | Behind Pump House and Letter Box- Retic Broken | FESA RHQ - Forrestfield | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 03 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-10 15:00:00 | Pass | Repairs to Reticulation SystemRemove Leaking Reticulation Solenoid ValvesReplace Valve Sockets, Re-seal & Re-fit Valves
MSA-DTAG | WA3087990 | Kitchen - No Hot water coming out of billi unit (Unit on right side of kitchen) | International House-Main Building-Level 14 | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 03 Mar 2020 | 2020-03-04 17:00:00 | 2020-03-12 13:50:00 | Fail | Must be removed from site to workshop Workshop repair completed and system reinstalled
MSA-DTAG | WA3089122 | Level 1, Presiden Buss’s chambers- Air con not working | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 03 Mar 2020 | 2020-03-04 17:00:00 | 2020-03-21 15:00:00 | Fail | Works completed.
MSA-DTWD | WA3087651 | level 3, AMEP Staff room - Blinds have no cords to open & close | Perth Campus B1 | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 03 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-09 12:00:00 | Pass | job completed- installed cords
MSA-DTWD | WA3087845 | Canteen - hot water service pilot light keeps tripping out | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Mar 2020 | 2020-03-06 17:00:00 | 2020-03-12 14:30:00 | Fail | repaired leaking pilot assembly
MSA-DTWD | WA3088951 | B block - lift is out of order | Bentley Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 0 | CLOSE | 03 Mar 2020 | 2020-03-03 17:17:12 | 2020-03-03 16:50:00 | Pass | job completed - DIRECT DRIVE UNIT - MICROPROCESSOR UNIT - COMPONENT RESET
MSA-DTWD | WA3089012 | E block, E101A + corridor behind - Water leaking through ceiling | Midland Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 03 Mar 2020 | 2020-03-10 17:00:00 | 2020-04-06 14:00:00 | Fail | Removed 2 sections of ducting penetrating through roof and patched and sealed holes -removed offsite. Job complete
MSA-MRWA | WA3087997 | L7 714 Flashing fluro, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 03 Mar 2020 | 2020-03-04 17:00:00 | 2020-03-03 10:43:00 | Pass | **completed job before task was raised in promap**
MSA-DCS | WA3089383 | unit 7, lobby water cooler, not cooling water | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 04 Mar 2020 | 2020-03-06 17:00:00 | 2020-04-01 11:21:00 | Fail | Technician attended to system and advised to replace unit - sending through BRAFReturned and replaced fountain with a zip economaster with maxi flow filter inside unit. Mounted the unit to the wall and checked under pressure and flushed systemONSITE LONGER THAN CHARGED. NEW MANUFACTURERS SERIAL NUMBER ZIP 2020030503020
MSA-DCS | WA3089602 | Welding training shed - roller door spring mechanism is faulty | Wooroloo Prison Farm | GMP-BR- HO | Building | Roller Shutters (BU) | UNIVERSAL DOORS | 1 | CLOSE | 04 Mar 2020 | 2020-03-05 08:19:55 | 2020-04-15 14:50:00 | Fail | ATTENDED SITE, SUPPLY & INSTALLED ONE (1) PAIR OF GUIDES, ONE (1) LOCK WITH LOCKING BARS & TWO (2) DOOR STOPS, CHECKED OPERATION, ALL OK.
MSA-DCS | WA3089653 | visits centre - roof leak above search room | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 04 Mar 2020 | 2020-03-05 08:45:25 | 2020-06-12 13:07:00 | Fail | located leak and rectified
MSA-DCS | WA3089723 | Unit 1, Cell D13- Personal lock has key stuck in lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 04 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-25 11:00:00 | Fail | replaced hinges, barrel & lock
MSA-DCS | WA3089874 | Admin, Transitional Manager - Door lock damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 04 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-09 08:30:00 | Pass | Attended site inspected transitional manager office. Require Head Office to approve modifications to doorhardware prior to proceeding. Advised by DOJ Locksmith 05/06/2020 that job will not be proceedi
MSA-DCS | WA3090106 | BR-concret products PA system not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Mar 2020 | 2020-03-09 17:00:00 | 2020-05-11 11:30:00 | Fail | Found faults with 2 speakers and damaged cabling running from the PA amp. Replaced 2 speakers and 30m of cable. Connected to amp, tested ok with microphone. Parts used:2 x Redback 10W horn speakers30m figure 8 cable (site stock)consumables
MSA-DCS | WA3090112 | laundry outside the entry grille roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 Mar 2020 | 2020-03-11 17:00:00 | 2020-05-08 10:28:00 | Fail | Leak located and rectified
MSA-DCS | WA3090118 | cabinet shop roof leaks | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-06 15:00:00 | Pass | located leak and rectified
MSA-DCS | WA3092245 | crisis care unit oven keeps switching out tripping | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 04 Mar 2020 | 2020-03-05 15:11:15 | 2020-03-19 14:00:00 | Fail | Found Faulty Power Switch, will require new one. Struggled to get contact with Prison but when did we were notified maintenance had replaced but was advised to drop off new switch to gate for spare.
MSA-DCS | WA3092271 | Control Room- PTZ 23 no signal | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Mar 2020 | 2020-03-09 17:00:00 | 2020-04-17 12:25:00 | Fail | Camera programmed and reinstalled after warranty repairs to unit. D2 housing also replaced.
MSA-DCS | WA3092295 | Unit 11, Cell A5- prisoner lock can not be unlocked from inside | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 04 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-05 14:45:00 | Pass | Replaced faulty lock.
MSA-DCS | WA3092343 | Fire panel error/unit panel area cannot be reset - showing indication of fire in unit | Karnet Prison Farm-Prisoner Accommodation Huts Unit 1 | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 04 Mar 2020 | 2020-03-05 00:08:25 | 2020-03-05 13:44:00 | Fail | Contacted site via phone, system isolated, on site staff said next day attendance ok
MSA-DTAG | WA3089864 | Lift 9 is ‘Out of Service’ | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 04 Mar 2020 | 2020-03-05 17:00:00 | 2020-03-04 12:15:00 | Pass | Landing door shoes scrapping level 4, rotated shoes not scrapping.
MSA-DTAG | WA3089885 | custody is experiencing faults with 4 cameras around the building- see notes below | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 04 Mar 2020 | 2020-03-05 17:00:00 | 2020-04-08 09:00:00 | Fail | Job completed - removed defected display adapters and installed new. Re-configured monitors and tested sound.
MSA-DTAG | WA3092283 | Custody Control room - 2 faulty hard drives associated with security system | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 04 Mar 2020 | 2020-03-11 17:00:00 | 2020-04-08 14:00:00 | Fail | Attended site. Custody Control Room 2 Hard Drives failed for the CCTV NVRs. Contractor. Raid disks started rebuilding monitored NVRs.
MSA-DTWD | WA3090023 | Wash Room- Leaking hose in washe pressure | Perth Campus B6 | GMP-BR | Equipment | Spray Equipment / Waterblasters (EQ) | Falcetta Plumbing and Gas | 3 | CLOSE | 04 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-24 17:00:00 | Fail | inspected and adjusted hoses, replaced pressure hose and hand piece
MSA-DTWD | WA3090030 | Wash Room- Vinyl floor is damaged | Perth Campus B6 | GMP-BR | Flooring | Vinyl (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 04 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-04 16:00:00 | Pass | Carried out repairs to damaged vinyl
MSA-DTWD | WA3090062 | E block. LSK Combi oven not keeping temperature | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 04 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-17 16:30:00 | Fail | 06/03/2020arrived on site, found the elements pulling 26a each, but the fan not running, found the bolt had come off the fan blade and the fuses had blown. I re fitted the bolt and washers, and replaced the fuses that had blown, and turned oven on, fan started up and found it to be very unbalanced and wobbling and vibrating, Will require a new fan blade at the minimum. Found the motor needs replacing too.17/03/2020Arrived to site and removed old fan and motor. New fan and motor have been installed. Test ran oven and unit is operating correctly.
MSA-DTWD | WA3090097 | H Block, HG01- multiple fluro lights out | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 04 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-09 15:01:00 | Pass | BRAF Declined
MSA-DTWD | WA3092230 | Room 1F22- Carpet lifting near first desk on right | Thornlie Campus | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 04 Mar 2020 | 2020-03-11 17:00:00 | 2020-04-20 09:00:00 | Fail | Due to COVID 19 site staff were unwilling to sign off documentation,. Copy of closing form to be forwarded to site for signature
MSA-DTWD | WA3092243 | Block 3, Room 3F1- Door requires re-attaching – bolts sheared | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 04 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-26 15:30:00 | Fail | Replaced door closer with new
MSA-DTWD | WA3092262 | block 7 Faulty RCD for Air Con (B6) wont re-set | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 04 Mar 2020 | 2020-03-09 17:00:00 | 2020-05-07 16:00:00 | Fail | Carried out replacement and installation of the Evap unit on Block 7 as per reported Braf.
MSA-DTWD | WA3092289 | Block 8, Plant Room- AC 3 Leaking core | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 04 Mar 2020 | 2020-03-11 17:00:00 | 2020-06-11 12:00:00 | Fail | Works completed as per brafThornlie TAFE 6kw - G8 - AC3Supplied and Installed 6kw High Wall Split System A/CInstalled mains power, refrigeration pipe work, drain and duct coverEvacuated Unit and CommissionedCleaned Site and Disposed of Rubbish
MSA-DCS | WA3092532 | 5x Corresponders won't reset. | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Mar 2020 | 2020-03-05 09:06:59 | 2020-03-05 07:30:00 | Pass | On arrival found multiple zones with comms fail, checked equipment in comms room- all ok.Ran test on all zones, re-set system, checked system in control room- all ok.Unable to test fence alarms as staff on strike
MSA-DCS | WA3093271 | Lenard A wing Shunt trip breaker will not reset | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-27 15:00:00 | Fail | Replaced shunt trip
MSA-DCS | WA3093678 | Unit 7, water leaking at front door from ceiling when raining | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 05 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-28 11:30:00 | Fail | located leak and repaired
MSA-DCS | WA3093805 | Uni 1, Entrance Grill - the electronic lock is faulty not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Mar 2020 | 2020-03-06 14:23:17 | 2020-05-06 12:00:00 | Fail | Rectified and fixed the electronic door due to faulty devices and power supply, job completed.
MSA-DTWD | WA3092699 | E block, room E1, vertical blinds need fixing | Murdoch Campus | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 05 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-31 13:10:00 | Fail | Supplied & Installed Vertical Blinds to Replace Damaged Blinds
MSA-DTWD | WA3092807 | A block, level 1, female toilets - leak Beneath sink around tap. | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 05 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-18 17:00:00 | Fail | Replaced basin mixer
MSA-DTWD | WA3093056 | B Block, Room B30 & 31- metal backing plate & sink top is damaged | Murdoch Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 2 | CLOSE | 05 Mar 2020 | 2020-03-10 17:00:00 | 2020-04-06 09:13:00 | Fail | Works attended and BRAF submitted, BRAF Declined so closed out costs to date. SK
MSA-DTWD | WA3093295 | Block 6, Bricklaying- Leaking skylights | Thornlie Campus | GMP-BR | Roofing | Rooflights and Skylights (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 05 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-09 15:00:00 | Pass
MSA-DTWD | WA3093306 | E block E26 corridor safety and repairs to storm damaged ceiling | Bentley Campus | GMP-BR-RC | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 05 Mar 2020 | 2020-03-06 17:00:00 | 2020-04-07 14:30:00 | Fail | Water damaged ceiling removed and replaced with new
MSA-DTWD | WA3093830 | F block emergency fan moved in a location as causing issues | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 05 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-06 13:56:00 | Pass | Attended site to quote works only as requested
MSA-DTWD | WA3093840 | block 7 noisy air con on roof of canteen-Engie on site | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 05 Mar 2020 | 2020-03-12 17:00:00 | 2020-05-08 14:30:00 | Fail | CARRIED OUT REPLACEMENT OF EVAP UNITS AS PER REPORTED FAULTS. AS PER BRAF
MSA-DTWD | WA3093845 | L Block workshop- repair leak in compressed air line | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 05 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-17 18:00:00 | Fail | Repaired Leak in comp air line
MSA-DTWD | WA3093881 | E Block, E25- Leaking split system air con | Bentley Campus | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 05 Mar 2020 | 2020-03-06 17:00:00 | 2020-03-31 13:45:00 | Fail | Found unit beyound economical repair, braf sent
MSA-MRWA | WA3093104 | Level 9, Hallway - West end exit light out please inspect and remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 05 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-09 13:30:00 | Pass | Attended site and signed in. Inspected exit sign, left site to pick up new exit sign, returned and replaced sign. Tested job complete.
MSA-DCA | WA3094343 | Whole building - Temperature is cold | Collection and Research Centre Welshpool | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 06 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-06 10:45:00 | Pass | Attended site 6-3-20 0800. Collections building cold. Applied tests and checks to find error present with main SA temp SP on BMS controls logic (displaying and trying to control to -9c). Notified Schneider controls as a technician was on-site a day prior carrying out routine Maintenance. Schneider attended site at a non cost and rectified code issue. System operating correctly and temperatures to have balanced through out CRC space. Left site 6-3-20 @ 1030.
MSA-DCA | WA3095159 | murray street side awning has come loose is a safety risk | King Street Arts Centre-Main Building-External Area | GMP-BR | Building | Materials (BU) | ICS Australia | 0 | CLOSE | 06 Mar 2020 | 2020-03-06 18:07:50 | 2020-03-06 16:17:00 | Pass | Missing bolt has been replaced and screwed
MSA-DCS | WA3094205 | Female visits toilet door - water damaged and requires replacing | Karnet Prison Farm | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 Mar 2020 | 2020-03-12 17:00:00 | 2020-06-10 09:20:00 | Fail | replaced doors and painted
MSA-DCS | WA3094223 | Medical Centre - various water damage spots to ceiling requires repairs | Karnet Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 Mar 2020 | 2020-03-12 17:00:00 | 2020-06-10 08:20:00 | Fail | sealed roof penetrations, repaired damaged ceiling and painted
MSA-DCS | WA3094323 | ODP, Front entrance - grill opening by itself when pushed on even when the button was set to lock | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-05-29 09:00:00 | Fail | Replaced two rocker switches, which had lost the restore function, with two push buttons. Tested operation of release buttons from both push button panels.
MSA-DCS | WA3094539 | Gatehouse - camera 46 & 47 not working, blank screens | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-04-17 16:00:00 | Fail | C46- image and PTZ functions tested ok. C47- work to be completed under work order WA3226541
MSA-DCS | WA3094897 | Carey house- hot water unit not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-10 14:30:00 | Pass | Supply and install new hot water unit for carey house.
MSA-DCS | WA3094962 | roadway within prison between rec and inner industries sallyport drain blocked in roadway | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-20 08:00:00 | Fail | High pressure jet clean, remove & dispose of waste from nominated pits & pipesas directed - Dispose of waste at DWER approved disposal site.
MSA-DCS | WA3094971 | unit 1 cell door A22 door is damaged | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-09-09 14:30:00 | Fail | Supplied and installed new metal clad door to cell.
MSA-DCS | WA3094976 | unit 1 A25, A24, A23,A20,A19 and A18 repair cell doors | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2021-02-12 13:53:00 | Fail | Attended site, could only complete one door as the unit forms part of a Project now.
MSA-DCS | WA3094980 | unit 1 cell door A7 middle hinge is damaged | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-06-19 15:30:00 | Fail | Attended site and assessed what repairs where required.Installed temporary hinges and sourced specialised prison hinges.Re attended site and carried out replaced damaged hinges.
MSA-DCS | WA3095192 | SHU(9)- East wing grill motor loose & limit switched out of sync, grill is getting stuck | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 06 Mar 2020 | 2020-03-07 14:45:06 | 2020-03-16 11:30:00 | Fail | Job completed - Inspect SHU unit East wing grill. Found motor side mounts broken and two stripped. Refit and tighten as best as possible. Will need to return. Will need new limits (close faulty). Still operational but instructed limited use. Replace limit switches to SHU unit East wing grill. Test, all okay. Refit motor. Re-thread motor side mounts. Test manually, all okay. Test in auto operation, all okay.
MSA-DCS | WA3095252 | Zone 15 Camera #2 no video input | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Mar 2020 | 2020-03-06 21:07:29 | 2020-03-27 15:15:00 | Fail | Attended site and recabled analog camera with cat5 cable and replaced camera with new Indigo BX620 IP camera. All cabled,installed,programmed and tested ok. Job complete
MSA-DFES | WA3094816 | Back Yard- hole in bitumen. | CFRS Armadale | GMP-BR | Paving & Roadworks | Asphalt (PR) | Pave Mix | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-04-28 10:30:00 | Fail | Works completed as per Breakdown Authorisation Repair
MSA-DTAG | WA3094328 | Level 13&15 Secretary button to operate sliding door not working | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-04-23 10:00:00 | Fail | Replaced exit button on Reception Door Level 13 & 15.Tested operation, ok.
MSA-DTAG | WA3094832 | Ground, Cell 3- Lock on door not locking properly | Armadale Courthouse | GMP-BR-HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 06 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-06 14:00:00 | Pass | Serviced lock on cell
MSA-DTAG | WA3095122 | L1 Youth Justice- Manager Office door won’t unlock, key turns and it clicks & tongue won’t release | Perth Children's Court | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 06 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-09 11:00:00 | Pass | No completion notes
MSA-DTWD | WA3094389 | E block, E75 Kitchen - fridge making loud noise | Bentley Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 06 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-06 14:08:00 | Pass | FOUND THE CONDENSER FAN MOTOR FAULTY, REPLACED WITH NEW. ALL OK
MSA-DTWD | WA3094606 | B Block - Lift has stopped working | Bentley Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 0 | CLOSE | 06 Mar 2020 | 2020-03-06 13:24:09 | 2020-03-06 15:03:00 | Fail | JOB COMPLETED - CONTROLLER - MICROPROCESSOR UNIT - COMPONENT RESET
MSA-DTWD | WA3095206 | C Block - BMS electricity meters are not accurately reflecting readings physical meters. | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | Schneider-DO NOT USE-refer ZSCH03_BMA | 2 | CLOSE | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-24 17:30:00 | Fail | Re calibrated meters so all match actual meters
MSA-DTWD | WA3095251 | Level 2, Room A206- lights not working | Perth Campus B5 | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 06 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-23 11:30:00 | Fail | Complete
MSA-MRWA | WA3094994 | Level 7, room 726 - Light flickering please replace | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 06 Mar 2020 | 2020-03-09 17:00:00 | 2020-03-06 14:44:00 | Pass | Replaced tube with new. Back in working order
MSA-MRWA | WA3094999 | Front Fence - Resecure shade-cloth along border fence | Materials Engineering Branch | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 2 | COMP | 06 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-09 14:05:00 | Pass | Refixed mesh to the bottom of the fence
MSA-MRWA | WA3095033 | Admin- Failed fluro lights, approx 12 | Jandakot Depot | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | COMP | 06 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-11 14:45:00 | Pass | Replaced faulty tubes
MSA-DCS | WA3095327 | Unit 12 -CD wing cell N-10 -Fire alarm is beeping | Melaleuca Prison | SPA-BR | Building | Materials (BU) | Automatic Fire Protection (ARA) | 2 | CLOSE | 07 Mar 2020 | 2020-03-11 17:00:00 | 2020-05-01 09:20:00 | Fail | Attended site for fault on unit 11 C/D wing vesda. Found fault on 1/2 urgent airflow all pipes reading 0% and displaying fault on pipes 1-4 flow sensor fail. Rebooted Vesda unit and performed manual scan of pipes but could not get any airflow to vesda unit. Recommend replacing Vesda as unit no longer reading any airflow in C/D 1/2.Returned to replace vesda unit. Programmed new vesda and tested, all operational. Multiple prison incidents and an extra guard as 2 required on the wing. Tested ok no faults on panel when left site.
MSA-DCS | WA3095537 | Wandoo Rehabilitation Facility- PTZ% camera not focusing | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 0 | CLOSE | 08 Mar 2020 | 2020-03-08 11:46:31 | 2020-03-08 09:30:00 | Pass | Job completed -Rebooted camera which then started to auto-focus
MSA-DCS | WA3095552 | Unit 1- Cell 211- The cell call system isn't working. | Roebourne Regional Prison | GMP-BR- HO | Building | Materials (BU) | Sapio Pty Ltd | 1 | CLOSE | 08 Mar 2020 | 2020-03-09 08:39:15 | 2020-03-09 09:00:00 | Fail | Assisted Office Martins Meyer through phone support.
MSA-DCS | WA3095565 | Zone 9, Outer perimeter, one of the cables maybe damaged, is not alarming properly. | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 2 | CLOSE | 08 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-25 11:30:00 | Fail | Zone 9 outer fence reported as constant alarm. No alarms on visit to site. Cable tested fine, reported that it goes off when wet indicatingpossible slice in cable. No visible damage. Will need to retest cable when activated in order to locate which section of fence (top or bottom) isdamaged or replace all cable on Zone 9.
MSA-DCS | WA3095810 | Jeelia, Cell C5- Aerial face plate damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 09 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-13 08:30:00 | Pass | job completed - Cell C5 Jeelia Wing has damage to inner of aerial plate. Plate has clamp on rear for termination.Unable to source replica plate as new plates require compression type screw fitting at rear.Work performed by Cian O'Halloran (13/03/2020):Reattended site. Jeelia Cell C5 aerial face plate damaged.Replaced wall plate and aerial lead.
MSA-DCS | WA3095829 | Unit 12, SOP, Cell A8- Personal Lock not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 09 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-30 11:00:00 | Fail | Attend site replace mortise lock, cam and strike plate.
MSA-DCS | WA3095854 | Visits centre - Aircon Evap not working | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 08:17:33 | 2020-03-09 14:00:00 | Pass | Faulty solenoid and sump dump please see work logs for attendance and details of works.
MSA-DCS | WA3095858 | Camera 174,63,62,52 & 53 are not functioning correctly | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 08:22:30 | 2020-03-12 10:30:00 | Fail | C53-used site spare TX fiber modem for fault finding. Found data cable issue. Replaced section of cable. Image and all PTZ functions tested ok back to the gatehouse. C53-found faults with both receiver and transmitter modems. Replaced both with modems from PFM stores. Image and PTZ functions tested ok. Parts used: Consumables
MSA-DCS | WA3095859 | Garage roller door is broken, will not stay up | East Perth | GMP-BR- HO | Building | Roller Shutters (BU) | UNIVERSAL DOORS | 0 | CLOSE | 09 Mar 2020 | 2020-03-09 12:24:07 | 2020-03-10 14:50:00 | Fail | Supply & installed 1x door spring
MSA-DCS | WA3095866 | Staff Support room- hole in ceiling | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-05-01 10:20:00 | Fail | WORKS COMPLETED ON WA3095867
MSA-DCS | WA3095867 | Staff Support room- roof leak | Hakea Prison | GMP-BR- HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 08:34:25 | 2020-04-17 10:20:00 | Fail | Roof leak found and rectified, ceilings x 2 repaired and painted.
MSA-DCS | WA3095912 | Boiler house - steam pipe leak | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Boilertronics | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-20 15:35:00 | Fail | Boiler Room - Repair Steam Leak
MSA-DCS | WA3095916 | Secure TV in cell HC2 intermitent signal, sound and picture flashing. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-20 09:30:00 | Fail | Checked HC2 TV, scan TV channel ok. Issue hasn't occurred for a week.Report if issue occurs
MSA-DCS | WA3095919 | entry into medical, door locka and barrel loose not excepting key | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 09:24:10 | 2020-03-26 12:40:00 | Fail | Door Barrels on Door in Medical - both worn and jammingTemporary Barrels fitted 9/3 New barrels to be fitted ( waiting on parts )New Barrels fitted 9/3
MSA-DCS | WA3095931 | Medical centre & lunch room - Vinyl lifting coming away from walls | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-04-06 13:00:00 | Fail | replaced vinyl
MSA-DCS | WA3095942 | Unit 7, D Wing oven fan is slow | Casuarina Prison | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-23 09:45:00 | Fail | Found oven lamp glass to be missing and fan cage had dropped out getting caught on fan. Order part and returned to fit new lamp glass.
MSA-DCS | WA3095996 | PE Beams keep activating in the arunter room | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 10:23:33 | 2020-04-20 12:02:00 | Fail | Job has been completed and PE beams are operational
MSA-DCS | WA3096028 | SHU (9) - Court Yard- Grille over drain is damaged | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-06-24 10:59:00 | Fail | SITE HAVE REQUESTED THIS JOB IS TO CLOSECLOSE OUT WORK ORDER AND INVOICE COSTS TO DATE.
MSA-DCS | WA3096149 | BR Unit 3 C9 cell call bad static cannot be heard | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 11:44:37 | 2020-03-09 14:30:00 | Pass | Audio ok in the cell, static can be heard in the control room. Removed and replaced intercom. Tested loud and clear in the control room and in the cell. Parts used:Austco cell intercom landscape styleConsumables
MSA-DCS | WA3096152 | BR Unit 3 C10 repairs to flooring vinyl | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-05-29 09:50:00 | Fail | Found that these repairs had been completed on a different job number.
MSA-DCS | WA3096276 | House 12, waste IO is broken | Boronia Pre-release | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-26 13:00:00 | Fail | Complete
MSA-DCS | WA3096300 | unit 3 cell 63 snd 65 not working | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 14:02:25 | 2020-03-10 12:20:00 | Pass | Replaced Cell Locks on Unit 3 Cells 63 & 65
MSA-DCS | WA3096404 | Unit 2, Cell B14 - Lino floor is lifting | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2021-01-13 16:45:00 | Fail | new vinyl flooring installed
MSA-DCS | WA3096511 | Multiple locks unsecure and loose from frame. Door closers not working. | Maddington (South East Metro) | GMP-BR- HO | Security | Access Control (SE) | Sapio Pty Ltd | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-10 12:00:00 | Pass | Replaced new power supply
MSA-DCS | WA3096554 | Unit 7 - No power in unit | Hakea Prison-Unit 9 64 Cell Prison Living | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 09 Mar 2020 | 2020-03-09 23:10:49 | 2020-03-23 14:00:00 | Fail | Reset power and updated legends
MSA-DFES | WA3095963 | SO Shower instantaneous elec HW extremely hot often trips circuit breaker at meter box | Kensington (old) | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-24 10:30:00 | Fail | CompleteAttended site, no one on site but it was left open for me to work on, reconnected power to new HWU tested all in working order New hot water uniy
MSA-DFES | WA3096020 | Lower Carpark (70)- reinstate the retic for the garden area | CFRS Perth | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-12 17:00:00 | Pass | Call Out & Labour no parts required
MSA-DTAG | WA3095893 | 1903 - Air Conditioner in CoA office is getting quite noisy | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-04-04 14:30:00 | Fail | Mark Kember Attend site. Investigate AC in court of appeal office. Found unit to have ticking noise. Use 8ft ladder to access indoor unit at high level. Found unit to ne vibrating. Check unit fan barrel and found to be clean. Run fan through various speeds and found to continue vibrating. Also noticed that fan motor bearings are noisy. Found fan barrel to be out of balance causing excess vibration. Recommend replacing fan barrel, end bearing and fan motor. Paul VeurinkAttended site. Signed in. Spoke with security. Wrote JSA. Brought tools and equipment and ladders inside to indoor unit. Found outdoor unit in custody courtyard, got security to open door for access to courtyard. Isolated and tagged unit. Went to indoor. Opened unit. Tested wiring. No power. Disconnected wiring and dismantled unit. Removed fan motor, bearing and fan barrel. Fitted new motor, bearing and barrel. Reconnected wiring and reassembled unit. Went to outdoor unit. Turned unit on.Went back to indoor unit. Tes
MSA-DTAG | WA3095896 | CCTV not working in upstairs security office. One computer also not powering up properly | Armadale Courthouse-Main Building-Level 1 | GMP-BR-HO | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-13 11:45:00 | Fail | /3/20 - Dylan Parslow, Joshua ParkFound HDMI leads unplugged, reconnected.Pc workstation faulty, doesn't boot up. Recommend replacement.BRAF submitted.13/3/20 - Dylan Parslow, Joshua ParkInstalled and tested replacement workstation for CCTV monitors.
MSA-DTAG | WA3096015 | Legal Aid Lawyer rooms- Air quality is poor | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-04-28 14:30:00 | Fail | Getting signatures slip from client
MSA-DTAG | WA3096402 | ground Fire system check with Australian HVAC -see notes | Rockingham Justice Complex | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-14 12:00:00 | Pass | Function test for ahu complete
MSA-DTWD | WA3096002 | G Block - Possible BMS issue AC8 & AC9 | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-11 10:24:00 | Pass | Returned to site collected keys and gained access to G block plant room. Checked and adjusted air flow louvers via control. Gained access to rooms for A/C 8 and 9 manually adjusted guid vains on both units and monitored system operation. Units are running to set points of A/C 8 24deg and A/C 9 26deg. Site FMs have been shown how to make adjustments to BMS. Units are working as per set point.
MSA-DTWD | WA3096018 | L1 D111 flashback arrestors in casting room faulty | Perth Campus B4 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 09 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-26 14:30:00 | Fail | replaced flashback arrestors
MSA-DTWD | WA3096040 | BLD 823 - Various 240 volt smoke dectors faulty | Muresk Institute | GMP-BR | Electrical | Materials (EL) | Damian Rak Electrical Pty Ltd | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-13 10:30:00 | Fail | Replaced smoke alarm batteries
MSA-DTWD | WA3096109 | G block ground G129 male toilets 2x blocked toilets | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-10 09:00:00 | Pass | Plunged blockages
MSA-DTWD | WA3096134 | Block 4- G floor, Plant Room - Air Con 8 not working | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-12 13:13:00 | Fail | ICON LOGIC COMPLETED NEW CONTROLLER
MSA-DTWD | WA3096143 | E Block, E11 Laundry- Split system Air Con not cooling | Bentley Campus | GMP-BR | Air Conditioning | Ducted Split System (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-10 14:30:00 | Pass | Attended site signed in and spoke with site FM. Gained access to Landry and investigated unit. U4 fault found active on system. Gained access to Condenser. Isolated and checks fuses and swith points on PCBs. Restored power and carried out further testing. Unit operation resumed as normal. Fault believe to have occurred due to powr surge. Confirmed cooling operation. All ok. 9deg air off coil.
MSA-DTWD | WA3096323 | E block LSK under bench fridge running hot | Bentley Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 09 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-30 11:00:00 | Fail | Returned to site to complete BRAF repair gained access to kitchen set work area up replaced the TXV, the valve strainer, units site glass and dryer. Leak seal applied to all fittings. Pressure tested once confirmed as holding placed on vac restored gas charge and tested system operation. Monitored equipment until set point achieved and confirmed correct cycling. Confirmed all parts of cabnet reassembled. Work area left tidy. Unit maintaining set point of 2deg. Cycling correctly.
MSA-DTWD | WA3096472 | B block ground external plant room, chiller will not start | Midland Campus | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 1 | CLOSE | 09 Mar 2020 | 2020-03-10 17:00:00 | 2020-03-11 11:00:00 | Fail | BRAF Declined
MSA-DCS | WA3096734 | Casuarina Prison - Electric fence screen in the control room is not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Mar 2020 | 2020-03-10 10:23:01 | 2020-03-16 11:26:00 | Fail | remove temporary network switch & install new 24 port POE network switch. test & confirm all ports operational. clear all alarms. attend control room & log workstation
MSA-DCS | WA3096873 | Control room, computer timings out by 57 minutes all cameras and recordings out | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 07:36:52 | 2020-04-18 16:38:00 | Fail | Checked time sync on all servers and workstations.Reprogrammed NTC time server software and adjusted all servers and workstations.Monitored and confirmed all server, workstations, cameras and NVRs sync to 10.1.0.1
MSA-DCS | WA3097111 | Unit 11, Cell A1- cell door lock is not working correctly | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 08:25:57 | 2020-03-10 14:45:00 | Pass | Modified strike to allow correct locking function
MSA-DCS | WA3097248 | Unit 2, Cell D8- Bottom of door frame has been damaged | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 09:10:57 | 2020-03-25 09:00:00 | Fail | door has been fixed by others?
MSA-DCS | WA3097387 | Sliding vehicle access gates require stopping point re-calibration | West Kimberley Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-17 09:45:00 | Pass | 17/03/20Stop incorrectly installed.Weld new stopping plates onto slide stops.
MSA-DCS | WA3097479 | Kitchen- All ovens require recallabrating due to power surge/outage | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 10:12:04 | 2020-03-11 10:50:00 | Fail | Calibration recently checked and are locked in ok. check & compare readings in controller and history all ok. check temp sensors & meat probes for calibration , ok.Spoke to chef about issues and believe ovens are functioning properly.
MSA-DCS | WA3097491 | Unit 1, Cell C8- Faulty Cell Call | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Mar 2020 | 2020-03-10 18:22:12 | 2020-04-23 09:00:00 | Fail | Job complete
MSA-DCS | WA3097618 | Vocational Skills, whole Unit-fluro lights in class room /lights in office to be replaced-see notes | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-19 16:00:00 | Fail | Checked damaged lights in voc skills. Picked up replacement lights, replaced in toilets and classrooms
MSA-DCS | WA3097625 | Level 3, whole floor - both lighting panels will not allow lighting to be switched on for 4 areas | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | LYNX INTEGRATED SYSTEMS | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 11:41:52 | 2020-03-10 15:30:00 | Pass | LYNXIS technician returned to site and commissioned 2 x touch screens.
MSA-DCS | WA3097787 | Oval/Smokers Huts/Front Units- Ant Infestation | Wandoo Rehabilitation Facility | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-16 12:50:00 | Pass | sent BRAF for approval for increased costJob completed with fipronil granules to all areas for ant infestation.
MSA-DCS | WA3097789 | Kitchen - small oven has error code E21 | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 13:16:20 | 2020-03-12 17:30:00 | Fail | Turned up on site to investigate E21 fault. Fault referred to a faulty temperature probe. Installed new probe which did not fix the error. Tried multiple new probes in all probe terminals and fault still active. Returned to workshop to get a new board returned to site. Installed new board and tested the combi oven and combi is now working correctly.
MSA-DCS | WA3097819 | Unit 4, K & L Block- (K)oven not working & (L)grill not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-04-20 09:30:00 | Fail | Replaced Faulty Oven
MSA-DCS | WA3097851 | Unit 5 - A & C concrete stair landing slab ,front of unit A/C side a tripp hazard | Casuarina Prison | GMP-BR- HO | Carpentry | Staircases, Balustrades and Handrails (CA) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-06-09 13:30:00 | Fail | new landing slab laid
MSA-DCS | WA3097871 | west admin superintendent office no TV reception | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 14:18:53 | 2020-03-11 11:00:00 | Pass | Checked signals from antenna, all ok.Reprogrammed TV to pick up channels. Channels picked up ok and image quality good.
MSA-DCS | WA3097949 | unit 3 cell call going straight to the main control room cannot be armed locally | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 15:38:53 | 2020-05-13 13:00:00 | Fail | Checked cell call system. Found issue with U3 changing from UNATTENDED to ATTENDED mode. Repaired and tested ok.
MSA-DCS | WA3097982 | Clean all 9 observation posts. Heavy rodent presence. | Hakea Prison | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-04-02 15:30:00 | Fail | To clean all cobwebs, dust and grime from the internal ceiling, windows, walls, floor, benches,staircase and underneath staircase to nine (9) Observation Towers
MSA-DCS | WA3097988 | case planning alarm will not arm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 16:59:25 | 2020-03-13 11:32:00 | Fail | Sourced parts, attended site, installed and programmed replacement network switch.Tested OKJob Complete
MSA-DFES | WA3097381 | grounds towers 2 & 3-repairs to towers -see additional notes of faults | FESA RHQ - Forrestfield | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 2 | CLOSE | 10 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-24 16:00:00 | Fail | Works completed as per approved BRA dated 12/03/2020
MSA-DFES | WA3097540 | engine room doors need to be checked as one is not working with chain | CFRS Maddington | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-11 08:45:00 | Pass | Technicians attended the site of Maddington Fire Station Engine Room Door W21775 (#4) on 11/03/2020. Following full test and inspection of door components identified fault was the manual override mechanism was disengaged and not working correctly.Removed manual override mechanism, cleaned and adjusted spring tension, installed new roll pin to mechanism, reinstated and test operation several times, all ok. Also carried out inspection to all other doors whilst on site, found frayed cable on front door #2.Technicians returned on site on 29/04/2020. Removed damaged cables on W21773 (#2) and replaced with new. Adjusted spring tension and carried out full inspection and test of operation ok. Full test and inspection of door components completed prior to leaving site.
MSA-DTAG | WA3097518 | Basement Cell 1 Water pressure low in water fountain | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-16 08:50:00 | Pass | DIAGNOSED & REPLACED FLOW RESTRICTOR ON FOUNTAIN
MSA-DTAG | WA3097732 | Lvl 10- Goods Lift door unable to open via swipe card from both sides | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-11 14:00:00 | Pass | Reattended site and replaced Mortice Lock with new, tested, all OK.
MSA-DTAG | WA3097977 | 1903 basement security control room issues with alarms as follows | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-11 12:30:00 | Pass | job completed- Replaced HDMI adapters
MSA-DTWD | WA3097119 | D Block, Cell D111 - Blinds need to be repaired | Leederville Campus | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-04-17 13:00:00 | Fail | Supplied & installed new blinds
MSA-DTWD | WA3097245 | C block room C205 air con FCU17 has gone into fault | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 0 | CLOSE | 10 Mar 2020 | 2020-03-10 13:09:28 | 2020-03-18 17:00:00 | Fail | Attended site, fpund fan motor not running , found air flow sensor not wprkimg correcty, submitted quote to replace both Fitted new fan with 12ft ladder to access, fitted new air flow switch and teatwd operation Running well
MSA-DTWD | WA3097624 | P block Refix pit cover in the path outside P001. | Balga Campus | GMP-BR | Building | Materials (BU) | M Construction (WA) | 2 | CLOSE | 10 Mar 2020 | 2020-03-13 17:00:00 | 2020-04-06 09:05:00 | Fail | Job complete
MSA-DTWD | WA3097633 | J block J002-Refix metal sheet to the wall west side | Balga Campus | GMP-BR | Building | External Walls (BU) | M Construction (WA) | 2 | CLOSE | 10 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-17 13:00:00 | Fail | Job complete
MSA-DTWD | WA3097790 | F Block, Room F47- Evap Air Con drive motor not working | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-11 09:15:00 | Pass | Accessed the roof to check the evaporator all working ok , found control had 3 speed switch and motors are 2 speed . Marked the wall switch to suit.
MSA-DTWD | WA3097805 | F Block, ladies toilet, behind wall cistern is not functioning correctly | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 10 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-20 19:00:00 | Fail | Replaced cistern
MSA-DTWD | WA3097866 | Creche - Room 10G66- light not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-05-18 14:00:00 | Fail | 10G66 Creche lighting - remove and replace with LED batten
MSA-DTWD | WA3097868 | Block 1, Exhaust fans in toilets not working | Thornlie Campus | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 17:00:00 | 2020-03-11 08:30:00 | Pass | Replaced broken belt for toilet exhaust fan
MSA-DTWD | WA3097894 | C block ground-disabled toilet not flushing properly | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Mar 2020 | 2020-03-11 17:00:00 | 2020-07-27 14:57:00 | Fail | Complete
MSA-MRWA | WA3097945 | ground external spay shed, Broken electrical conduit-see notes | Materials Engineering Branch | GMP-BR | Electrical | General Electrical (EL) | MR - Handyperson - PFM | 3 | COMP | 10 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-17 10:00:00 | Pass | Covered broken conduit
MSA-DCS | WA3098132 | Master control room - All controls at the gate house are not working | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Mar 2020 | 2020-03-11 10:20:06 | 2020-03-11 15:22:00 | Fail | Sourced parts, attended site, repaired tecom fault which was causing gate controls to malfunction.Tested OKJob CompleteParts (SEME Stock):Network SwitchConsumables
MSA-DCS | WA3098326 | Unit 1, Cell D1- Porcelain part of toilet seat broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-04-15 14:00:00 | Fail | Remove and replace broken toilet, alter pipework to suit, jackhammer wall to fit new toilet, clean up and dispose of rubbish.
MSA-DCS | WA3098498 | Boiler House whole Unit system pump 1 gland leaking | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-05-05 11:30:00 | Fail | Remove pump and deliver to repairer for repairs. Pick up pump, reinstall and commission.
MSA-DCS | WA3098510 | Unit 13, A2 - Broken toilet seat & taps have no pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-11 14:00:00 | Pass | Toilet seat was replaced by in house Maintenance Men. Remove blocked restrictor and install new quarter turn valve to adjust pressure
MSA-DCS | WA3098511 | Unit 14 cell A01 sink blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-11 15:00:00 | Pass | Remove Basin trap in plumbing duct and clean to clear blockage. Reinstall and test.
MSA-DCS | WA3098514 | Unit 14, Cell A3- Shower & sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-11 14:00:00 | Pass | Remove grate, plunge, Moflo, rinse, plunge,reinstall grate and test. Plunge basin.
MSA-DCS | WA3098575 | Unit 2 - C6 toilet not flushing properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-12 09:00:00 | Pass | Adjust push button assembly in plumbing duct.
MSA-DCS | WA3098665 | Unit 14, Cell D01- No hot water pressue | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-12 10:00:00 | Pass | Adjust water pressure from the plumbing duct to The Basin
MSA-DCS | WA3098713 | Level 3, whole floor - both lighting panels will not allow lighting-see notes | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-30 15:00:00 | Fail | Replaced failed lighting touch screens.
MSA-DCS | WA3098755 | CCU (11) - C6-leaking tap and shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-12 12:00:00 | Pass | Remove and replace 2 x quarter turn spindles in plumbing duct behind cell.High profile inmate and had to wait for him to be relocated so as we could commence work.
MSA-DCS | WA3098767 | MPU (8) - M16-aerial point damaged | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-30 12:30:00 | Fail | Job completed - Replaced TV Point in MPU M16. Tested signal, OK.
MSA-DCS | WA3098785 | Medical Records- Hot water unit overflow is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 11 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-16 14:41:00 | Pass | AM VISIT - TECH REPORTED UNIT WORKING COULD NOT GET IT TO FAULT - DESCALED AND CHECKED SOLENOID RAN TESTED - IT FAULTED AFTER HE LEFT - NEXT ATTENDANCE IN AFTERNOON TECH REPLACED INLET SOLENOID TESTED. - INTERMITTENT FAULT COULD NOT BE DETECTED ON FIRST VISIT
MSA-DCS | WA3098820 | Abbattoir changeroom water leak copper pipe | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-12 14:30:00 | Pass | Repair water leak on hot water line at abattoir
MSA-DCS | WA3099015 | Medical centre - aircon 5 & 3 frozen soild, have turned off | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 11 Mar 2020 | 2020-03-12 13:35:22 | 2020-04-08 15:30:00 | Fail | Compressor change complete
MSA-DFES | WA3098546 | Engie room door, Modified shaft broken, which has damaged the door and track wheels | CFRS Canning Vale | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 11 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-12 13:30:00 | Pass | Removed broken axle and replaced with new, installed and welded new sprocket and reinforced tomake more durable and safe, retensioned door and reset limits, door now in good workingcondition.
MSA-DFES | WA3098551 | Admin ground various lights to be replaced-see additional notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-25 10:45:00 | Fail | Complete
MSA-DTAG | WA3098558 | ground custody-All camera’s not been displayed in custody’s monitors-see notes | Midland Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 11 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-11 15:15:00 | Pass | 11/3/20 - Dylan Parslow, Joshua ParkInvestigated issues with CCTV.Custody PC faulty, requires replacement.Admin registry front camera faulty requires replacement.Issues caused by power outage.
MSA-DTAG | WA3174147 | Retrospective work order attended 11/3-CCTV in custody not working after power outage | Midland Courthouse | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Mar 2020 | 2020-03-17 17:00:00 | 2020-04-15 11:00:00 | Fail | Replaced and programmed replacement camera. Tested OK.
MSA-DTWD | WA3098312 | Level 2, Foyer behind Pink container - Large glass pane container | Perth Campus B5 | GMP-BR | Glazing | Glass wall (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 11 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-27 11:50:00 | Fail | ATTENDED SITE & PATCHED TO SECURE LARGE BROKEN PANEL & MEASURED FOR NEWWITH 2 SQM OF SAFETY FILM RETURNED LATER DATE TO REGLAZE10.38 CLEAR LAMINATED SAFETY GLASS1-2436 X 1193POLISHED EDGESBLACK SILICONE USED AND FROST STRIP APPLIED4 MEN AND ACRO PROPS, PLATFORM LADDERS & EXTENSION LADDER REQUIRED
MSA-DTWD | WA3098336 | BLD 826, Hallway - Faulty smoke alarms | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 11 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-11 13:30:00 | Pass | Replaced smoke alarm
MSA-DTWD | WA3098393 | T block, hair dressing & Massage area - air condition to be reprogrammed for 4 hours | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 11 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-12 11:57:00 | Pass | Rooms /FCUT38 /FCU-GF-08,T39 /FCU-GF-03,T40 /FCU-GF-09,T41 /FCU-GF-04,T42 /FCU-GF-10A & FCU-GF-10B,T48 /FCU-GF-05A & FCU-GF-05B ,T52 /FCU-GF-01A & FCU-GF-01B,T54 /FCU-GF-02A & FCU-GF-02BT46 /FCU-GF-06T50 /FCU-GF-07Modified programs to allow FCU units to run for 4 hours instead of 1 hours when operated from the Delta room controller located in the conditioned space within the programmed time. Scheduled Occ times as requestedSaved Databases to controller Flash drive
MSA-DTWD | WA3098528 | B block L4 male toilet leaking HW tap in hand basin | Bentley Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 11 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-12 08:30:00 | Pass | Serviced hot tap.
MSA-DTWD | WA3098591 | M block cutting room Exhaust fans in the tile cutting room are not working properly | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | Ronley Holdings Pty Ltd | 2 | CLOSE | 11 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-12 08:00:00 | Pass | No completion notes
MSA-DTWD | WA3098776 | D block D233 L2-replace damaged two keys G071 - 2.4 | Joondalup Kendrew Campus | GMP-BR | Security | Monitoring (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 11 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-16 10:40:00 | Pass | job completed - replaced 2x damaged keys
MSA-DTWD | WA3098869 | G block ground G129 (male toilet, 3rd cubicle)-Blocked toilet-see notes | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-13 09:00:00 | Pass | Complete
MSA-DCA | WA3100901 | Research room on 3rd floor – Door D3/39 between research room and staff corridor does not lock | State Library of WA | GMP-BR | Security | Access Control (SE) | Schneider-DO NOT USE-refer ZSCH03_BMA | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-12 16:00:00 | Pass | Removed an power supply board from the level 3 public cabinet and installed to cabinet in the Beaty Stack. Checked and tested power supply and battery charge voltage. Asked Ben to monitor the battery as the battery voltage was down to 6 v.
MSA-DCA | WA3100999 | Auditorium- Main AC system that serves Auditorium as faulty isolator switch | Subiaco Arts Centre-Main Building | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 12 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-12 16:00:00 | Pass | Identified faulty isolator switch on acg16 in auditorium.Raised job and called electrician to site.Inspected power supply and found 2 fuses blown.Replaced with site stock.Replaced failed isolator switch and tested operation of unit.Found unit operating correctly,Cleared site and left.
MSA-DCS | WA3100150 | Unit 3, B1 - blocked toilet, not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-13 08:00:00 | Pass | Pull apart button assembly and remove part of broken spring. Reinstall and test
MSA-DCS | WA3100154 | Unit 14, A wing, C03 - sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-13 15:30:00 | Pass | Remove trap to clear blockage, clean, reinstall and test.
MSA-DCS | WA3100187 | Unit 14, A wing, A01 - sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-13 09:00:00 | Pass | Plunge sink to clear blockage
MSA-DCS | WA3100218 | Unit 14, A wing, A16 - sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-12 13:00:00 | Pass | Remove Trap clean out blockage, reinstall and test
MSA-DCS | WA3100322 | kitchen, stick blender broken - can be picked up form outside stores | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 12 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-25 09:10:00 | Fail | Pickup up stick blender and delivery to repairers. Repaired and delivery back to site.
MSA-DCS | WA3100330 | Unit 4, D5 - Main cell lock is jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 08:03:46 | 2020-03-12 16:15:00 | Pass | serviced main cell lock and replace fixings.
MSA-DCS | WA3100443 | whole of prison generator needs to inspected | Wooroloo Prison Farm | GMP-BR- HO | Equipment Hire | Compressors, Generators (EH) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 0 | CLOSE | 12 Mar 2020 | 2020-03-12 13:13:04 | 2020-03-12 12:30:00 | Pass | Check over genset and complete safety documentation. Found fuel taps to both gensets turned off. Found high level relay damaged due to corrosion. Swap relay from Kll to K16 and test fuel transfer operationTidy work area and complete job paperwork
MSA-DCS | WA3100576 | Unit 3 - A6 floor drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-12 13:10:00 | Pass | Plunge floor waste to clear blockage. This job was actually completed 1 week ago but for some reason was not logged by the prison until now.
MSA-DCS | WA3100697 | Zone 6, Microphonics cable broken | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 10:56:59 | 2020-04-29 16:10:00 | Fail | 28/4 Re terminated coupler checked cable resistance tested ok
MSA-DCS | WA3100725 | Video link toilets basins blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-13 13:30:00 | Pass | Plunge overflow relief Gully outside to clear blockage. This blockage was caused by the workers on the broad site.
MSA-DCS | WA3100868 | Unit 14 - Lunch Room Hot water billy faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 12 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-13 10:01:00 | Pass | THIS IS A DUPLICATE WORK ORDER NEEDS TO BE CANCELLED OUT THE SAME JOB WAS SENT TO US ON WA 3102895 SO THIS WO IS NOT GOING TO BE USED!
MSA-DCS | WA3101148 | Unit 2, control - air con not working | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 13:30:36 | 2020-03-13 10:08:00 | Pass | COMPLETED
MSA-DCS | WA3101186 | deisel tank power board high and low relay faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 14:14:30 | 2020-04-03 12:30:00 | Fail | Checked relays , recommend relays be changed out along with contactor for pump as water has ingressed relay R 15. Will estimate and return . Also will reseal top of cabinet to ensure no moisture can get in to new relays . Test ran system ok at tis time.Picked up new relays and pump contactor, returned and fitted them . Repaired the hole in the cabinet to prevent future water ingress. Test ran system ok.
MSA-DCS | WA3101228 | TRANSPONDER TR1 7 –Unit 1 House 1 Grounds Perimeter | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 14:55:37 | 2020-03-12 16:00:00 | Pass | Transponder 17 Unit1 House 1 comms failure alarm. Alarm constantly coming up on MDAS. Contacted client and spoke to Control room and advised to check if alarm restores following day, as its intermittent. Following day contacted Alan and he checked system alarm restored and all is in working order.
MSA-DCS | WA3101229 | Alarms indicating zone 9 and zone 11 omnitrax are offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 14:57:16 | 2020-03-12 15:00:00 | Pass | Contacted site and spoke to Control room. Alarms for zone and 11 omnitrax offline have since restored, and cleared. Possible power failure onsite.
MSA-DCS | WA3101249 | L9 fire door exit Swipe reader not working - staff unable to exit the firedoor | Westralia Square | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-12 17:00:00 | Pass | On arrival found L9 south stairwell reader not responder to card swipes.Checked cabling, programming, etc- found door set to lockdown.Contacted staff for authorisation to set door for secure, tested all equipment at floor- all ok
MSA-DCS | WA3101366 | unit 1 B15 - raw sewage coming up the drain pipe | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 12 Mar 2020 | 2020-03-12 21:26:10 | 2020-03-25 14:33:00 | Fail | Unblocked drain using drain machine
MSA-DTAG | WA3100301 | Lift 1 is displaying "out of Service" | Central Law Courts | CJS-MW | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 12 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-12 09:45:00 | Pass | Belt and lock adjusted Lift running all floors
MSA-DTAG | WA3101236 | Basement, Custody interview room 1 -(Intercom) Phone in Interview room 1 is Faulty. | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 17:00:00 | 2020-06-08 13:30:00 | Fail | Installed new intercom pair in Custody Interview Room 1. Tested operation, ok.Job completed.
MSA-DTWD | WA3100079 | toilet area - bad sewage smell that is coming from the pipe work | Armadale Campus? 45 Commerce Ave | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 12 Mar 2020 | 2020-03-12 17:00:00 | 2020-03-13 11:05:00 | Fail | campus and owner of building to address in future
MSA-DTWD | WA3100490 | Pool ladies toilet blocked toilet | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 12 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-12 14:30:00 | Pass | Cleared blockage
MSA-DTWD | WA3100530 | BLD 832 L1 stairwell Down light blown | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 12 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-13 11:30:00 | Pass | Repaired down light
MSA-DTWD | WA3100641 | On road in front of main switchboard in front of cottage 823 - 826-burst water pipe | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 12 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-12 12:30:00 | Pass | Checked burst water pipe front of Cottage 823
MSA-DTWD | WA3100652 | B block metal fab, welding by overhead lights not working | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 12 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-16 11:00:00 | Pass | Attended site and signed in. Located B block fabrication. Spoke with lecturer in charge. Found over welding bay lights not working. And high bay fluros not working. Found tripped breaker for welding bay lights all working okay. The high bay lights are old fluros and many are not working. Advised to replace with 4 x led 250w hi bay lights and re locate 2 smaller hi bays into more suitable area. Need scissor light to access so will need to submit BRAF to continue. Notified staff. Job not complete
MSA-DTWD | WA3100974 | admin ground staff toilet-male staff toilet is blocked | Clarkson Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-13 08:00:00 | Pass | Attended site and cleared blockages to single wc pan. Checked and tested operation of all toilets in that area.
MSA-DTWD | WA3101151 | U Block U5 classrooms - rodents in ceiling space - baits required | Rockingham Campus | GMP-BR | Pest Control | General Pest (PC) | JODAN PEST CONTROL | 2 | CLOSE | 12 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-14 11:30:00 | Pass | Rodent control
MSA-DTWD | WA3101183 | 25Ab fire doors-Carpet strips extending under fire doors have to be moved back | Perth Campus B1 | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 12 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-27 12:30:00 | Fail | Installed Edge strips as requested by site
MSA-MRWA | WA3101211 | Admin Library Conference room Replace warm fluoro lights with daylight | Materials Engineering Branch | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | COMP | 12 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-17 10:30:00 | Pass | Replaced light
MSA-MRWA | WA3101218 | Bitumen Asphalt Lab 1st floor gym hall Replace non-functional fluoro light | Materials Engineering Branch | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 3 | COMP | 12 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-17 11:01:00 | Pass | Replaced lights
MSA-DCS | WA3102150 | Investigate WTMD ongoing fault | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Mar 2020 | 2020-03-19 17:00:00 | 2020-05-11 11:53:00 | Fail | repaired by L3 11/5/20 On arrival system was frequently alarming and showing 4 stars of background noise as a minimum. Replaced PSU and background noise reduced to a steady 2 stars. Monitored for 15 mins and system experienced a couple of alarms when nobody present. I believe this is due to the less than ideal location of the system as noted on previous site visits. As the location cannot be easily modified, I slightly reduced the system sensitivity and tested to supervisors satisfaction.
MSA-DCS | WA3102166 | Laundry- sheet machine has a leaking steam pipe | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | Boilertronics | 2 | CLOSE | 13 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-20 12:00:00 | Fail | Call out to attend to fault on steam leak in laundry.
MSA-DCS | WA3102432 | CCU (11) - equipment rack room fluro lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-18 10:00:00 | Pass | Repaired faulty lights in CCU equipment room
MSA-DCS | WA3102512 | Unit 2, top landing urinal blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 12:30:00 | Pass | Clear blocked drain using drain machine.
MSA-DCS | WA3102523 | Dairy pasturising room leaking tap fittings | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 13:30:00 | Pass | Repair leaking pipes and taps in pasteurising room.
MSA-DCS | WA3102528 | Dairy water pipe above hand basin leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-13 14:30:00 | Pass | Replace copper tube above basin in dairy
MSA-DCS | WA3102530 | Unit 4, Day Room- south auto boil not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-19 15:25:00 | Pass | attended diagnosed and replaced solenoid on unit orig callout did not specify type of unit and we have not serviced before --had to return with part for it
MSA-DCS | WA3102540 | unit 1 cells 3,6,8,9,10 and 22 broken double gpos | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-18 12:30:00 | Pass | Replace broken gpo’s and damaged plug tops in unit 1 cells
MSA-DCS | WA3102545 | Pole flood light near unit 4 not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-17 11:00:00 | Pass | Investigate and repair unit 4 pole lights
MSA-DCS | WA3102550 | WWTP contacter faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-18 15:00:00 | Pass | Investigate faulty wwtp contactors. Source replacements. Install new contactors.
MSA-DCS | WA3102551 | carey house connect new electric hot water system | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 15:00:00 | Pass | Investigate Carey House HWS. Job requires quote for asbestos removal
MSA-DCS | WA3102553 | Unit 3, Cell D8 - light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 13:30:00 | Pass | Investigate and repair unit 3 D8 wall light
MSA-DCS | WA3102556 | Official visits monitors office lock needs to be changed from SO key to AOSR as damaged | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 13 Mar 2020 | 2020-03-14 10:09:33 | 2020-03-13 16:30:00 | Pass | replaced cylinder on door as requested.
MSA-DCS | WA3102626 | Unit 2, Entry walk way - Perspex roof sheeting damaged | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-08-10 11:18:00 | Fail | REPLACE 38 SHEETS IN CREAM
MSA-DCS | WA3102810 | New east gym main lock on back entry door is hard to operate | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-04-21 15:15:00 | Fail | No completion notes
MSA-DCS | WA3102820 | Reception - clothing store side entry door to storeroom needs to be keyed to MKH | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-16 14:00:00 | Pass | Completed - Attend site, supply and install replacement cylinder.
MSA-DCS | WA3102827 | kitchen deep thermostat faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-04-17 12:00:00 | Fail | Kitchen deep fryer faulty. Check fryer & controls. Adjust thermostat & check cut out.
MSA-DCS | WA3102829 | Orchid pump faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 13 Mar 2020 | 2020-03-14 12:50:32 | 2020-03-17 10:30:00 | Fail | Orchid Pump faulty. Pump law pressure. Check pump & controls. Remove foot valve clean out valve & fit new screen. Dismantle pump motor, remove turtle shells from impellor. Return, assemble all, prime & test.
MSA-DCS | WA3102865 | Amenities -no.3 button on electronic lock is faulty/not registring at times | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-26 10:30:00 | Fail | Attend site dismantle lock, clean electronic lock, re assemble and replace battery pack.
MSA-DCS | WA3102884 | Unit 7, SCU, D Wing- Birko electric hotplate, temperature knob is not working | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-23 10:10:00 | Fail | Temp knob not working on hot plate, turned hot plate on testing each setting, all have tested to be ok.
MSA-DCS | WA3102895 | Unit 14, Tearoom- Hot water unit in staff room not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-19 12:10:00 | Fail | ZIP HYDROTAP A40191158I NOT HOT WATER CHECKED TESTED REPLACED LEVEL SENSOR TESTED
MSA-DCS | WA3102896 | Unit 13, Tearoom- Hot water unit in staff room not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-19 12:55:00 | Fail | Zip Hydrotap A403396895 filter blocked up replaced and plv blocked and required to be replaced
MSA-DCS | WA3102934 | plant room unable to download CCTV data | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-17 10:04:00 | Pass | Reported unable to download data from old system.Extracted data from servers, converted and provided to security.Parts Used (SEME Stock):Consumables
MSA-DCS | WA3102944 | Unit 14, Cell C13- Sink Blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 14:33:00 | Pass | Remove trap in plumbing duct, clear blockage, replaced trap and test
MSA-DCS | WA3102947 | Unit 4 - B Wing - Shower not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 14:33:00 | Pass | Replace missing split pin in shower spindle
MSA-DCS | WA3103054 | unit 3 cell 33 and 36 keys will not open locks | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-18 13:00:00 | Pass | Unit 3 Cell 36 - lock replaced and rebate kit fittedUnit 3 Cell 33 - Wooroloo maintenance had rectified
MSA-DFES | WA3102880 | Kitchen- Zip water unit not working | Advisory Services and Built Environment Branch Reg | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 13 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-27 11:09:00 | Fail | Old Zip unit replaced and new Billi MF SERIAL NUMBER R106406822LCH installed NEW CAPEX ASSET INSTALLED OLD UNIT UNREPAIRABLE
MSA-DFES | WA3102987 | Applied training ground-waterproof power point (3 phase)-see notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-20 11:30:00 | Pass | Locate faulty gpo. Replaced faulty gpo with new. Advised staff of work completed.
MSA-DFES | WA3103040 | Outside Community Garden-rebury and repair any damage to the retic | Armadale Regional Office | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-24 18:30:00 | Fail
MSA-DFES | WA3103042 | CCTV C7 Camera not working . | Armadale Regional Office | GMP-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-18 11:00:00 | Pass | Found camera had lost its programming from system, re program and focus, test, all ok. Also found keyboard faulty on main system, replace with customer supplied spare, test, all ok.
MSA-DTAG | WA3102190 | Lvl 5- Male public toilet is blocked – St Georges Terrace | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 13 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-13 15:00:00 | Pass | Complete
MSA-DTAG | WA3102195 | Lvl 5- Female public toilet is blocked – Hay Street | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 13 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-13 14:30:00 | Pass | Complete
MSA-DTAG | WA3102464 | 1987 L1 A/C on level 1 fails intermittently | Supreme Court | BUG-MW | Air Conditioning | Room Air Conditioners (AC) | Icon Logic Pty Ltd | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-13 12:30:00 | Pass | No completion notes
MSA-DTAG | WA3102857 | Public toilet - Unisex toilet is blocked – opposite Caffisimo | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 13 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-13 15:30:00 | Pass | Complete
MSA-DTWD | WA3102152 | North Block, Room N205- Toilet seat is damaged | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-17 13:00:00 | Pass | Complete
MSA-DTWD | WA3102364 | Main Entrance- Broken guide strips in main sliding door (DOOR UNSAFE) | Perth Campus B2 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 13 Mar 2020 | 2020-03-13 17:00:00 | 2020-03-13 11:19:00 | Pass | On inspection, found both nylon floor guides broken for unknown reason.Replaced both floor guides, tested and adjusted, all ok.
MSA-DTWD | WA3102397 | Records Room- Carpet is worn and exposing metal strips | West One Services | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 13 Mar 2020 | 2020-03-16 17:00:00 | 2020-04-20 13:56:00 | Fail | Works are complete. Waiting on site to sign off paperwork due to TAFEs COVID - No Sign policy - Completion slip emailed to site for signing
MSA-DTWD | WA3102458 | S Block, Main Air Con has fault | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-04-01 09:30:00 | Fail | Replaced faulty oil inlet solenoid coils for compressor
MSA-DTWD | WA3102511 | S Block, Science Classroom - Helium gas had a back flash | Murdoch Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | BOC LIMITED | 0 | CLOSE | 13 Mar 2020 | 2020-03-13 13:46:03 | 2020-03-13 13:00:00 | Pass | Found Manifold to have a spike when pressure is increasedRe-Kit manifold test all ok
MSA-DTWD | WA3102520 | E block poss mould or moisture in brick work needs investigation | Bentley Campus | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-27 12:20:00 | Fail | Thorough investigation of roof and structure to identify water ingress source. Some possible issues identified but nothing obvious. Suspect mould was sampled and tested and results were negative. Report supplied to client. Client did not want further action at this time and requested the job be closed off
MSA-DTWD | WA3102524 | Campus grounds several trip hazards across campus | Bentley Campus | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-31 15:15:00 | Fail | Ground down multiple sections of raised concrete path edges, removed and replaces several areas of badly damaged pathway
MSA-DTWD | WA3102667 | H block female toilet water running continuously | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-24 15:30:00 | Fail | replaced taps and repaired spout
MSA-DTWD | WA3102693 | A Block. Room AF3/4/10- Air Con Faulty | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-23 09:08:00 | Fail | As per BRAF.Returned to site. Again d access and checks Daikin BMS for active fault. No faults active. CU 1 has not go back into fault. Gained access to roof plant deck and rechecked CU1 master and slave. Systems working to set point. Work area has been left tidy. Equipment running as required.
MSA-DTWD | WA3102705 | Level 1, Front Lawn- Irrigation control system | Perth Campus B3 | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-16 14:00:00 | Pass | Irrigation technician ran through the irrigation system with the gardener, identified two faulty valves. Replace faulty valves and fix two minor leaks in the irrigation system.
MSA-DTWD | WA3102731 | A Block, Room A146- AHU 9 | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Building Automation & Electrical Services Pty Ltd | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 00:00:00 | Pass | No Charge
MSA-DTWD | WA3102734 | D Block BMS has lost communications | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Building Automation & Electrical Services Pty Ltd | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 00:00:00 | Pass | No Charge
MSA-DTWD | WA3102757 | C block L1 C109 Repair trip hazard entry | East Perth Campus | GMP-BR | Paving & Roadworks | Concreting (PR) | AWB Co. | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-20 12:50:00 | Pass | Repair trip hazards in paving to multiple locations
MSA-DTWD | WA3102841 | Block 3 - Male toilets Centre cubicle pan is leaking water | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-07-08 17:09:00 | Fail | Remove old pan and replace with replacement pan
MSA-DTWD | WA3102853 | E block- E63 freezer 1 running warm at -2.5 deg C | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 1 | CLOSE | 13 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-17 09:00:00 | Fail | Attended site , found freezer at -2 degrees, wemt to plamtroom and assessed, found that freezer was low on gas, proceeded with gas leak repair , found that the leak was on the suction accumulator, aquired a new one from airefrig, completed fitting new accumulator , re pressure tested and left for weekemd Reattended and found that pressure had dropped, found nipple leakimg on service valve , nipped up and tested, pressure ok, recharged with 5kg of r404A , test and let run down overnight Reattended and at temp, told chef it can be reloaded
MSA-DTWD | WA3102952 | L1 kitchen lights blown not working-male toilet and stairwell lights have blown | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 15:32:00 | Pass | Attend site. Signed in . Replaced faulty fluro out in ground floor male toilet and innstaircase next to reception. Replaced faulty floors to level 1 kitchen and blown fuse. Inspected exhaust fan in kitchen not working found motor and fan to be seized . Have taken measurements for replacement unit. Job not completed .will require braf for replacement .BRAF declined. Complete
MSA-DTWD | WA3102954 | A Block AG27 - Toilet door lock not working | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 13 Mar 2020 | 2020-03-20 17:00:00 | 2020-04-02 09:00:00 | Fail | A Block - AG27 - Toilet door lock not working.Lock repaired.
MSA-DTWD | WA3103001 | Q block L1 Q115-zip boiling not working | Joondalup McLarty Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-23 14:30:00 | Fail | Replaced front screen to zip. 23/3/20. Unfortunately couldn’t get on to pro maps yesterday so closing today.
MSA-DTWD | WA3103013 | E Block E29 classrooms has 3 flickering lights | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 13 Mar 2020 | 2020-03-18 17:00:00 | 2020-04-01 10:13:00 | Fail | Attend site. Signed in. Removed 11x old light fittings in E29 and installed LED panels .disposed of all of parts. . Tested all working properly. Cleaned site. Signed out .job completed
MSA-MRWA | WA3103021 | L1 first aid room Flickering fluro please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 13 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-17 13:20:00 | Fail | Replaced tube
MSA-MRWA | WA3103023 | ground G – Ross McKenzie’s desk, repair and return to service. | Heavy Vehicle Services | GMP-BR | Furniture | Office Furniture (FU) | MR - Handyperson - PFM | 1 | COMP | 13 Mar 2020 | 2020-03-16 17:00:00 | 2020-03-16 10:34:00 | Pass | Refitted desk bracket with a new screw
MSA-DCS | WA3109997 | All units - cell calls and PA system issue voice distorted not clear | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Mar 2020 | 2020-03-18 17:00:00 | 2020-04-19 18:22:00 | Fail | Ci-OH cable damaged.Replaced handset from site stock and tested PA systemLoud and clear
MSA-DCS | WA3110022 | shower drain blocked - MMU, cell M3 | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Mar 2020 | 2020-03-15 17:27:26 | 2020-03-15 09:00:00 | Pass | unblocked and issue resolved
MSA-MRWA | WA3109996 | security patrol alarm active | Jandakot Depot | GMP-BR | Security | Security Management System (SE) | MCS Security Group | 0 | CLOSE | 14 Mar 2020 | 2020-03-14 17:46:00 | 2020-04-23 13:43:00 | Fail | Report sent 23.04.20
MSA-DCA | WA3121589 | In chiller plant room 1 and 2 alarming | Collection and Research Centre Welshpool | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 15 Mar 2020 | 2020-03-15 11:51:13 | 2020-03-15 10:47:00 | Pass | completed.
MSA-DCA | WA3121601 | Art Gallery of WA - James St- unit 6 high humidity | Art Gallery of WA - James St | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 15 Mar 2020 | 2020-03-15 13:11:11 | 2020-03-15 12:48:00 | Pass | COMPLETED
MSA-DCS | WA3121585 | Perimeter Zone 5,6 and gate 6 didnot activate while doing test. | Boronia Pre-release | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Mar 2020 | 2020-03-15 11:19:22 | 2020-03-15 13:00:00 | Fail | Replaced main 6000 and 1 8input parts came form hakea critical stores all other devices came online and fence tested all ok
MSA-DCS | WA3121602 | Gatehouse - Inner Perimeter gate won't close | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Mar 2020 | 2020-03-15 13:09:07 | 2020-03-17 10:02:00 | Fail | Sourced parts, attended site, repaired cable fault between CER and sliding gate controller. Tested OKParts used (SEME Stock):ConsumablesJob Complete
MSA-DCS | WA3121642 | Casuarina Prison- cell call system in U 14 is faulty | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Mar 2020 | 2020-03-15 15:30:42 | 2020-03-15 16:15:00 | Fail | Both primary and secondary technicians are stuck with jobs when job come in. Called prison and advised we will attend the job ASAP. Attended site checked and U14 D1 cell call activated itself before. When technician arrived site, problem not happened anymore. Technician was told insect spray has been sprayed on cell call point by prisoner before. Suspected it causing the problem. Tested cell call with control officer and confirmed it is loud and clear. Can’t see any problem.
MSA-DCS | WA3121643 | Melaleuca-Unit 11- Boiler fault. | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Boilertronics | 0 | CLOSE | 15 Mar 2020 | 2020-03-15 15:30:28 | 2020-03-15 16:00:00 | Fail | Attended after hours call out to site to investigate fault on Hot Water Boiler.
MSA-DCS | WA3121676 | K unit monitor 3 is freezing | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Mar 2020 | 2020-03-15 17:37:35 | 2020-03-20 11:30:00 | Fail | Replaced faulty KVM and re-configure camera views for two monitors from DVM. Job completed.
MSA-DCS | WA3121694 | VISITS-CCTV in visits are not recording footage. | Wooroloo Prison Farm-Visitors Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Mar 2020 | 2020-03-16 15:22:40 | 2020-03-15 18:30:00 | Pass | Attended site checked and found NVR5 is offline and causing all Visit cameras are not recording. Reboot NVR5 and get it back online and tested all cameras recording again.
MSA-DCS | WA3121727 | Wandoo Rehabilitation Facility - Zones 7 and 9 - shows activated/alarmed but its not alarmed. | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Mar 2020 | 2020-03-16 20:06:58 | 2020-04-24 15:30:00 | Fail | Checked Intelliflex Zone 7 cable resistance, ok. Tested activation, ok. Zone 9 cable requires replacementJob closed as no further works required under this work order, fault was repaired under Work Order Number WA3170192.
MSA-DCS | WA3123246 | Melaleuca Prison - Internal Gate Magnet failed to secure the gate | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 16 Mar 2020 | 2020-03-16 10:30:30 | 2020-03-16 09:00:00 | Pass | test gate and locks- gate has dropped. Mag lock has not worked for sometime. Advised call centre AFD will be required.
MSA-DCS | WA3123287 | unit 11 all control room monitors are down | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Mar 2020 | 2020-03-16 10:59:18 | 2020-03-16 09:23:00 | Pass | Travelled to site, found software fir CCTV in unit 11 frozen, closed siftware and checked auto boot function operating correctly. Restarted workstation and restored system software and tested operating correctly.
MSA-DCS | WA3123433 | Hotham Laundry-Washing machine operating spasmodically | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 3 | CLOSE | 16 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-26 15:58:00 | Fail | Collect WM from stores and return to workshop. Test wm operation and determine motor faulty. Fit recon motor and test in work shop. OKReturn to stores. *** This WM Has significant corrosion and is Due for replacement ***
MSA-DCS | WA3123439 | Unit 3 - A Wing A4 sink blocked cannot clear | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-18 12:00:00 | Pass | Plunge Basin, use moflo in floor waste Gully to clear blockage.
MSA-DCS | WA3123448 | Unit 1 - A & C A13 Tap running and toilet keeps blocking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 14:35:00 | Pass | Clean sand out of Shell valve and Inlet valve on toilet
MSA-DCS | WA3123450 | Unit 4 - B & D B/D wing urn is leaking from the tap. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-16 15:00:00 | Pass | drain down unit, remove tap and clean out scale build up, reinstall tap and test
MSA-DCS | WA3123453 | Unit 14 - D12 personal lock is faulty, having trouble opening door | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 16 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-20 12:00:00 | Pass | Job completed - Attend site replace mortise lock, install rivnuts and adjust face plate to suit door.
MSA-DCS | WA3123467 | Unit 6 - A Wing (self care) has floor tiles lifting | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Mar 2020 | 2020-03-20 17:00:00 | 2020-06-22 10:15:00 | Fail | VINYL REPAIRS
MSA-DCS | WA3123474 | control MF fence zone 9B constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Mar 2020 | 2020-03-17 08:10:58 | 2020-03-16 13:30:00 | Pass | Rectified and fixed damage connector. Job completed
MSA-DCS | WA3123487 | Unit 14 cell C13 shower bllocked and requires attention. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-16 14:37:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test
MSA-DCS | WA3123492 | Unit 4 - A2 Prisoner personal lock not working correctly, door will not shut unless double locked | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-18 10:30:00 | Pass | Replaced door plate and lock
MSA-DCS | WA3123507 | INF (10) - Yard-garden shed in infirmary has hole in corrugated iron roof panels | Casuarina Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-06-19 13:02:00 | Fail | LIFTED ROOFING SHEET SO WATER WILL NOT GO BACK IN
MSA-DCS | WA3123510 | Unit 2 - Front Entrance outside light is broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 16 Mar 2020 | 2020-03-17 08:25:11 | 2020-04-06 10:00:00 | Fail | Investigated damaged bollards in unit 2. Isolated. Picked up replacement parts and installed
MSA-DCS | WA3123515 | Amenities - Tearoom Tap in Kitchen constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-16 14:38:00 | Pass | Remove and replace 1/4 turn spindle in kitchen
MSA-DCS | WA3123526 | Unit 14 - A & C drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-16 14:42:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test
MSA-DCS | WA3123574 | Unit 5 - D Wing Cell D4 lower bunk personal light faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-18 15:00:00 | Pass | Repaired faulty lights in unit 5 cell d4
MSA-DCS | WA3123583 | MDAS Monitor illustrates a yellow screen with the following fault | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-18 17:30:00 | Pass | Job complete
MSA-DCS | WA3123599 | Tamper (R) Cell Block 3 Male Medical Observation 3/1 (R 3.6.1) | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Mar 2020 | 2020-03-19 17:00:00 | 2020-04-07 16:01:00 | Fail | Located receiver and checked enclosure for damage, Replaced internal spring, tested tamper and confirmed correct operation and location Secured enclosure and alarm has cleared
MSA-DCS | WA3123645 | Unit 14 - C Wing cell B04 sink requires unblocking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-16 16:00:00 | Pass | Remove trap in plumbing duct, clear blockage, reinstall and test
MSA-DCS | WA3123698 | Unit 4 - B Wing cleaning cupboard light not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-20 14:00:00 | Pass | Checked damaged light in unit 4, picked up replacement light, installed and tested
MSA-DCS | WA3123776 | Gatehouse - transponder #2 is not responding | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Mar 2020 | 2020-03-16 13:39:55 | 2020-03-17 12:00:00 | Fail | Replaced receivers 19 and 20 and housing for both, tested PDAs at both locations, checked signals with control- all ok.
MSA-DCS | WA3123782 | Unit 1 - A & C A wing cells A13 sink tap leaking through wall. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-18 15:00:00 | Pass | Repair leak on basin waste within basin in the cell
MSA-DCS | WA3123798 | Unit1 ,cell A11 no water pressure in sink tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 09:00:00 | Pass | Remove Basin Palmer remove Shell valve, cleanout restrictor and reinstall.
MSA-DCS | WA3123814 | Unit 1 cell A 8 leaking toilet . | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 10:00:00 | Pass | Remove and replace 1x faulty Inlet valve in plumbing duct
MSA-DCS | WA3123957 | Unit 14 - B & D vinyl has peeled and bubbled- see notes | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-10-23 14:00:00 | Fail | DAMAGED FLOORING UPLIFTED & REPLACED
MSA-DCS | WA3123969 | Unit 4 cell D12 leaking sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-27 13:30:00 | Fail | Pick up parts. Remove and replace faulty time flow tap on basin
MSA-DCS | WA3124034 | unit 3 control room door lock jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 16 Mar 2020 | 2020-03-17 11:28:36 | 2020-03-16 15:15:00 | Pass | Serviced lock.
MSA-DCS | WA3124180 | Unit 13 - D Wing-Smell coming from drain in D02 Unit 13 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-20 09:00:00 | Pass | Moflo, rinse and plunge drain to clean pipes
MSA-DCS | WA3124196 | ECR - MDAS comms is failing to read | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Mar 2020 | 2020-03-16 16:39:23 | 2020-03-16 14:15:00 | Pass | On arrival found multiple transponder comms fails.Checked equipment in comms room- all ok.Checked programming, re-set system, cleared all alarms, tested PDA- all ok
MSA-DCS | WA3124255 | ISU unit camera 87, 88, 89 and 90 all frozen | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Mar 2020 | 2020-03-17 13:27:25 | 2020-03-19 15:30:00 | Fail | Investigated and repaired multiple CCTV faults in ISU and Admissions Areas.Tested OKJob Complete
MSA-DCS | WA3124263 | unit 11 C10 emergency cell call system is showing up tampered | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Mar 2020 | 2020-03-17 13:33:23 | 2020-03-16 15:30:00 | Pass | On arrival found unit in U11 C10 operating correctly, removed unit from wall for further investigation.Checked cables, connection, voltage- all ok.Tested to unit control and gatehouse- all ok.When arriving back at gatehouse, found device in tamper alarm.Staff from unit 11 called and advised that fault is due to prisoner holding call button constantly
MSA-DCS | WA3124303 | Master Control room - MDAS system fault | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Mar 2020 | 2020-03-16 18:04:22 | 2020-03-17 15:30:00 | Fail | Rectified and fixed the KVM fault MDAS systems. Job completed
MSA-DCS | WA3124313 | Admin canteen freezer keeps icing up | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-18 11:00:00 | Pass | Essential ref. attended , found freezer iced up due to unit not being level .DE iced unit level unit and left operational.
MSA-DFES | WA3124381 | Front Pump Engine room door arm has broken away from it's screw | Kensington (old) | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | COMPFIN | 16 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-17 14:30:00 | Pass | Reviewed doors found one with broken spring caused by door arm support giving way.Second door was operational but there was concerns onsite about the age of the springs and this was the reason behind the initial descriptionDescription of work required:" Removal of the existing components.“ Dismantle spring support bar on both doors" Supply and installation of 4 x new replacement F962 springs" Test and check door operation." Lifting equipment to be provided by Assa Abloy Entrance Systems" The above work is to be carried out during normal business hoursJOB COMPLETED
MSA-DTAG | WA3123844 | Ground floor front door - Aiphone LEF-5 intercom non functional | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Mar 2020 | 2020-03-16 14:07:55 | 2020-03-24 10:15:00 | Fail | Sourced part and back to site continued with fault finding. Tried to replace new intercom in reception but still hear strong static noise. Further check located the problem to be the interference from the 240Vac power cables and light getting in through the cable from reception to entry. Rerun cable from reception to entry and tested all ok after.
MSA-DTAG | WA3124235 | main entrance carry out fire mode test with Grama Bazita on Saturday 21 March from 08.00am – 14.30pm | Joondalup Courthouse | GMP-BR-HO | Air Conditioning | Materials (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-04-04 16:30:00 | Fail | Attend site with grama bazita and icon logic. Carry out further checks on fire system. Access mechanical switchboard 1,2,3, and 4. Confirm all fire relays are being powered from the fire panel. Put panel into alarm and found Power to remain to fire relays. Found the way the panel has been wire would cause the fire relays to remain on no mater what. Grama bazita reported that the panel was a mixture of old and new printed circuit boards that are not compatible with each other. Fire panel still requires further work to correct operation.
MSA-DTAG | WA3124242 | carry out fire mode test with Australian HVAC on Saturday 21 March from 08.00am – 14.30pm | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-21 12:00:00 | Pass | Will need to return with 2 sparkys and controls boys for mech system to further investigate system. Will require a full day of shutdowns
MSA-DTAG | WA3124387 | Level 31 director general door access denied out of hours | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-07-16 11:00:00 | Fail | Resolved and programmed card for 24 hour Access.
MSA-DTWD | WA3123824 | Tower block level 1 Mens toilet - broken flush button | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-17 12:00:00 | Pass | Complete
MSA-DTWD | WA3123827 | L1 Aberdeen st Entrance Light bollard broken | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-04-09 08:24:00 | Fail | Replaced broken bollard top with new. Tested all working properly. job completed
MSA-DTWD | WA3124193 | ground entrance sign has been graffited | Joondalup McLarty Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 16 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-19 09:15:00 | Pass | REMOVAL OF GRAFFITI FROM SIGN LOCATED GROUND ENTRANCE
MSA-DTWD | WA3124320 | Foyer billi filter needs changing as it is flashing | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 16 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-18 08:20:00 | Pass | CHECKED UNIT REPLACED FILTER A402010837 - FOYER BILLI QUADRACLIENT WOULD NOT SIGN RE COVID 19 ISSUES AROUND THIS
MSA-DTWD | WA3124340 | D block L2 D201-Aircon Fan Coil has stopped working | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-05-28 16:00:00 | Fail | Picked up required parts,attended site, isolated and tagged out system.removed cieling tiles and removed burnt out fan motor,installed new motor and barrel, wired into system and tested, monitored system and left all operational
MSA-MRWA | WA3123619 | L1 first aid room-flickering light | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 16 Mar 2020 | 2020-03-17 17:00:00 | 2020-03-17 15:08:00 | Pass | Replaced light
MSA-MRWA | WA3123747 | ground front garden Fence has large gap at pole, rectify to close gap | Materials Engineering Branch | GMP-BR | Building | Steel Fencing & Gates (BU) | MR - Handyperson - PFM | 3 | COMP | 16 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 10:30:00 | Pass | Fit new wire to the end of the fence
MSA-DCA | WA3151251 | Alarm fault on RO Plant (Mechanical) | Art Gallery of WA - James St - Administration Block (Block A) External East | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-18 10:00:00 | Pass | Attended call. RO plant fail alarm. Replaced pre filter cartridges and manually carried out back wash of carbon tanks. Carbon Tanks require replacement. Quotation to follow, not RM item. Reset RO plant and adjusted ballast for maintaining exceptable pump head pressure. Reset FCU Humidifiers as suffered water loss after pump failure. No further alarms. All related plant equipment in operation.Closed job.
MSA-DCS | WA3139779 | Unit 8 A5, 9 B7, C2 C4 and C6 toilets leaking in plumbing duct | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-26 16:30:00 | Fail | Replaced leaking pan lines in various ducts in u8
MSA-DCS | WA3139893 | kitchen cool room 4 door handle broken | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 07:54:17 | 2020-05-14 07:45:00 | Fail | Check door after installation. All ok. Unit operational at time of.departure
MSA-DCS | WA3139900 | BR unit 1 D10 camera cover is broken | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 07:57:11 | 2020-03-18 08:17:00 | Fail | Replaced camera window, job completed.
MSA-DCS | WA3139903 | External gardens-zone 24 retic not working | Hakea Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 17 Mar 2020 | 2020-03-19 17:00:00 | 2020-04-17 08:58:00 | Fail | external zone 24 not working, BRAF SUBMITTED AND SUBSEQUENTLY DECLINED. NO FURTHER ACTION TAKEN.
MSA-DCS | WA3139906 | crises care entry door electronic lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 08:02:14 | 2020-03-17 10:30:00 | Pass | test lock and door no fault found.
MSA-DCS | WA3139910 | BR crises care CCTV monitor 3 not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 08:04:10 | 2020-03-17 15:30:00 | Pass | Fixed video feed for crisis care monitor, job completed
MSA-DCS | WA3139914 | CCU (11) - Control Room-Monitor number 5 has an intermittent fault and keeps cutting out | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Mar 2020 | 2020-03-19 17:00:00 | 2020-04-09 15:12:00 | Fail | Access heavily restricted due to infirmary area, gained access to control room. Supplied and replaced CCTV monitor 5, replaced and altered mounting bracket due restricted space with surrounding monitors, run cabling through cavity, replaced BNC for new and tested monitor fully operational.
MSA-DCS | WA3139916 | Unit 14 - A & C-leaking pipe in laundry cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-19 12:00:00 | Pass | Remove spout, thread seal spout, reinstall spout and test
MSA-DCS | WA3139921 | Unit 14 - B11-B-11 tap continuous running in sink. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-19 11:00:00 | Pass | Remove and replace 2 x quarter turn spindles to basin in plumbing duct
MSA-DCS | WA3139934 | karakin C25 Door handle is broken on cell door | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-04-08 09:45:00 | Fail | supply and install custom door handles and fixings
MSA-DCS | WA3139938 | jasper staff office Roof leak during rain in kitchen area | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-05-05 17:01:00 | Fail | located leak and rectified
MSA-DCS | WA3139973 | Kitchen - Brat pan not going up or down | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-23 14:00:00 | Fail | Kitchen Brat pan ram not lifting. Check pan & controls. Disconnect power, remove faulty ram. Repair gears in ram. Return & install. Ram now working correctly. Report to staff.
MSA-DCS | WA3140016 | Kitchen - Front Entrance Kitchen front gate ramp requires repairing as it is now a trip hazard | Casuarina Prison | GMP-BR- HO | Carpentry | Staircases, Balustrades and Handrails (CA) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 09:10:23 | 2020-03-17 15:00:00 | Pass | secured ramp
MSA-DCS | WA3140026 | ISU B07 Camera is blank not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-23 15:25:00 | Fail | Attended site, traced cables, repaired cable fault with B07. Tested Camera and recording OK.Job Complete
MSA-DCS | WA3140033 | Unit 5 - D10-Hand basin in cell is blocked, not draining away. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-19 13:00:00 | Pass | Plunge drain, remove trap, remove spoon from trap, reinstall and test
MSA-DCS | WA3140035 | MPU (8) - Day Room-Staff aircon unit needs attention | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-27 12:30:00 | Fail | Arrived on site and signed in tools,checked pressure test system held pressure overnight,released nitrogen and vac out system and recharge with R22, test run unit all running ok at present.
MSA-DCS | WA3141874 | Level 1 bank of lights around desks:W1.51, W1.43, W1.40, W1.33, W1.32, W1.26, W1.22, W1.20, W1.18 | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 10:27:43 | 2020-03-17 16:00:00 | Pass | Repaired lighting on Level 1
MSA-DCS | WA3143736 | Unit 14 - Court Yard-Gate camera appears to not be working. | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-30 13:00:00 | Fail | Attended site and replaced camera lens with new 2.7mm lens. Seme stock used. All replaced and tested ok. Job complete
MSA-DCS | WA3143877 | Unit 14 - A & C lights in wings programs rooms cannot be turned on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-17 12:00:00 | Pass | Investigated access control systems and all working ok. Requires electricians to inspect switchboard side.
MSA-DCS | WA3144147 | Staff room - bain marie is shorting the circuit | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-26 12:31:00 | Fail | Replaced simmerstat, 1000w QI Lamps & lamp socket
MSA-DCS | WA3144213 | Unit 5 - Cell A22 has a broken toilet pan | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | COMPFIN | 17 Mar 2020 | 2020-03-18 11:20:10 | 2020-03-17 17:35:00 | Pass | Replaced broken toilet pan and adjusted pipework to suit
MSA-DCS | WA3145136 | MECHANICAL W/S 15 amp gpo not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-19 15:00:00 | Pass | Investigate mechanical workshop 15 amp gpo not working. Rewire gpo.
MSA-DCS | WA3146810 | Unit 4 Control room - PA handpiece is faulty - intermittently working | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-04-23 12:52:00 | Fail | Hand piece tested multiple times without fault. Hand set has been replaced before so job will be closed as fault could not be replicated.
MSA-DCS | WA3151022 | Gymnasium - Office-gym camera faulty/no picture | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-24 08:00:00 | Pass | Attended site and investigated the fault.Found faulty fibre modem S732DVT-EST2 - replaced with critical spare part on site.Tested.All ok at departure
MSA-DCS | WA3151042 | Unit 14 - Program Room East-lights in programs room not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-04-06 15:30:00 | Fail | Repaired multiple faulty lights in unit 14 programs room. Repaired damaged cable in roof space.Ongoing intermittent fault, checked lights & tested circuit. Unable to find any faults, only thing left to do is replace all ballasts & RCD's.
MSA-DCS | WA3151069 | Cript front gate BMS system faulty boiler and pumps not firering up | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Schneider-DO NOT USE-refer ZSCH03_BMA | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 13:56:55 | 2020-03-18 10:30:00 | Pass | On investigation found when pinging master controller found losing ping replies intermittently, suspect network issue from gate house to master controller in boiler room, moved PC (Front End) from gate house to boiler room connected directly to master controller in doing so system now operating as required .
MSA-DCS | WA3151077 | Administration - Office Plant room door not closing properly keeps sticking | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-04-10 10:00:00 | Fail | Job completed - service lock, replace bolt throw and temp. repair door closer arm. Attend site replace door closer and adjust to suit
MSA-DCS | WA3151177 | L8 2x Meeting Room 8.4 & 1x Outside RM8.W lights out | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-17 18:00:00 | Pass | Repaired lighting on level 8
MSA-DCS | WA3151192 | The image on camera PTZ 20 is blurred. | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 15:40:36 | 2020-03-19 08:00:00 | Fail | Site spares used : fibre modem 732R .Job complete
MSA-DCS | WA3151196 | L2 ladies toilets light has gone out | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-20 15:45:00 | Pass | Repaired lighting on level 2
MSA-DCS | WA3151233 | Entry control screen is permanently down | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Mar 2020 | 2020-03-17 21:04:07 | 2020-03-18 10:12:00 | Fail | Sourced parts, attended site, repaired faults with multiple monitors and MDAS system.Tested OKJob Complete
MSA-DCS | WA3174366 | Investigate and repair damage to Lenard Unit post incident | Banksia Hill Detention Centre | GMP-BR-RC | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Mar 2020 | 2020-03-23 17:00:00 | 2020-04-23 10:00:00 | Fail | REPAIRS MADE- SMASHED WINDOWS REGLAZED
MSA-DCS | WA3184112 | External zone 2 - broken retic - Replacement of cancelled WA3097807 | Hakea Prison | GMP-BR- HO | Landscaping & Gardening | Materials (LG) | Pumps n Pipes | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-04-02 14:00:00 | Fail | main line break required BRAF and excavator. all in working order when finished
MSA-DFES | WA3139968 | both front engine room doors springs are broken | Kensington (old) | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-27 11:15:00 | Fail | Technician attended the site of Kensington Fire Station on 17/03/2020 for 2 x damaged doors.Detailed for further repairs, required to reattend with parts on 19/03/2020REMOVED AND REPALCED DAMAGED SPRINGS / REINFOCED WINDRACE - COMPLETED
MSA-DFES | WA3151194 | Workshop - 2nd row of newly installed lights are dull, please adjust to be as bright as others | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-18 11:45:00 | Pass | Locate faulty lights. It was reported one row of high bay lights were more dull than the others. On arrival the lights are the same has the others in the workshop. Discussed with Cathy and she also agreed they looked to same. Tried to find out the type of light they were so I could confirm if they could change the settings but I could not find them. It was noticed yesterday the lights were dull and it was overcast on that day and there is skylight above the lights.
MSA-DFES | WA3151198 | workshop alarm panel beeps when trying to set itself twice a day | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Monitoring (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-20 16:00:00 | Pass | 19/3/20 - Dylan ParslowInvestigated issues with alarm keypad.Had to also visit Cockburn to access log. Found PE Beam alarm activating during the day. Reprogrammed input.24/3/20 - Dylan ParslowReported issue still continuing.Checked programming again from Cockburn, changes made had not uploaded correctly. Reprogrammed, and tested. All ok.No charge for return visit.
MSA-DFES | WA3151229 | Front door - lock is not working - building cannot be secured | CFRS Belmont | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 17 Mar 2020 | 2020-03-17 20:46:09 | 2020-03-17 18:05:00 | Pass | Replace broken mortice lock on front door
MSA-DTAG | WA3140028 | front counter doors not staying open | Westralia Square | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-17 10:54:00 | Pass | Adjusted programming for Level 10 access to override access zone. Tested OK.
MSA-DTAG | WA3147068 | Milestone - 3 recorders not working | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Equipment | Security Equipment (EQ) | Sapio Pty Ltd | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-18 16:30:00 | Pass | Supreme Court Milestone Recorder 1 faulty. Deleted footage on storage ray hard drives. Checked Milestone Recorder 1,all OK
MSA-DTAG | WA3147877 | Ground floor - Intercom tunnel that connects Midland court to Midland police Station is not working | Midland Courthouse | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-19 09:30:00 | Pass | Checked intercom not working at all. Further check located the problem to be the power issue. Rectified the fault and tested it all ok.
MSA-DTAG | WA3148061 | Reticulation for the garden in front of the building is not working | Midland Courthouse | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-24 09:00:00 | Pass | Tested controller & found master valve solenoid faulty
MSA-DTAG | WA3151066 | Male toilets (in PRB) leaking urinal - unknown liquid is dripping from the base of the urinal | Central Law Courts-Main Building-Level 6 | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 17:00:00 | 2020-04-08 10:00:00 | Fail | Complete
MSA-DTWD | WA3139927 | L1 Facility entrance door Access control door not responding | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | Schneider-DO NOT USE-refer ZSCH03_BMA | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-19 12:00:00 | Pass | Replaced controller and re programmed.Replaced batteries with 7 and hour batteries as 5 are not available for r weeksWill return with 5 and hour batteries.Checked and tested doors to confirm door operation
MSA-DTWD | WA3142898 | L2 A222 Repair white board fallen of wall | East Perth Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-20 12:30:00 | Pass | Complete
MSA-DTWD | WA3146155 | block 1 windows not securing 1G27 office-Josh must attend | Thornlie Campus | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-25 15:30:00 | Fail | Replaced damaged window sashes with new
MSA-DTWD | WA3151101 | B block B17 rear extit door lock not working with key | Murdoch Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-20 12:00:00 | Fail | Replaced lock & key
MSA-DTWD | WA3151176 | Printing area - water leak from ceiling | West One Services | GMP-BR | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 17 Mar 2020 | 2020-03-18 17:00:00 | 2020-03-17 17:00:00 | Pass | Attended P1 and found box gutters and downpipes to be blocked - removed all debris
MSA-DTWD | WA3151188 | B24 fault with fire sensor 13-please call security when on site 040 777 3870 | Murdoch Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 0 | CLOSE | 17 Mar 2020 | 2020-03-17 19:43:54 | 2020-03-19 11:30:00 | Fail | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro TAFE- MurdochSite contact: Security - 0407 773 870Work Order Number: WA3151188Priority #: 0Call out Date: 17/03/2020Target finish: 17/03/2020 19:43Original information: B24 fault with fire sensor 13-please call security when on site 040 777 3870Attended site:Date:17/3/20Start Time:16.00Finish Time:17.00Techs on Site:1Works Carried Out: Brigade had reset the panel so I couldn’t find the one in alarm. Is conventional zone on a zone monitor. Left that isolated to return tomorrow to find. Is about 6 m at the highest and 3 m at lowest Returned to site:Date:18/3/20Start Time:09:45Finish Time:13:30Techs on Site:1Works Carried Out: Checked detectors at a lower height in office area. Was not able to get to zone monitor which is in roof space in office area and will need a EWP for detectors in soils prep warehouse.Left zone 3 isolated until further investigation. Returned to site:Date:19/3/
MSA-DTWD | WA3151221 | E Block roof leak above E38 coolroom | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-20 12:30:00 | Pass | Sealed around several roof penetrations
MSA-DTWD | WA3151228 | A Block Level 3 Room A354A Roof leaking into staff kitchen & common area | Leederville Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 0 | CLOSE | 17 Mar 2020 | 2020-03-17 20:50:20 | 2020-03-27 15:00:00 | Fail | Completed works as per BRAF
MSA-DTWD | WA3168160 | Retrospective work order do not attend - Replaced 2 x broken ‘break glass alarms’ | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | SCAVENGER SUPPLIES PTY LTD | 3 | CLOSE | 17 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 15:45:00 | Pass | Replaced 2 x broken ‘break glass alarms’Location:South Metro TAFE-Mandurah Campus (formerly Peel)work completed on 2 different dates
MSA-MRWA | WA3140000 | ground Notices and Permits kitchen-filter CW tap water is cloudy specks of white dots in water | Heavy Vehicle Services | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-18 09:30:00 | Pass | Attended 18.3.2020 checked system A40191047F no specks of white or anything else evident possible bubbles may have appeared in water could not see any issue with unit
MSA-MRWA | WA3140047 | smoking area table glass table requires cleaning | Materials Engineering Branch | GMP-BR | Furniture | Outdoor Furniture (FU) | MR - Handyperson - PFM | 3 | COMP | 17 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-17 15:11:00 | Pass | Cleaned both tables
MSA-MRWA | WA3143094 | Ground floor kitchenette 2 lights are out | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | COMP | 17 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-18 10:00:00 | Pass | Replaced ceiling globes back in working order. Counter light is broken and require electrician to attend
MSA-DCA | WA3164422 | VIP Carpark Safety sensor beam does not work. Gate does not stop closing if beam interrupted. | Perth Concert Hall | GMP-BR | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-18 16:31:00 | Pass | Replaced faulty set of pe beams on gate. Tested ok.
MSA-DCA | WA3164798 | Ground - EPS Area -fault with fume hood, not working. Possibly due to power outage at weekend | Collection and Research Centre Welshpool | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-19 08:30:00 | Pass | Attended site 19-3-20. Fume cupboard in CRC servicingacid digestion area not operating correctly. Apllied tests and checks to find VSD to have tripped. Reset VSD and checked operation voltage and current (ok). Investigation found VSD to have tripped due to power interruption. Job to be closed and quotation to be submitted to supply a UPS for the system.
MSA-DCS | WA3163603 | ECR all of the monitors, entry control and camera's are down | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Mar 2020 | 2020-03-18 11:00:31 | 2020-03-18 10:15:00 | Pass | Attended site checked and found Monitors 2&3 workstations are down. Reboot workstations, reassigned cameras to monitors and tested all ok.
MSA-DCS | WA3163611 | front of the prison sallyport not closing properly | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 18 Mar 2020 | 2020-03-18 11:08:10 | 2020-03-23 16:00:00 | Fail | 23/03/20replace motors and controller to match new motors
MSA-DCS | WA3163616 | visits area cameras not working in this area | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Mar 2020 | 2020-03-18 11:12:03 | 2020-03-18 12:30:00 | Fail | Fixed multiple off line ip cameras from visits, job completed.
MSA-DCS | WA3163727 | Unit 6 - B10-cell window in B10 vent will not close and open correctly | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Mar 2020 | 2020-03-24 17:00:00 | 2020-05-11 10:00:00 | Fail | EXISTING VENT REPAIRED
MSA-DCS | WA3163754 | Unit 3 - A4-faulty power point near window | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-18 11:30:00 | Pass | Replaced damaged cell gpos in unit 3 a4
MSA-DCS | WA3163789 | PCS serveral roof leaks | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-05-05 16:41:00 | Fail | located leak and rectified
MSA-DCS | WA3163791 | Unit 6 roof leak A wing day room near fridge-this has been repaired recently and before that | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-06-12 12:56:00 | Fail | located leak and rectified
MSA-DCS | WA3163796 | CCU prage office air con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-04-14 09:16:00 | Fail | Further works required. BRA declined
MSA-DCS | WA3163798 | CCU air con in cells 7 to 11 not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-04-02 16:13:00 | Fail | System is running correctly
MSA-DCS | WA3163818 | External Gardens by the training building main retic line is leaking | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 11:30:00 | Pass | replaced damaged sprinklers
MSA-DCS | WA3163829 | External Gardens - Zone 7 retic is not working | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-25 15:00:00 | Fail | located solenoids and found faulty wiring soldered faulty joints
MSA-DCS | WA3163832 | External Gardens - Zone 8 retic is not working | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-31 17:00:00 | Fail | FOUND FAULTY WIRING REPLACED BROKEN SPRINKLERS
MSA-DCS | WA3163834 | External Gardens - Zone 9 retic is not working | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-30 15:02:00 | Fail | Zone 9 Retic not working wiring issues
MSA-DCS | WA3163835 | External Gardens - Zone 10 retic is not working | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-04-30 14:00:00 | Fail | zone 10 retic not working, CORRECTED WIRING ON ZONE 11 AND THEN ABLE TO RECTIFY ISSUES ON ZONE 10. ALL REPAIRED AND IN WORKING ORDER.
MSA-DCS | WA3163837 | External Gardens - Zone 11 retic is not working | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-04-30 08:00:00 | Fail | RETIC ZONE 11 NOT WORKING. MULTIPLE WIRE FAILURES, FULL TRACKING AND FAULT FINDING REQUIRED
MSA-DCS | WA3163838 | Unit 13 - A14-shower drain in cell A14 has a blockage. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-19 14:00:00 | Pass | Plunge, moflo, rinse, plunge to no avail. Pickup K-50 drain machine to clear blockage.
MSA-DCS | WA3163840 | External Gardens - Zone 12 retic is not working | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 14:00:00 | Pass | Major works to be undertaken and will require quotations in the future.
MSA-DCS | WA3163852 | unit 4 D landing camera has narrow zoom | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 08:37:14 | 2020-04-24 09:01:00 | Fail | Encoder and camera replaced. Refer to work notes for further detail.
MSA-DCS | WA3163913 | dairy pressure switch faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-20 15:00:00 | Pass | Investigate dairy pressure pump not working. Found faulty pressure switch. Requires replacement. Source replacement part. Install and test new pressure switch at dairy.
MSA-DCS | WA3164062 | medical center light fitting hanging from ceiling | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-19 08:30:00 | Pass | Investigate and repair medical light fitting
MSA-DCS | WA3164070 | Boiler House - Workshop-main hot water system faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-19 08:38:00 | Pass | Liaise with Schneider electrics in getting the BMS system up and running
MSA-DCS | WA3164288 | Crypt - Control Room-battery backup alarms faulty on electrical circuit | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-18 13:30:00 | Pass | Checked and tested UPS systems in gatehouse crypt. All ok
MSA-DCS | WA3164306 | ceiling needs to be cut for blocked drain for air con | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Main Reception Area | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Mar 2020 | 2020-03-25 17:00:00 | 2020-04-01 07:45:00 | Fail | MANHOLE CREATED & PAINTED
MSA-DCS | WA3164523 | unit 3 cell 40 needs to the barrel change and fit master cell 40 | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-20 17:30:00 | Pass | Unit 3 Cell 40 - master key did not work this cell as this is the incorrect key Lock was in non operational stateOld lock removed , new lock fitted
MSA-DCS | WA3164617 | Jasper A-B-C 2x multiple flus & flashing damaged | Banksia Hill Detention Centre | GMP-BR-RC | Building | Steel Work (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 13:39:49 | 2020-05-05 17:04:00 | Fail | replaced flues and flashings and electrical works.
MSA-DCS | WA3164622 | Jasper A-B-C 2x fire strobe damaged | Banksia Hill Detention Centre | GMP-BR-RC | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 13:41:32 | 2020-03-19 09:00:00 | Pass | 19/03/2020Attended site to replace strobes - Unable to access as no escorts available.24/3/20 JN MSReplaced strobes and tested operation - all ok.
MSA-DCS | WA3164625 | Jasper A-B-C 2x aerial damage | Banksia Hill Detention Centre | GMP-BR-RC | Electrical | General Electrical (EL) | Sapio Pty Ltd | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 13:43:17 | 2020-03-23 10:30:00 | Fail | Job completed - stalled new TV antenna in Jasper Wing. Commissioned and tested. TV reception clear. Job completed
MSA-DCS | WA3164642 | Administration - Security Office-The Keywatcher laptop in Security isn't reading any databases. | Casuarina Prison | GMP-BR- HO | Security | Keys & Access (SE) | BJ SYSTEMS | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 12:37:24 | 2020-05-06 10:00:00 | Fail | 18/03/2020 - Keywatcher was offline. Restarted network connection. West keywatcher has lost transactions. Need to find out how to fix database. Need to re-attend with support to correct issues06/05/2020 - Found missing setting and corrected. Now able to run report of recent events
MSA-DCS | WA3164649 | L2 team leaders office water has come coming from the light fitting | Midland (North East Metro) | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-07-22 10:00:00 | Fail | Attended site and carried out inspection.Vacuumed up all pidgeon waste and removed all small rubbish from roof.Sealed up all holes in roof sheets.Electrition attended site and removed fluorescent lights from ceiling, removed water damaged ceiling and replaced. Reinstated fluorescent lights.
MSA-DCS | WA3164658 | Veg Prep W/S cry-vac machine has a burning smell and making a noise when in operation | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-24 13:30:00 | Fail | Veggie Prep Cryovac Machine has burning smell & is noisy. Check machine & controls. Remove for repairs. Run cycle, found 3ph power plug had burnt pins. Clean up pins & tighten all connections. Test ok.
MSA-DFES | WA3164262 | Roof leak in both of tunric rooms | CFRS Canning Vale | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 17:00:00 | 2020-06-18 11:30:00 | Fail | CARRIED OUT ROOF LEAK REPAIRS AND PAINTED OUT WATER STAIN ON THE CEILING
MSA-DTAG | WA3164020 | disable public toilet light flickering | Midland Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-18 12:00:00 | Pass | Replaced tube and starter
MSA-DTAG | WA3164212 | Basement Lift call button has become detached from the control panel | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 18 Mar 2020 | 2020-03-18 14:57:34 | 2020-03-18 13:45:00 | Pass | Replaced damaged button on basement.
MSA-DTAG | WA3164778 | registry ground front glass door making loud squeaky noise | Mandurah Courthouse | GMP-BR-HO | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 13:22:00 | Pass | Found sticky substance covering bottom rail of door that grip the rubber of the floor guide and make noise. Cleaned both rails and tested door. All ok. NO CHARGE - As this is covered under warranty as maintenance was just completed.
MSA-DTWD | WA3163597 | D block L3 staff kitchen Hot water unit Boiler to sink has ceased working | East Perth Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 18 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-31 13:45:00 | Fail | REMOVED TO WORKSHOP - TESTED DIAGNOSED REPLACED HOT LEVL SENSOR KIT , HOT SAFETY LEVEL KIT LOOM BOILING HEAD GASKET - HOT PUMP AND REINSTALLED UNIT ZIP HYDROTAP A404211089
MSA-DTWD | WA3163690 | TM169 coming up on screen as temper fail every 12 secs | Munster Campus (ACEPT) | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 18 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-31 12:31:00 | Fail | 20/03/2020Attend site for TM169 tamper,Found 2x tamper switch dirty/sticky have cleaned, now working fine when onsite.24/03/2020Attend site and see Rick, found No faults on system or Titan?, Rick will take a photo if/when fault happens again, will callSecurex when in fault, all alarm working when onsite
MSA-DTWD | WA3163929 | reception and tower fire panels are in fault | West One Services | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-18 16:00:00 | Pass | Flt on network system requires honeywell tech
MSA-DTWD | WA3164371 | F Block - Air Con in the back work room of the Library is leaking water from the front vent | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-31 12:45:00 | Fail | Attended site, found unit pumping water, but stopped after 5 minutes, suspect pump faulty, replace pump and drain Quote submittedAttended site, isolated system , removed old drain pump and clear tubing , installed new pump and accessed roof to install new tubing , tested 8L of water through pump and all working well
MSA-DTWD | WA3164376 | E block E608 Water leaking from air conditioning-see notes | Midland Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-20 13:15:00 | Pass | Block 6 leak above air conditioner from duct - will need to disconnect system and dry pans - remove of ductworkJob related to BRAF submitted on WA3089012 so closing this off costs to date.
MSA-DTWD | WA3164385 | BLD House 816 Water Meter major leak | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-19 14:00:00 | Pass | Replaced badly leaking water meter and meter tap to house 16
MSA-DTWD | WA3164470 | house 813 Leaking water meter | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 15:00:00 | Pass | Replaced leaking water meter to house 13
MSA-DTWD | WA3164551 | F Block Roof area above F114 gutters are severely rusted | Midland Campus | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-04-24 10:15:00 | Fail | Works as per BRAF Complete
MSA-DTWD | WA3164573 | canteen faulty bain-marie not working | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 18 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-19 11:25:00 | Pass | Arrived on site, found the crimp on energy reg has burnt off. Re crimped and tested unit Test ok
MSA-DTWD | WA3164730 | BLD 832 Burst water pipe next to kitchen | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-25 17:00:00 | Fail | Removed section of brick and concrete to expose leaking water pipe and reinstate at building 832
MSA-DTWD | WA3164774 | CRAC unit - Hire of temporary server room a/c for March 2020 | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 18 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-25 09:44:00 | Pass | Portable Hire for March 2020
MSA-MRWA | WA3163897 | ground G – Dumb Waiter Store – replace light, return to service. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 18 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-18 10:45:00 | Pass | Attended no fault found possibly intermittent changed globes and will monitor
MSA-MRWA | WA3164639 | ground front gate reception not receiving calls from the gate intercom when button is pressed | Materials Engineering Branch | GMP-BR | Security | Access Control (SE) | Siemens Ltd | 1 | CLOSE | 18 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-20 11:30:00 | Fail | Tested intercom unit, unit is powered on & dialing tone is present. Staff stop receiving call after a staff left & account deleted. Possible routing issue
MSA-DCA | WA3166685 | staff toilet male disable cubicle slow leak from toilet bowl | State Library of WA-Main Building-Level 4-4.10. - Male Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-23 10:20:00 | Pass | Removed toilet replaced pan collar and key seal reinstalled toilet
MSA-DCS | WA3165099 | Kitchen - brat pan behind oven is not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 07:27:24 | 2020-04-20 12:30:00 | Fail | 19/03/2020 - Called as requested to the bratt pan not working. Found the ignition in very poor condition and burner starting to corrode out as well, released the ignition probe to get the unit to operate and made temporary repairs to the burners. Tested and working ok although parts needs replacing.20/04/2020 - Cleaned burner jets, installed burners, replaced some missing insulation on some wires, repaired with tape. Checked burner pressure, ok and checked operation of the unit. All good.
MSA-DCS | WA3165102 | Kitchen - steam oven pipe has broken off | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 07:30:55 | 2020-03-19 13:05:00 | Pass | Arrived to site to find RO bladder tank valve was snapped off. Old bladder tank valve has been removed and new valve installed. Unit is now operating correctly.
MSA-DCS | WA3165169 | Unit 11 - Seniors office air con is not turning off | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 19 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-20 12:39:00 | Pass | Adjusted SP
MSA-DCS | WA3165198 | Unit 8, A Wing near cell A3- roof leak in skylight | Hakea Prison | GMP-BR- HO | Roofing | Rooflights and Skylights (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-05-05 16:50:00 | Fail | located leak and rectified
MSA-DCS | WA3165200 | Unit 7, H Wing- half way down wing roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-05-05 16:51:00 | Fail | located leak and rectified
MSA-DCS | WA3165278 | Unit 5 - D Wing Cell D4 Sink tap leaking badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-20 11:00:00 | Pass | Remove and replace 1x quarter turn spindle
MSA-DCS | WA3165293 | Unit 13 - C Wing Cell C16 loose taps and shower drain blocking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-23 08:30:00 | Pass | Remove grate, remove hair, moflo, rinse, plunge, reinstall grate and test. Tighten up tapset.
MSA-DCS | WA3165297 | Unit 5, Cell C14 & C15 Service duct- flexiable ventilation tube is broken | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 14:12:00 | Pass | Replaced duct work
MSA-DCS | WA3165303 | unit 2 C wing water isolation valve leaking will not turn off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-24 21:00:00 | Fail | Replaced faulty isolation valve
MSA-DCS | WA3165304 | unit 3 B wing water isolation valve leaking will not turn off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-24 23:05:00 | Fail | Replaced faulty isolation valve. No lid found. Backfilled but it needs a new inspection lid
MSA-DCS | WA3165329 | klitchen cool room 7 display panel faulty | Hakea Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 09:14:02 | 2020-03-24 16:24:00 | Fail | System is displaying correctly
MSA-DCS | WA3165336 | Unit 4 - A & C-sinks blocked dayroom | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-20 11:00:00 | Pass | Plunge both sinks to clear blockage
MSA-DCS | WA3165338 | Boiler House- BMS faulty | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Schneider-DO NOT USE-refer ZSCH03_BMA | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-24 09:30:00 | Pass | Returned PC to gate house, reconnected comms cable and demonstrated issues we are having, Datatec have instructed they will service\clean there fibre's to improve communication
MSA-DCS | WA3165352 | Amenities leaking roof-see additional notes | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-07-27 10:34:00 | Fail | INSTALL NEW FLASHING & SHEETING - TURN UP VALLEY EDGES ON APEX ROOF - CLEAN
MSA-DCS | WA3165382 | Eyre, Kitchen- Urn is not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-24 10:45:00 | Pass | Assessment on unit is boiling issue. Rheem notified for warranty Rheem finally attended on 6.4.2020 and replaced parts under warranty.
MSA-DCS | WA3165448 | permiter fence camera 295 response road camera not working fuzzy | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Mar 2020 | 2020-03-19 14:02:51 | 2020-05-15 16:15:00 | Fail | Investigated SHU PTZ camera. Tested camera, tested head end equipment and maxpro equipment, traced data cables and repaired cable fault. Tested Signature Slip and PTZ control from both maxpro system and Indigo systems.Tested OKJob Complete
MSA-DCS | WA3165480 | orchid pump house pump pressure realife valve faulty | Wooroloo Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-04-06 14:00:00 | Fail | Pressure Relief Valve faulty on Orchid pump. Check valve & controls. Dismantle pipework, remove valve. Install new valve. Return make up new brackets to hold valve. Install, set pressure on valve. Check flow rate at dripper lines.
MSA-DCS | WA3165482 | orchid pump house control pannel faulty | Wooroloo Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-27 12:00:00 | Fail | Control Panel faulty on Orchard Pump Filter system. Check controls & wiring. Dismantle & replace faulty relay & power supply to filters. Assemble & test. Reset backwash times & test.
MSA-DCS | WA3165940 | Unit 5, Cell D7- Antenna cable and point is broken | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-20 11:00:00 | Pass | Replaced both TV Points & Patch Cable. Tested signal, OK.
MSA-DCS | WA3166053 | Laundry, light is faulty in office | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-23 10:30:00 | Pass | Checked light in laundry, picked up replacement and installed.
MSA-DCS | WA3166056 | gym east disconnect emergency stop buttons and remove key reset Switch alter wiring to suit | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-24 15:00:00 | Pass | Removed em stop
MSA-DCS | WA3166278 | Paint Shop - water tap eastside corner copper pipe leaking, water inside paintshop | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-23 11:00:00 | Pass | Knock out bricks, cut pipes, alter pipes and install new tap
MSA-DCS | WA3166303 | Recreation entry office- window frame is coming apart | Bandyup Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-04-17 12:30:00 | Fail | FRAME/ GLASS RE SECURED
MSA-DCS | WA3166386 | unit 12 Cell A9 door has dropped and draging | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 11:47:03 | 2020-03-20 15:00:00 | Fail | realigned cell door
MSA-DCS | WA3166471 | unit 8 cell D4 water leaking from back of toilet pan outlet near wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 15:17:00 | Pass | repaired leaking toilet pan
MSA-DCS | WA3166585 | control room monitor from door to gatehouse is open, actually closed | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 12:50:07 | 2020-03-19 14:30:00 | Pass | Job complete
MSA-DCS | WA3166612 | kitchen - cool room 5 keeps tripping power | Hakea Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 13:14:53 | 2020-03-23 12:06:00 | Fail | Danny hellwig to attend
MSA-DCS | WA3166657 | gate house intercom not working SEME on site | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-19 16:30:00 | Pass | Job complete
MSA-DCS | WA3166670 | gardens cucumber shed wet wall panels require repairs falling out | Karnet Prison Farm | GMP-BR- HO | Building | Internal Walls (BU) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-28 12:40:00 | Fail | Replaced pads
MSA-DCS | WA3166671 | number 1 soak pump faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-05-22 13:00:00 | Fail | Investigate number 1 soak pump. Found not to be working. Removed pump from dam and disconnect. Connect temporary pump. Will need to quote on replacement.Source replacement part, replace number 1 soak pump
MSA-DCS | WA3166718 | reception holding cell air con not working in both cells | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-20 13:00:00 | Pass | See work logs
MSA-DCS | WA3168167 | Bandyup Prison - Unit 1 - Cell B10 and B11 - Toilet is backing up and close to overflowing. | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-20 17:30:00 | Pass | Carried out attempts to clear blockages. Rerurn visit required.
MSA-DFES | WA3166326 | Main office, front door- combination security door lock is broken | CFRS Maddington | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-19 16:30:00 | Pass | replace faulty digital lock to main office door
MSA-DFES | WA3166614 | Alarm system, code red box on alarm panel showing system 1 fault | CFRS Duncraig | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-19 14:10:00 | Pass | On arrival no fault on FIP or code red box- all clear
MSA-DFES | WA3166689 | Transportables-Briefing Room/PPC Store and Old AT Office-gutters overflowing when it rains | FESA RHQ - Forrestfield | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-20 12:00:00 | Pass | Gutters were full of leaves. Cleaned gutter and downpipes
MSA-DTAG | WA3165184 | Level 6 - business support - display monitor is not working | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 19 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-19 13:00:00 | Pass | Adjusted workstation time and date settings to match Milestone server as the difference in settings would not allow Milestone application to run on workstation. Job completed
MSA-DTAG | WA3165379 | Ground, Cell 2- Toilet constantly running | Mandurah Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 11:30:00 | Pass | Complete
MSA-DTAG | WA3165390 | Camera outside sallyport- Camera is constantly faulting and has the alarm going | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-19 14:30:00 | Pass | Attended site checked and found camera outside sally port was intermittently dropping off signal before. When technician arrived site, problem not happening anymore. Checked camera video cable and connections are ok. Reboot camera and tested it ok. If problem keep happening, maybe new camera need to be replaced.
MSA-DTAG | WA3165406 | Supreme Ct cameras turn yellow graphics-offline | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-19 11:30:00 | Pass | Unable to see cameras from Pacom Unison. Adjusted time on Pacom Server and checked.Job completed.
MSA-DTAG | WA3165518 | Basement sallyport door issues-please see additional notes | Supreme Court | GMP-BR-HO | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 17:00:00 | 2020-04-01 13:30:00 | Fail | 19/3 Adjusted photocells as necessary to stop intermittent reactivation of door and tested operation. Would recommend replaced old style send/ reflect with faac style photo beams to ensure secure operation each time. Braf raised1/4 Reattended and replaced faulty safety sensor. Reconfigured power supply. Moved mounting brackets to prevent false activation from bottom slat. Tested ok.
MSA-DTAG | WA3166366 | Special Clean request for CELL 1 - Prisoner has scabies | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 0 | CLOSE | 19 Mar 2020 | 2020-03-19 15:33:17 | 2020-03-19 18:30:00 | Fail | Job done as per Work Order
MSA-DTAG | WA3166722 | Duress alarms are not registering correctly in court custody control. | Rockingham Justice Complex | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-20 14:30:00 | Pass | Reported fault "duress" alarms are not registering correctly in court custody control. Part of GMS found without alarm running and no audio speakersoff. Reactivated and switched on. Tested OK.
MSA-DTWD | WA3165074 | H block - disabled toilet is blocked and overflowing into shower recess | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Mar 2020 | 2020-03-19 17:00:00 | 2020-03-19 16:30:00 | Pass | Found that disabled toilet block was blocked, used drain plunger and mo-flow to clear blockage
MSA-DTWD | WA3165292 | E block, Male toilets 4th cubicle blocked toilet. | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-20 10:42:00 | Pass | blocked toilet 4 cubical down male toilets e block unblocked
MSA-DTWD | WA3165357 | A Block, Main Entrance Exterior- Rope on flag pole is broken | East Perth Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-23 07:45:00 | Pass | Attend site Met and spoke with Steve Issue with rope fraying and having a knot in the line, unable to pull the rope through eyelet due to the knot rope needs to be replaced and flag removed and installed on new rope BRAF Submitted - Declined.
MSA-DTWD | WA3165360 | A Block, East End Ground Floor male cubicle - Blocked toilet | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-20 10:28:00 | Pass | blocked toilet male east end ground level toilet unblocked now
MSA-DTWD | WA3165487 | B Block, Room B13 - roof leak adjacent to windows | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-20 13:30:00 | Pass | Sealed box gutter joins
MSA-DTWD | WA3166268 | block 6 6E54 – Carpentry & Joinery Water leaking into classroom | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-05-13 15:45:00 | Fail | Works are now completed - Please see photos attached
MSA-DTWD | WA3166274 | Lifts 3 & 4 not working | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-19 14:30:00 | Pass | Reported lift 4 had loud noise when travelling and lift 3 not moving form lvl 1, found lift 3 RTS2 not coming in, checked andcleaned all floors landing contacts and tracks , tested lift 4 numerous times both directions, did not hear any loud noise when test
MSA-DTWD | WA3166282 | B Block, Student LadiesToilet appears to be leaking at the base, strong smell coming from cubicle. | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-19 17:00:00 | Pass | Found that the pan collar was leaking, could not remove pan without breaking it so siliconed around old rubber
MSA-DTWD | WA3166285 | A block staff room, under sink HWS faulty | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-04-06 11:23:00 | Fail | COMPLETED
MSA-DTWD | WA3166302 | block 4/5 urninal in male toilet blocked-may need grinding | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Mar 2020 | 2020-03-20 17:00:00 | 2020-03-19 14:45:00 | Pass | Complete
MSA-DTWD | WA3166317 | U block U5 stained floating ceiling panels | Rockingham Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-25 15:45:00 | Fail | Replaced stained ceiling Batts with new
MSA-DTWD | WA3166715 | A Block, west entry door jam has detached from wall | Rockingham Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 19 Mar 2020 | 2020-03-24 17:00:00 | 2020-04-21 12:00:00 | Fail | Removed old faulty door and replaced with new door and painted.
MSA-DCA | WA3168162 | Large Winch room, external- Portion of gutter has come away from building (see notes below) | Maritime Museum Victoria Quay-Main Building-External Area | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 20 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-24 09:30:00 | Fail | Temp Fence erected around hazard. Contacted PFM for further direction. Directed to close off and turned into quote WA3183495
MSA-DCA | WA3168259 | External Heating water pump leaking | Shipwreck Galleries-Main Building-Ground Floor-Plant Room - Car Park | GMP-BR | Mechanical Services | Pumps (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 20 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-24 10:30:00 | Fail | Completed approved repair works to remove and repair HWP system. Replaced cartridge seal and O ring assembly. Carried out tests and checks. System operating correctly.
MSA-DCA | WA3280177 | ***Retrospective Work order*** - External Heating water pump leaking **Claims Purposes only | Shipwreck Galleries-Main Building-Ground Floor-Plant Room - In Front of Lift | GMP-BR | Mechanical Services | Pumps (MS) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-05-25 07:30:00 | Fail | Retrospective work order for previous completed works. Works completed.
MSA-DCS | WA3167871 | front potable chlorine plant aniliser screen not working & filter housing leaking | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 2 | CLOSE | 20 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-21 12:47:00 | Pass | Fuse replaced in Analyser. New filter housing installed
MSA-DCS | WA3167902 | control room personel duress unit 13 transponder 21 unit 14 trans 22 comunication failure | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Mar 2020 | 2020-03-20 11:29:53 | 2020-03-23 11:42:00 | Fail | Investigated multiple duress transponder communnication faults, repaired all faults and tested OK.Job Complete
MSA-DCS | WA3167925 | area between zone 2 and obs post 8 pole lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Mar 2020 | 2020-03-24 17:00:00 | 2020-05-22 14:30:00 | Fail | Repaired pole lights.
MSA-DCS | WA3167953 | Amenities - Female Changeroom-dripping tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 12:00:00 | Pass | Remove and replace 2x quarter turn spindle in change rooms
MSA-DCS | WA3167960 | Unit 3 - D Wing-Night lights not working Cell D13 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-25 12:00:00 | Pass | Repaired faulty obs light in unit 3 d13
MSA-DCS | WA3167978 | SHU (9) - Lobby Area flickering light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 15:00:00 | Pass | Repaired multiple faulty lights in SHU lobbies and corridors. Waited access due to staff lunch. Returned and repaired the rest
MSA-DCS | WA3167981 | SHU(9), Cell A3- Hot water tap above the sink is unable to be turned off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 13:30:00 | Pass | Replace missing split pin in spindle (Delayed access by Assistant Superintendent)
MSA-DCS | WA3167992 | Unit 3 - A Wing A13 PERSONAL KEY LOCK SPINS CONTINUOUSLY | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 12:30:00 | Pass | Replaced hinges & lock latch bolt
MSA-DCS | WA3168112 | Health centre, ward 2- smoke alarm is activating | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 20 Mar 2020 | 2020-03-20 13:22:53 | 2020-03-20 11:30:00 | Pass | L2 D54 health day ward in maintenance fault. Replaced detector and performed loop test all ok. While on site vesda 4+5 in fault on panel noescorts available to investigate further
MSA-DCS | WA3168113 | unit 7 tumble dryer noisy/rumbling | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 20:00:00 | Pass | Dryer noisy. Check dryer & controls. Dismantle, remove all rollers & jockey pulley. Fit new parts. Repair wiring that was rubbing on belt. Assemble & test. Return to store.
MSA-DCS | WA3168175 | Admissions rec air con tripped & wont reset (suspect cable damage on unit) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-24 09:00:00 | Pass | Checked found the rat is inside the unit, removed and resettled the breaker. Started the unit and checked found OK.
MSA-DCS | WA3168354 | Unit 10, Control Room door lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Mar 2020 | 2020-03-21 11:24:18 | 2020-03-20 16:00:00 | Pass | replaceed faulty cylinder.
MSA-DCS | WA3168363 | external perimeter, zone 18 external MW2 constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-20 14:30:00 | Pass | Rectified and fixed constant alarming Zone 18 MW external .job completed
MSA-DCS | WA3168366 | Repair faulty lights in Training Rooms 2,3,4 and 8 | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-25 14:45:00 | Pass | Replaced failed lamps and starters
MSA-DCS | WA3168385 | unit 1 cell 21 gpo broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-27 10:00:00 | Pass | Investigate and replace unit 1 cell 21 gpo and replace damaged plug top
MSA-DCS | WA3168389 | Temporarily disconnect remote access from roller doors to Programmed Stores | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-20 15:30:00 | Pass | Disconnected stores roller doors. Left job open for further advice
MSA-DCS | WA3168449 | Unit 3, D Wing, Cell D13- Cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 08:30:00 | Pass | Repaired faulty lights in unit 3 d13
MSA-DCS | WA3168452 | INF (10)- B Wing, Cell B8- Tap not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 14:30:00 | Pass | Remove and replace 1x quarter turn spindle
MSA-DCS | WA3168462 | Unit 1 - A7 Toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-23 12:34:00 | Pass | Plunge toilet to clear blockage
MSA-DCS | WA3168498 | control unit 4 vesta in fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 20 Mar 2020 | 2020-03-21 13:08:24 | 2020-03-21 11:16:00 | Pass | Attended site for fault unit 4. When arrived found pipe 4 low cleaned out all sampling points all sitting fine when left
MSA-DCS | WA3168502 | control unit 5 vesta fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 20 Mar 2020 | 2020-03-21 13:13:26 | 2020-03-21 12:02:00 | Pass | Attended site for fault on fire panel. When arrived found pipe 4 low cleaned sampling points and all sitting normal when left.Recommend full comprehensive clean two times tech 8 hours. Design not suitable for cells that’s why it always goes into airflow faultAlso while on site unit 6 low airflow cleaned out back to normal working condition when left.Also while on site unit 1 went into alarm guards reset and back to normal checked it out but all sitting fine
MSA-DCS | WA3168551 | CCU cells 1,2,3 and 4 all the drains are blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Mar 2020 | 2020-03-21 13:37:24 | 2020-03-20 18:35:00 | Pass | Unblocked shower drains
MSA-DCS | WA3168563 | Kitchen- power point is faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-25 11:00:00 | Pass | Replaced cracked outlets
MSA-DCS | WA3168571 | Administration - Toilet-URINAL BLOCKED IN MALE TOILET ( FLOODS WHEN FLUSHING) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 15:30:00 | Pass | Use one bottle of bolgard in urinal drain, rinse and plunge
MSA-DCS | WA3168632 | control no camera activation for external zone 24, and try and bring up camera manually wrong camera | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Mar 2020 | 2020-03-20 19:27:17 | 2020-04-16 11:26:00 | Fail | Repaired Senstar and camera server faults, Tested perimeter alarms on zone 24 OK, tested camera switching and recording OK.Job CompleteParts:Consumables
MSA-DCS | WA3168689 | Fire alarm - Node 3 M1-15 Industries SPK M/Valve | Casuarina Prison-Industries | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 20 Mar 2020 | 2020-03-20 22:06:45 | 2020-03-20 22:00:00 | Pass | Node 3 M1-15, sprinkler mon. Valve in alarm. Upon investigation, found tamper alarm not seated correctly at completion of works on system.Fully opened valve and re seated tamper alarm correctly. Alarm cleared
MSA-DCS | WA3168690 | MDAS monitor fault for transformer RM (TR14) low battery | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Mar 2020 | 2020-03-20 22:11:16 | 2020-03-23 13:30:00 | Fail | Collected parts and attended site. Replaced TR14 battery with new 12vdc 7ah. All replaced and tested ok. Had to gain access to work area as was in construction area. Job complete
MSA-DCS | WA3168691 | Unit 5 SMS Cabinet tamper has been isolated | Casuarina Prison-Prisoner Accommodation Unit 5 | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-23 14:54:00 | Pass | Deisolated input and found tamper in alarm, physically checked reed switch and found centre pin missing.Sourced replacement, replaced reed switch and resistors
MSA-DFES | WA3168635 | Main Dining Room has two rips in vinyl near vending machine | FESA RHQ - Forrestfield | GMP-BR | Flooring | Vinyl (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 13:45:00 | Pass | Patched damaged vinyl area near vending machine
MSA-DFES | WA3168638 | dinning room Zip Hot Water boiler is showing signs of Corroding and has an error message. | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 12:52:00 | Pass | Installed new unit as per quoted NEW MAXIFLOW SCALE FILTER SYSTEM + ZIP ECONOBOIL 5 LITRE BOILING WATER UNIT MF SERIAL 2019101505015
MSA-DFES | WA3168640 | Hallway Bathroom off gym-flexible hose on cold water faulty-see additional notes | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-26 12:50:00 | Fail | Replacing the Flexi hose, changing the grout on the basin vanity
MSA-DTAG | WA3168029 | Ground and 1 Bathrooms and cleaning closet no hot water | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-25 09:30:00 | Fail | Attend to investigate not hot water to male and female toilets on ground floor and first floor, found 80lt Rheem storage electric hwu in plumbing duct behind cleaners cupboard has blown out its tank, resulting in no hot water.Unit cannot be removed from duct as air conditioning ducting is directly in the centre of room and it will be impossible to remove HWU, ducting will need to be removed and electrician to disconnect hardwire before unit can be removed and new one install, will need to liaise with other trades.On return, removed old unit from duct and installed new, reconnected pipe work. Check ok
MSA-DTAG | WA3168559 | ground rear carpark Fence has had a hole cut in it, so people are able to access the building. | Perth Children's Court | GMP-BR-HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 11:45:00 | Pass | Replaced damaged mesh
MSA-DTWD | WA3167857 | C block L1 C108 Sink is leaking from pipes underneath | Leederville Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-20 08:47:00 | Pass | sink pipe said to be leaking but when i arrived on site no leaking taps or waste pipes tightened up wasted pipe just to make sure and let it run for about 5 minutes still not leaking
MSA-DTWD | WA3167977 | A Block, Room A123- Light switch and dimmer broken | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-23 14:28:00 | Pass | Repalced faulty dimmer switch and 2 gang switch plate. Job completed
MSA-DTWD | WA3168287 | M Shed- external tap, stainless steel Sink & basin are broken | Murdoch Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-27 16:00:00 | Fail | installed new stainless steel basin, tap, hose tap
MSA-DTWD | WA3168289 | TUV yard sevice building inhouse rainwater tank overflowing | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 20 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-23 18:30:00 | Fail | re-set floats power cables and lifting chain
MSA-DTWD | WA3168303 | T block T031 and T012 entry door handles broken | Murdoch Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 1 | CLOSE | 20 Mar 2020 | 2020-03-23 17:00:00 | 2020-03-20 12:00:00 | Pass | job completed - replace 2x handle
MSA-DTWD | WA3168324 | A Block, A11 - EWAS system in alarm and beeping and showing Zone 4 in fault.-see notes | Midland Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-04-23 11:00:00 | Fail | Investigated ews fault and found 4 x faulty horn speakers that need replacement. Quote to be sent in to be approved
MSA-DTWD | WA3168459 | Wash Room- Washer pressure is faulty | Perth Campus B6 | GMP-BR | Equipment | Spray Equipment / Waterblasters (EQ) | Falcetta Plumbing and Gas | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-24 19:30:00 | Pass | repaired unit with parts from other unit
MSA-DTWD | WA3168463 | Back of new creche- door fence is faulty | Perth Campus B1 | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 20 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-25 11:00:00 | Pass | Replaced damaged drop-bolt with new Magna Latch
MSA-DTWD | WA3168512 | Q block L1 plantroom the BMS system fault-Please contract NRP | Joondalup McLarty Campus | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-26 10:00:00 | Fail | NRP return to site with IT TAFE 26/03/2020
MSA-DTWD | WA3168522 | 3x fence repairs are rquired along the southern boundary of the Balga Campus. | Balga Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-07-17 14:30:00 | Fail | Cleared boundary fence and carried out fence repairs
MSA-DTWD | WA3168565 | L2 Main doors- Auto doors not opening from inside | Perth Campus B4 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-05-19 12:48:00 | Fail | 1045838 Found door wedged open and not responding. Reset controller and tested. Both sensors working. Checked controller and all wiring. Working ok after reset. Multiple calls to the same fault. Possible intermittent fault with r2000 controller. Recommend power train 301 locking upgrade. Braf being raised19/5 - Removed existing faulty door equipment and replaced with new es200Operator upgrade and new activation/safety sensor. Adjusted and tested operation upon completion and left in good working order.
MSA-DTWD | WA3168606 | BLD 801, Kitchen- Faulty light | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-24 15:00:00 | Pass | Replaced faulty light
MSA-DTWD | WA3168608 | BLD 871 outside- burst water pipe | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-22 09:33:03 | Pass | Dig up and repair burst 40mm PVC water pipe outside Building 871
MSA-DTWD | WA3168664 | A Block - damaged security cable for alarm system | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 20 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-31 15:00:00 | Fail | Complete
MSA-DCS | WA3168746 | casuarina Prison Unit6 Awing water Blubbing up throught he drains | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 21 Mar 2020 | 2020-03-21 11:51:08 | 2020-03-21 11:00:00 | Pass | Attended site and found blockage had cleared, run hose down drains and flushed multiple toilets and all working correctly
MSA-DCS | WA3168751 | Sally port door is faulty.- Security system issue, Seme to attend. | Albany Regional Prison | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-21 22:00:00 | Pass | Contacted site , site had rectified motor fault with WD40 , lubricated contacts and tested door. All working and tested ok. Job complete
MSA-DCS | WA3168779 | Albany Regional Prison- in unit 1 c YArd - cell call system 8, 9, 12 are fault | Albany Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Mar 2020 | 2020-03-22 11:44:52 | 2020-03-27 09:36:00 | Fail | cell calls repaired.
MSA-DCS | WA3168788 | Gatehouse- MDAS system is not working. | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Mar 2020 | 2020-03-21 16:19:48 | 2020-03-21 15:15:00 | Pass | Afterhours callout , travelled to site and located duress system PC. Found network issue on system. Reset PC and network switch. Reloaded programme and retested duress system. All back online and tested ok. Job complete
MSA-DCS | WA3168806 | temper alarm is going off for no reason 1-tU18, near zone 10 | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Mar 2020 | 2020-03-21 19:14:38 | 2020-03-21 18:44:53 | Pass | After hours callout. Attended site and located TU18 in EC cabinet. Reset senstar network and retested fence alarms. All reset and tested ok. Job complete
MSA-DCS | WA3168812 | unit 1 - prisoner cell call will not respond directly to unit 1 | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Mar 2020 | 2020-03-25 17:00:00 | 2020-04-17 08:30:00 | Fail | New network access installed to new network switch.
MSA-DCS | WA3168814 | Kitchen - tap water running constantly | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Mar 2020 | 2020-03-22 17:03:05 | 2020-03-22 10:17:00 | Pass | Service tap in kitchen
MSA-DFES | WA3168800 | AC leaking onto carpet. Located Ground floor outside male and female toilets | CFRS Fremantle-Structure A-Main Building-Ground Floor-Male WC | GMP-BR | Air Conditioning | Ducted Split System (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 21 Mar 2020 | 2020-03-21 18:45:09 | 2020-03-25 21:09:00 | Fail | All ac,s feeding into failed condensate pump are now draining independently of each other. 1x gym drain is still on a pump. Once ceiling dries out completely it will require replacement of small section.
MSA-DCS | WA3168870 | One of the fridge in the kitchen has died out. | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 22 Mar 2020 | 2020-03-22 11:54:17 | 2020-03-23 09:00:00 | Fail | Essential ref. found cool room coil iced up due to faulty fan motor. DE ice coil and replace motor and left operational.
MSA-DCS | WA3168934 | Hakea Prison - Zone 2 - fire alarm keeps activating in the assessment area. | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 22 Mar 2020 | 2020-03-23 14:07:53 | 2020-03-23 14:05:00 | Pass | Hakea PrisonAttended site for alarm in Zn control 2. Zn20 Admin continually activation without cause. Checked area for active detector but could notlocate. Investigated old EP detector but no issue found. Left alarm isolated and will require re attendance with 2 techs for further investigation.23/03/2020GA/MSInvestigated alarm in Admin after tracing out cabling found broken mcp causing alarm. Replaced break glass and left normal
MSA-DCS | WA3168939 | Unit 1 Cell Call E7 has been damaged | Albany Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Mar 2020 | 2020-03-23 14:49:57 | 2020-04-23 08:00:00 | Fail | Job complete
MSA-DCS | WA3168945 | zone 4 the alarm is keep going off | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Mar 2020 | 2020-03-22 19:37:38 | 2020-03-22 18:00:00 | Pass | Rectified and fixed zone 4 cowling microphonics, job completed.
MSA-DCS | WA3168950 | ISU-B Wing OB cells, the CCTV cameras are lagging. | Banksia Hill Detention Centre-Block H Accommodation | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Mar 2020 | 2020-03-22 20:27:03 | 2020-03-22 19:00:00 | Pass | Afterhours callout. Travel to site , reset CCTV PC. PC running slower than usual and possible slower CPU usage due to running 5 x monitors. If issue re occurs then reccomend replacing workstation
MSA-DCS | WA3169041 | Control room - INDIGO CCTV work station 1 not working | Albany Regional Prison | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Mar 2020 | 2020-03-23 13:52:12 | 2020-03-27 09:44:00 | Fail | restart server & tested ok. job complete
MSA-DCS | WA3169106 | Hakea-Melaleuca Prison - automatic gate is not locking up | Melaleuca Prison | GMP-RM | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 23 Mar 2020 | 2020-03-23 10:49:10 | 2020-03-23 11:00:00 | Fail | inspected and tested gate not a lock fault
MSA-DCS | WA3169116 | healtcare pharmacy door not locking | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 23 Mar 2020 | 2020-03-23 11:19:10 | 2020-03-23 10:30:00 | Pass | replaced faulty mortice lock.
MSA-DCS | WA3169119 | gym east water supply valve faulty | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-24 17:50:00 | Pass | Replaced faulty valve at the gym. No water running through that tap. Unable to find isolation valve
MSA-DCS | WA3169125 | Abattoir faulty freezer temperature display | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 23 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-25 11:30:00 | Pass | essential ref. attended.Found temperature sensors faulty, return with new replacement sensor, left system operational
MSA-DCS | WA3169174 | Unit 14, B & D Wing- Power to the switches under the window, kitchen keeps tripping out | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-25 15:00:00 | Pass | Replaced faulty gpos in unit 11 kitchen
MSA-DCS | WA3169185 | Unit 1, Cell D7- Prisoner internal lightswitch housing has come away from wall | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 09:00:00 | Pass | Replaced damaged cell switch in unit 1 d7. Waited access for cell
MSA-DCS | WA3169189 | Unit 7, C Wing, Cell C9- Cell window is faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-04-03 11:00:00 | Fail | RE ADJUSTED/ RE ALIGNED SASH
MSA-DCS | WA3169191 | Unit 7 - A Wing SCU - A6 internal springs broken. Window will not stay open. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-25 11:00:00 | Pass | SASH RE BALANCE COMPLETED
MSA-DCS | WA3169193 | Unit 7, C Wing, Cell C4- cell window is sticking | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-25 14:00:00 | Pass | SPIRAL BALANCES / FEET RENEWED
MSA-DCS | WA3169222 | Unit 1, Control Room- PA is not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-23 14:56:00 | Pass | Tested PA system locally and confirmed operational, Tested PA system in comms room while second technician attempted to use PA in unit office.Swapped inputs around with no difference. Reverted all cabling back to normal. Swapped phones and confirmed operational.Tested suspect faulty phone and found if button "1" is pressed hard enough the pa system activates
MSA-DCS | WA3169232 | Unit 14 - C Wing-Unit 14 cell C02 blocked shower. Requires attention. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 13:13:00 | Pass | Remove grate remove hair, moflo, rinse, plunge, reinstall grate and test
MSA-DCS | WA3169275 | Unit 3, B Wing, Cell B02- personal lock cannot be opened by staff key | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-23 11:00:00 | Pass | Job completed - replace hinges, door plate, and lubricate barrel.
MSA-DCS | WA3169283 | Karakin, A Wing- Smashed window approx 600x450 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-24 13:00:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3169286 | Yeeda C wing Smashed window approx 1600x700 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-24 15:00:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3169559 | Reception, Vent is hanging from ceiling | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-24 11:30:00 | Pass | Attended site and carried out repairs to ceiling vent that had come loose.
MSA-DCS | WA3169564 | Admin building- Mixer tap is not working | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 09:00:28 | 2020-03-23 12:22:00 | Pass | Zip Tap wasn’t working Reset filter and worked fine after
MSA-DCS | WA3169574 | unit 4 cell a3 no hot water | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-27 10:00:00 | Pass | Inspected hot water system and tested water temp. All operating correctly.
MSA-DCS | WA3169624 | Entry Building- Zone 7 outer alarm fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 09:22:24 | 2020-03-25 10:00:00 | Fail | Replaced Zone 7 bottom half of cable with new.
MSA-DCS | WA3169697 | official visits holding cell 1 floor is peeling away | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-04-29 18:00:00 | Fail | repaired vinyl
MSA-DCS | WA3169727 | Hakea-Melaleuca Prison - automatic gate is not locking up | Melaleuca Prison | GMP-RM | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Mar 2020 | 2020-03-23 14:21:18 | 2020-03-23 12:15:00 | Pass | Trace fault and mechanical failure, advice officer on site to refer the problem with other contractors.
MSA-DCS | WA3169818 | external screw has come out of the roof above the HWS-please check all of roof | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-05-15 10:06:00 | Fail | inspected roof, replaced screws.
MSA-DCS | WA3169956 | Unit 1, B Wing entry- Grill door lock is not working correctly | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 12:03:13 | 2020-03-23 15:30:00 | Pass | Attended site checked and found Unit 1 B Wing Grill gate key switch not opening gate correctly. Push to open button in Unit office is working correctly. Further check located the problem to be the key switch on the wall itself. Rectified the problem and tested it all ok.
MSA-DCS | WA3169958 | Hakea-Melaleuca Prison - automatic gate is not locking up | Melaleuca Prison | GMP-RM | Building | Materials (BU) | AFD Contracting | 0 | CLOSE | 23 Mar 2020 | 2020-03-23 16:06:37 | 2020-03-24 01:00:00 | Fail | 23/03/20 - 13:50 to 16:00diagnose fault to automatic gate. Need special diagnostic tool to find fault. All electrical connects are fine but trip switches had activated.Will retrieve diagnostic tool and return.23/03/20 - 20:00pm to 01:00amreplace faulty gate motor and controller
MSA-DCS | WA3169989 | Eyre, A Wing- Drains for wing are blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-26 08:46:00 | Pass | Cleared blockage to drains in Eyre A-block
MSA-DCS | WA3170000 | Upstairs- Window frame is coming away from the glass | Midland (North East Metro) | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-05-20 10:30:00 | Fail | Attended site and made damaged glass sliding window safe.Re-attended site and repaired sliding window, replaced existing glass with safety glass.
MSA-DCS | WA3170001 | laundry No1 dryer not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 12:56:48 | 2020-03-24 08:30:00 | Pass | Reset hilimit and test OK, Check got fan impellor blockage ok, checked duct blockage ok. Left dryer working
MSA-DCS | WA3170004 | Unit 1, Cell D6- Main cell door lock is jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 12:59:38 | 2020-03-23 15:00:00 | Pass | inspected and repaired lock
MSA-DCS | WA3170005 | Front Gate- cashier office- Air Con is not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 13:01:10 | 2020-03-26 15:30:00 | Fail | Txv replaced. Unit fully operational. Supply air 12
MSA-DCS | WA3170092 | Education - Room 1 repair /replace antanna cable in education | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-30 11:30:00 | Fail | Installed new TV point and tested
MSA-DCS | WA3170099 | ODP, Room 1- overhead lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 13:30:00 | Pass | Repaired faulty lights in odp classrooms
MSA-DCS | WA3170106 | Amenities, Taps are leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 13:14:00 | Pass | Remove and replace 1x quarter turn spindle
MSA-DCS | WA3170114 | Back Shed/Office- needs to be sealed up due to Geckos entering building | Warminda Hostel | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-26 11:30:00 | Pass | Attended site and carried out works to back office, sealed up all holes in walls and ceilings so insects can not enter.Cleaned down walls removed insect markings.
MSA-DCS | WA3170117 | Amenities, Gym, male change room- fluro lights flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 08:30:00 | Pass | Repaired multiple faulty lights in gym change rooms and weights area
MSA-DCS | WA3170131 | Unit 4, PTZ Camera 45 is black on the screen | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-04-01 14:30:00 | Fail | Check through recording history and found power outage to camera hardware during this time reported was evident. Reason for the outrage could have been some sort of maintenance on site.
MSA-DCS | WA3170138 | sewerage plant new tanks overflowing | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | WATERCON - DO NOT USE********* | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 14:27:22 | 2020-03-23 16:08:00 | Pass | Watercon employee attended site 23/03/2020 opened valve and lowered water level in tank.
MSA-DCS | WA3170141 | SOG Base- light in corridor is not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 13:30:00 | Pass | Repaired corridor light
MSA-DCS | WA3170143 | SOG Base- back door leading carpark frame is broken | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 11:30:00 | Pass | DOOR & FRAME REPAIRED
MSA-DCS | WA3170160 | Amenities BLOCKED DRAIN OUTSIDE AMENITIES BUILDING | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 13:16:00 | Pass | Use 100mm plunger and 7 rods to clear blockage
MSA-DCS | WA3170192 | perimeter zone 9 outer showing alarms and not alarming | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 15:04:13 | 2020-04-28 15:00:00 | Fail | Replaced cable on upper section of Zone 9. Calibrated and tested.Job complete
MSA-DCS | WA3170223 | Kitchen- bain marie is not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 16:06:28 | 2020-03-24 07:32:00 | Pass | Arrived on site found it was the cold salad bar not the Bain Marie that had failed.
MSA-DCS | WA3170242 | Visits, Number 3, Non-contact booth - lock is not working | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 16:31:08 | 2020-03-24 12:15:00 | Pass | Adjusted door frame locking strike to enable secure locking of door
MSA-DCS | WA3184216 | Chem agent clean up post incident in Lenard and Jasper Units | Banksia Hill Detention Centre | GMP-BR- HO | Cleaning | Cleaning (CL) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 23 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 13:30:00 | Pass | Job Completed - cleaned up glass and pepper spray contamination.
MSA-DFES | WA3169825 | front entry gate-is out of aligment when closing hitting wall, wall has also has become unstable | O'Connor Fleet Storage | GMP-BR | Building | External Walls (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 17:00:00 | 2020-04-02 08:45:00 | Fail | BRAF was presented and we have just received notice that it has been declined.
MSA-DFES | WA3169889 | Area 12, Male toilet will not flush | CFRS Fremantle | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 12:44:00 | Pass | Cleared blockage to male toilet.
MSA-DFES | WA3177739 | Retrospective work order do not attend-NO SIGNS OF FORCED ENTRY OR DAMAGE MONITORING ADVISED | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 17:31:00 | Pass | Guard Attendance 23-03-2020DFES Staff Onsite - No signs of forced entry or damage
MSA-DTAG | WA3169277 | cameras as we have visual to some cameras but some are failing to connect to the server -see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 23 Mar 2020 | 2020-03-23 12:43:25 | 2020-03-23 10:00:00 | Pass | Cameras not connecting to server. Restarted services of Sat Rec 1 as cameras weren't connecting.Once connection to server was completed, cameras came online
MSA-DTWD | WA3169066 | S block L2 Auto Door to S Block passage sounding alarm | Mount Lawley Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 23 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 10:05:00 | Pass | Found that the low battery alarm was sounding, replaced faulty battery, tested all ok.
MSA-DTWD | WA3169069 | C block L1 C110 light not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 23 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-23 15:30:00 | Pass | Attended site and signed in. Located c110. Turned on all lights and found 1 out. Removed cover and replaced tubes. Found not to be the fault. Replaced electronic ballast and reinstated light fitting. Tested all okay. Job complete
MSA-DTWD | WA3169139 | L1 Oxford St entrance removal of graffiti | Leederville Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 23 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-25 13:20:00 | Pass | REMOVAL OF GRAFFITI FROM ENTRANCE OF OXFORD ST
MSA-DTWD | WA3169184 | G block male toilet sink is blocked and drain in floor overflowing | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 16:15:00 | Pass | Unblocked drains
MSA-DTWD | WA3169265 | A block L1 A111 Tap ripping in Female toilet student services | East Perth Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 09:00:00 | Pass | Isolated water supply. Serviced tapware to basin in female toilet area. Turnes on supply. Tested operation and cleaned up area.Note: Hot water temp to basin is 65° and should be regulated to a safe temp.
MSA-DTWD | WA3169534 | canteen gas HWS not working | Rockingham Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-24 14:40:00 | Pass | Replaced thermocouple
MSA-DTWD | WA3169694 | G block workshop emergency gas solinoid for the welding bays not operating | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Gas (PD) | BOC | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 12:00:00 | Pass | Checked over, turned cylinder supply on and checked. Found that theemergency shut off had been activated. Reset system and gas was flowing through to blow pipe. System tested to make sure it was working correctly. Completed paperwork, locked up storage area and left site.
MSA-DTWD | WA3169899 | C block entry and garden shed doors have been broken into need securing | Mount Lawley Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 16:30:00 | Pass | Attend site Locate gardener store room Inspect c block door Rebate has been damaged Board up non active door Spoke with Steve Meyer Replace old mortice lock and square lever set to work with existing barrel Guard needed to protect door being jimmy opened Source parts from Detail door hardware Left site and got parts Return Open door and remove old lockSet new lock and fit Fit handles and test key is working Mark and fit latch guard to door face Clean up
MSA-DTWD | WA3169944 | T Block, T111 & T118 - Air Con is to high- BMS | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 23 Mar 2020 | 2020-03-24 17:00:00 | 2020-03-23 17:00:00 | Pass | Travelled to site, signed in, found Kevin & got a swipe cardChecked rooms T111 & T118 from BMS found both rooms in standby mode operating to a temperature set point of 24.5deg. Found both room temps over 25 with cooling valves partially open.Checked in the rooms and set the controllers to occupied mode” I” button in top RH corner, set point displayed changed to 22.5 deg on both controllers. Checked at BMS & found both units now operating in occupied mode with a set point of 22.5 deg & cooling valve at 100%.Checked programOccupied set point = 22.5Standby set points =20.0 / 24.5Occupied runtime = 120minControl loop dead band =1Control loop PB = 2This means if the set point is 22.5deg (Occupied Mode) the chw Valve will start to open at 23 deg & be fully open at 24deg.The HW Valve will start to open at 22deg & be fully open at 21degIf the set point is 24.5deg (Standby Mode) the chw Valve will start to open at 25 deg & be fully open at 26deg.Left equipment operating as required
MSA-DTWD | WA3170065 | A Block, AF01F near print room- Leak above window | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-25 11:00:00 | Pass | Window seal had come out. Resealed window with silicone.
MSA-DTWD | WA3170072 | A Block, AF201 Cygnet building stairwell area- leaking through window | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 23 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-25 15:00:00 | Pass | Leak identified and area sealed with sealant paint
MSA-DTWD | WA3170144 | A block L2 ladies toilet east ladies toilet continuously running | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-24 15:00:00 | Pass | COMPLETED
MSA-DTWD | WA3170166 | A Block, 1st Floor, AF2.02- Air Con not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 23 Mar 2020 | 2020-03-26 17:00:00 | 2020-07-30 09:05:00 | Fail | Found that the condenser coil has multiple leaks, is heavily corroded and is also currently running on R22 refrigerant (it has been in service since 1999) and is beyond economical repair. Braf to be submitted for replacement of ac4 systemattended site to replace Maritime TAFE AC 4 ReplacementInstall Commair ducted unit, ductwork and repair pipework.tested, all ok.
MSA-DCA | WA3170946 | multiple alarms on the fire panel and faults | PICA-Main Building-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-31 09:15:00 | Fail | 24/03/20:Attended site and found all of loop 1 with short circuit and off line. Traced to water leaking into detector at device 1026 female toilet causing short.Removed device but unable to re fit as water still leaking through even after relocating. Looped our cables to clear open fault but will need to return to fit new detector and base.Parts required 1 x Notifier base and 1 x Notifier type A rate of rise thermal.Left sounder disabled till device replaced.Leave for at least a week to dry out.Also note screen back light has failed and requires replacing as difficult to read display.1 x 2800 Cpu required.Will re-attend on Tues 31/03/20 at 9am to rectify faults as approved by R.Withey31/03/20Returned to site and fitted new detector and base to water damaged area reset and de-isolated and left normal.
MSA-DCA | WA3171657 | Ground - elevator priority switching does not operate, unable to isolate that area are not to used | Perth Concert Hall | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-24 14:05:00 | Pass | Not chargeable. Follow up required
MSA-DCA | WA3171757 | L1 Public ladies toilet; last cubicle-Intermittent leak onto the floor from under toilet bowl | State Library of WA | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-26 15:38:00 | Pass | Removed toilet installed new key seal and pan collar reinstalled toilet
MSA-DCA | WA3172142 | High temperature alarm | Collection and Research Centre Welshpool-Harry Butler Centre-Ground Floor-G.12 - Ultra Freezers | GMP-BR | Refrigeration | Freezers (RE) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 24 Mar 2020 | 2020-03-24 21:59:31 | 2020-03-24 21:30:00 | Pass | Attended call-out. Met with client. Accessed C & R Freezer. No power on controller. Controller front panel broken. Located breaker for freezer control in roof plant room, tripped. Reset but kept tripping after a few seconds. Investigated. Drain Heater in freezer indoor unit faulty. Disconnected and ran unit. Monitored temp dropping to SP. On site tech to replace faulty drain heater in the morning. Left site.Closed job.
MSA-DCS | WA3170819 | Duress alarm is not working in unit 13 and 14. | Casuarina Prison-Prisoner Accommodation Unit 14 | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Mar 2020 | 2020-03-24 11:02:21 | 2020-03-30 11:07:00 | Fail | Sourced parts, attended site, investigated comms fault between gatehouse and field equipment, found another contractor has been upgrading equipment.Contractor completed repairs,Tested OKJob Complete
MSA-DCS | WA3170832 | kitchen salad bar not cooling | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 07:19:04 | 2020-03-24 12:30:00 | Pass | essential ref attended found faulty condenser fan motor , replaced and left system operational
MSA-DCS | WA3170836 | kitchen dough mixer and bread slicer not working | Karnet Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 07:20:55 | 2020-04-24 13:15:00 | Fail | WORK COMPLETED 24/4/20 1.15PM
MSA-DCS | WA3170839 | front gate cashier office outside wall broken tap external | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 07:22:15 | 2020-03-25 00:15:00 | Pass | Replaced hose tap and installed new isolation valve
MSA-DCS | WA3170874 | Unit 3 - A & C-NO HOT WATER IN A/C SHOWERS | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 14:00:00 | Pass | Turn on TMV's
MSA-DCS | WA3170880 | gate control light switch button has sunk in panel. | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-26 14:15:00 | Pass | Disassembled light switch and re-fitted mechanism to plateSecured with super glue. Refitted plate to wall with long screws for future access Test Ran O.K.
MSA-DCS | WA3170882 | Unit 3 - C Wing-C7 SINK BLOCKED AND CAN'T CLEAR IT | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 13:19:00 | Pass | Plunge basin to clear blockage
MSA-DCS | WA3170891 | Unit 5 - B Wing Sink in cell B 7 blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 13:22:00 | Pass | Plunge basin to clear blockage
MSA-DCS | WA3170893 | Unit 5 - B Wing Sink in cell B 7 blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-24 14:00:00 | Pass | Job was raiyas B7 but was C7. Remove trap to clear blockage, reinstall and test
MSA-DCS | WA3170951 | Gascoyne kitchen Urn tap damaged-see notes | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 12:20:00 | Pass | Replace urn tap to kitchen in Gascoyne
MSA-DCS | WA3170958 | laundry No4 washing machine has fault F5 door will not open | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 08:25:08 | 2020-05-11 16:58:00 | Fail | Work Completed as per quote & BRAF
MSA-DCS | WA3170991 | P beam 22 not working | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-04-08 18:22:00 | Fail | Realigned all 5 PE beams in stack, adjusted tamper switch,Replaced resistor for both alarm and tamper relay.Tested alarms and confirmed all cleared
MSA-DCS | WA3170994 | PE beam 14 constant alarm | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-04-09 14:22:00 | Fail | PE beams in constant alarm in the morning.Removed cover and re aligned and address all 5 PE beams in stack 14
MSA-DCS | WA3170999 | kitchen fridge No5 has a broken light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 08:43:32 | 2020-03-24 13:00:00 | Pass | Replaced light and light switch
MSA-DCS | WA3171009 | unit 1 office urn leaking hot water | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 08:55:53 | 2020-03-24 16:15:00 | Pass | WORKS WERE COMPLETED 24.3.2020 ATTENDED AND DIAGNOSED CANNOT BE REPAIRED. WE WERE THEN ISSUED A NEW WO TO REPLACE SO CLOSING THIS OFF AND INVOICING FOR LABOUR AND CALLOUT FOR ATTENDANCE AND DIAGNOSING
MSA-DCS | WA3171010 | cabinet shop compressor faulty | Wooroloo Prison Farm | WSM-BR-SITE | Equipment Hire | Compressors, Generators (EH) | CLEVELAND COMPRESSED AIR SERVICES | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 08:57:39 | 2020-05-22 12:53:00 | Fail | Job complete
MSA-DCS | WA3171021 | SOG outside male change room exit light not working | Hakea Prison | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-26 15:00:00 | Pass | Picked up and replaced exit
MSA-DCS | WA3171033 | Above desk next to W8.104- light is flashing | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-24 14:30:00 | Pass | Repaired lighting on level 8
MSA-DCS | WA3171077 | Unit 1, Cell Call system is not working | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Mar 2020 | 2020-03-24 17:41:57 | 2020-03-24 16:17:00 | Pass | All nodes reset and alarms cleared. All unit cell call staff stations tested as ok.
MSA-DCS | WA3171096 | Lvl 9 - between meeting room 9.1& reception desk - tenancy side - Flashing light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-24 15:30:00 | Pass | Repaired lighting on level 9
MSA-DCS | WA3171566 | Gatehouse - 2 fire alarms activating in unit 2 | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 10:14:37 | 2020-03-25 10:10:00 | Pass | 2 faults on FIP upon arrival. Unit 2 room 29 detector missing causing room 31 to show multi device fault. Replaced 1x XP95 smoke in room 29.Remounted detector as found to be loose. Both faults cleared. System normal at time of departure
MSA-DCS | WA3171581 | Kitchen- Oven 1 seal is broken | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 10:24:44 | 2020-03-24 15:20:00 | Pass | Replace doorseal, adjust & test for leaks with trolley. no leaks.
MSA-DCS | WA3171649 | Kitchen, large hot box door is broken | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 10:30:00 | Pass | Hot box door broken. Remove broken door. Fit new hinges & install door.
MSA-DCS | WA3171655 | ISU, Cell C08- Broken power point | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-25 15:00:00 | Pass | Replaced broken gpo
MSA-DCS | WA3171658 | ISU, Cell A01- Smashed obs window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-30 15:00:00 | Fail | OBS WINDOW REGLAZED
MSA-DCS | WA3171675 | Unit 8, A & B wing lobby door does not catch in lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 11:10:35 | 2020-04-21 14:15:00 | Fail | supplied and installed replacement lock.
MSA-DCS | WA3171720 | Amenities, Male Changeroom- Shower dripping constantly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-25 08:00:00 | Pass | Remove and replace 2x quarter turn spindles in shower
MSA-DCS | WA3171721 | Unit 14 - A & C water drinking fountain leaking causing floor flooding on the dayroom | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 09:25:00 | Pass | CHECKED FOR LEAKS - TESTED RAN AND NO LEAKS PRESENT COULD BE THAT WATER WAS SPLASHING OVER - A40191278L FOUNTAIN
MSA-DCS | WA3171724 | Laundry, PRV leaking behind laundry on main water inlet line | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-25 08:00:00 | Pass | Test RPZD and all is in working order, the unit discharged due to a pressure loss downstream which is what it is designed to do.
MSA-DCS | WA3171729 | Unit 4 - A & C A WING CLEANING CUPBOURD SINK IS BLOCKED. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-25 08:00:00 | Pass | Remove floor polish from great and plunge trough to clear blockage
MSA-DCS | WA3171814 | Unit 2, Cell A5 sink tap pipe is broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 12:22:05 | 2020-03-25 10:57:00 | Pass | Replaced leaking pillar tap and reconnected tap to watwr supply in the duct
MSA-DCS | WA3171818 | Unit 2, A Wing yard, broken sewer pipe 100m plastic | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 12:26:36 | 2020-03-25 12:25:00 | Pass | Cut out broken and reinstalled new drain
MSA-DCS | WA3171822 | Unit 2, Cell B6 - Plug sink waste is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-25 17:00:00 | Pass | Replaced plug waste and waste pipe
MSA-DCS | WA3171826 | Assessments building - water leaking from ceiling | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 12:29:08 | 2020-03-24 17:50:00 | Pass | Attend to investigate leak in ceiling in assessments office, after entering roof void found leak to be coming from air conditioning duct. Have advised call center to assign work order to appropriate trade.
MSA-DCS | WA3171832 | Outside new canteen west - retic solenoid is not shutting off | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-16 09:00:00 | Fail | REPLACED SOLENOID 50ML VALVE
MSA-DCS | WA3171862 | Unit 1 Cell A15 hot tap is leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-08 14:30:00 | Fail | Job appears to have been completed
MSA-DCS | WA3171865 | Unit 2 Cell B14 - leaking sink tap | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-08 15:00:00 | Fail | Job appears to have been completed.
MSA-DCS | WA3171870 | Unit 2 A & B Day room - hot water tap leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-06 12:45:00 | Fail | Replaced spindles and reseated tapware to kitchen sink. Cleaned up and tested.
MSA-DCS | WA3171871 | Unit 2 C & D Day room - hot water tap leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-06 11:30:00 | Fail | Picked up new spindles for leaking kitchen tapware. Replaced spindles and reseated tapware. Cleaned up and tested.
MSA-DCS | WA3171929 | stores Boom gate is broken-- will not open electronically | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-25 08:30:00 | Pass | Inspect Stores entry boom gate. Found to be operational. Found manual release slightly loose causing some slack in the system. Tighten and test operation, all okay.
MSA-DCS | WA3171937 | kitchen office require new lock, handles and lock barrel | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-09 14:05:00 | Fail | Attended site to replace mortice lock and furniture in Kitchen. Will need to return with stock.
MSA-DCS | WA3171940 | Kitchen, Workshop- Large stick blender electrical cord damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 15:15:00 | Pass | Repaired cable and sealed with glued heatshrink .Test ran ok.
MSA-DCS | WA3172033 | Unit 3 - C9-C09 Cell door coming loose off the hinges & lock needs a service . | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-04-16 12:00:00 | Fail | replaced door plate
MSA-DCS | WA3172063 | Unit 4 PRU - PTZ 44 camera is flcikering from black to picture, no inputs | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-04-01 14:50:00 | Fail | Check through recording history and found power outage to camera hardware during this time reported was evident. Reason for the outrage could have been some sort of maintenance on site
MSA-DFES | WA3170795 | outdoor area emergency light has fallen off the wall- see notes | VFRS Mundaring | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 24 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-30 12:15:00 | Pass | Locate faulty light. Replaced faulty tube with new. And fix the light back onto the wall.
MSA-DFES | WA3170804 | outdoor area shade sale bracket broken-see notes | VFRS Mundaring | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 24 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-25 14:30:00 | Pass | New eyebolt in bricks, refit shade sail
MSA-DFES | WA3170865 | nthn end of building near small kitchenette, water leak above desk on right | DFES Regional Office - Belmont | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 24 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-26 07:50:00 | Pass | Investigated leak - found multiple causes - loose screws, anchor points and flashings. Resealed all of them
MSA-DFES | WA3171037 | Applied training ground outside heritage shed - tree needs lopping | FESA RHQ - Forrestfield | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Dom's Total Grounds Maintenance | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 17:00:00 | 2020-04-03 12:00:00 | Fail | BRAF was done and once approved tree loppers attended and lopped tree & removed fallen branches
MSA-DFES | WA3171577 | front gate keeps getting stuck and will not open | DFES Rescue Helicopter Base | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 17:00:00 | 2020-04-01 15:30:00 | Fail | Technician attended the site of Helicopter Rescue Base Main Entry Gate on 24/03/2020. Following full test and inspection of door components identified fault was the loose gate post, motor movement and limit bars loose.Temporarily refixed gate post.Returned on site on 01/04/2020. Removed existing gate post and refixed into correct position. Upon removal of gate post and adjusting of gate leaf, found collapsed wheel bearing on front wheel carriage, replaced both cantilever wheel carriages at time of repair works.Adjusted motor clearances and gate alignment, test operation, all ok.
MSA-DFES | WA3171611 | BAT Building-Door handle has snapped off on BAT Building | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-01 12:00:00 | Fail | Replaced broken door handle with new
MSA-DFES | WA3171635 | ground applied training shed Whirly Bird has come off the rails on the workshop roof | FESA RHQ - Forrestfield | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-26 15:15:00 | Pass | Damaged Whirly bird replaced
MSA-DFES | WA3171791 | Remote pad on the outside of the gate is not operational | CFRS Ellen Brook | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-04-21 15:45:00 | Fail | Technician attended the site of Ellenbrook Fire Station Entry Gate W20759 on 24/03/2020. Following full test and inspection of door components identified fault was the entry keypad not working. Technician established that there was no continuity on cable between motor & keypad, there has been recent landscaping in the area which presumed has caused damage to conduit. Recommended installing a wireless keypad if we can source one compatible with motor, if not we will need to dig up broken conduit, fix and rewire cable. Client has also asked for an antenna to be mounted to boost receiver signal.26/03/2020. Restored power and tested operations of gate. Noted remotes functioning ok. Inspected further and found pes requiring alignment. Also noted covers damaged from bore water. Polished covers and re aligned PEs. Noted PEs are ok however recommended to fit new units as beam strength is weak. Tested gate operations all ok. Inspected keypads and noted outside unit stopped operating at one
MSA-DFES | WA3171938 | East exit door of the Admin building is coming off the hinges | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 24 Mar 2020 | 2020-03-24 17:29:07 | 2020-03-24 15:15:00 | Pass | Fixings pulling through aluminium and coming loose. Remove old fixings and installed new.
MSA-DFES | WA3172111 | Kitchen - Filter for under bench hot and cold-water system requires replacing | CFRS Belmont | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-26 15:00:00 | Pass | ATTENDED A40190379M ZIP HYDROTAP RESET COUNTER TESTED OK
MSA-DFES | WA3172121 | Engine Room (area 12)- Roller door remote for 1st LT roller door | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-20 12:00:00 | Fail | Technician attended site of Welshpool Fire Station, Engine Room (area 12) - Roller door A40352192F on 27/03/2020. Identified that remotes intermittent/ faulty. Not compatible with the new remotes. Unable to be coded into existing receivers. Front and rear doors and interlinked and operate off the same button. Recommended new 4 channel receiver with air keys remotes.Technician returned on site on 20/04/2020. Supplied and installed new receiver for new remotes. Supplied and coded 6 new remotes. Carried out full test of operation ok.
MSA-DFES | WA3172127 | Station Watchroom (Area 8)- self closing hinge U/S, leaks & does not operate effectively | CFRS Welshpool | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-26 12:00:00 | Pass | Replaced old door closer with new
MSA-DFES | WA3173485 | retrospective work order donot attend-site check | CFRS Midland | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-24 21:02:00 | Pass | Guard Attendance 16:14 - 16:26
MSA-DFES | WA3173489 | Retrospective work order do not attend-No cause found | DFES Regional Office - Belmont | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-24 16:26:00 | Pass | Guard Attendance 24/03/2020
MSA-DTAG | WA3170962 | L1 plumbing duct Disconnect old HWU & re-connect new HWU - see notes | Perth Children's Court | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-25 11:30:00 | Pass | HWU not on rcd so recommend to put it on one to prevent further damage to hwu in future
MSA-DTAG | WA3170984 | L1 plumbing duct Remove exhaust fan ducting to allow access for new HWU -see notes | Perth Children's Court | BUG-MW | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-25 11:00:00 | Pass | Works completed.
MSA-DTAG | WA3170996 | Replace buzzer box for the keyless doors as one of the buttons has gone through the box is broken | Rockingham Justice Complex | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-24 12:45:00 | Pass | Sourced part and travel to site to replace the damaged intercom. Tested it ok after replacement.
MSA-DTAG | WA3171088 | Lvl 5, Sherriff’s Office- Kitchen sink drain emanating a bad smell | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-03 12:16:00 | Fail | Complete
MSA-DTWD | WA3170828 | T block cafateria freezer temp is remaining warm not cooling | Murdoch Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 0 | CLOSE | 24 Mar 2020 | 2020-03-24 11:16:16 | 2020-04-17 17:30:00 | Fail | Defrosted freezer room Evap coil and reprogrammed controls. Monitoring for week.Replaced defrost pan heater as per BRAF
MSA-DTWD | WA3171013 | Canteen managers office door key is jammed | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 1 | CLOSE | 24 Mar 2020 | 2020-03-25 17:00:00 | 2020-03-25 11:10:00 | Pass | Repaired damaged lock
MSA-DTWD | WA3171089 | B block cleaners room lock faulty | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-27 15:30:00 | Pass | replaced lock
MSA-DTWD | WA3171589 | BLD 833 Homestead,cooler room- Led fluro light | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-24 16:00:00 | Pass | Replaced LED tubes
MSA-DTWD | WA3171761 | Conference room BLD 832- 2x power points faulty | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-24 16:00:00 | Pass | Replaced faulty power points
MSA-DTWD | WA3171811 | N Shed, Controller working intermittently unable to program | Murdoch Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 12:00:00 | Pass | Attended site to investigate the irrigation controller, determined the fault was in the field wiring.Returned the following day with locator, located and repair bad cable joins and replaced two faulty decoders.
MSA-DTWD | WA3171838 | E block lights at high level E100-Multiple (20+) fluoros out-see notes | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-24 07:28:00 | Fail | Repalced multiple fluros out throughout E100 using scissor lift.job completed
MSA-DTWD | WA3171961 | D Block, Classroom D31, Reverse cycle split A/C not operating | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-25 15:40:00 | Pass | Arrived you site, signed in checked in with Denis.Gathered tools and equipment started fault check on unit, put unit through full reset, put into test mode all ok, apparently build a had power issue over weekend. May have caused fault. Cleaned up and completed paperwork and signed out.
MSA-DTWD | WA3172043 | H Block, H20 female toilet, cistern constantly running | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-31 16:23:00 | Fail | Replace cistern
MSA-MRWA | WA3171872 | Kitchens x 3- Broken wall mounted paper towel holders in 3 kitchens require replacement. | Heavy Vehicle Services | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 3 | COMP | 24 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-27 10:33:00 | Pass | Lids missing to older dispensers may have to look at installing newer models
MSA-MRWA | WA3171883 | Office- Flickering Fluro lights throughut the building | Heavy Vehicle Services | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | COMP | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-27 10:25:00 | Pass | Replaced roughly 40 globes through hvs site
MSA-MRWA | WA3172083 | Front Auto Gate- Intercom signal not activating administration phone. | Materials Engineering Branch | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 24 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-27 11:00:00 | Pass | 27/3/20 - Dylan Parslow, Joshua ParkInvestigated issues with intercom.Intercoms dialing out.Fault appears with phone system, recommend phone contractors look at the issue.
MSA-DCA | WA3172368 | return air in fault no air con | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 25 Mar 2020 | 2020-03-25 11:47:32 | 2020-03-25 10:00:00 | Pass | Attended call-out. Investigated active alarms. AC 9 RAF VSD faulted on Over Current alarm. Reset and monitored. AC 3 SAF, RAF, Fire Alarm, all active. AC 3 graphical not loading. Carried out cold restart of controller @130. Monitored operation during rebooting. All alarms cleared. All mechanical equipment operating.Closed job.
MSA-DCA | WA3172410 | west office air con unit in fault error message low on gas | Subiaco Arts Centre-Main Building-Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-05-14 14:30:00 | Fail | Arrived onsite. Found AC G.1 displaying abnormal indoor pipe temperature fault code. Reset fault and checked system operation. Found system to be short on refrigerant. Also found compressor is losing its compression and not cooling effectively. Also found faulty indoor coil pipe sensor. Will submit information for repairs. Due to age of unit parts may no longer be available.
MSA-DCA | WA3173694 | Lift 5 out of order | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-25 15:41:00 | Pass | Found lift stuck at ground floor,found JFIS main breaker on controller in machine room tripped,errors mains powerinterrupted,switched JFIS , relearnt lift ,tested and returned lift back into service.
MSA-DCS | WA3172325 | Perimetre fence Zone 15 - No camera working - Perimetre keeps activating | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Mar 2020 | 2020-03-25 10:54:43 | 2020-03-25 12:00:00 | Fail | Attended site checked and found Zone 15 Cowling activating intermittently. Checked in EC cabinet found ambient noise is high. Recalibrate sensor and reboot controller and tested it ok. Camera will be fixed under open job.
MSA-DCS | WA3172339 | unit 11 none of the cells have power but the switchboard is on | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 07:13:21 | 2020-03-25 10:30:00 | Pass | Investigated power issues in unit 11. Found BMS system not turning relays on. Manually overrode controls. SEME to rectify
MSA-DCS | WA3172340 | unit 6 back of major water leak under road and concrete | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 25 Mar 2020 | 2020-03-25 11:18:19 | 2020-03-25 09:35:00 | Pass | Inspected leak at u6. Leak on retic pipe. Management advised. Dug up to find the cause of the leak. No pipe found.
MSA-DCS | WA3172358 | perimiter mw zone 3 constant alarm - SEME on site | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-25 15:19:00 | Pass | Microwave set zone 3 found with allignment out, returned allignment to 1.7 and tested operating correctly, monitored with no further activations.
MSA-DCS | WA3172360 | control room duress system no response | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-20 15:20:00 | Fail | Rectified faulty duress point after locating, system no longer alarming and operating correctly.
MSA-DCS | WA3172395 | zone 11 MW zone 2 inner fence both constant alarm- SEME on site | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 08:10:01 | 2020-04-06 14:00:00 | Fail | Attended site and replaced zone 11 microwave with new Ultrawave set. Seme stock used. All programmed, replaced and tested ok job complete
MSA-DCS | WA3172432 | Education - Storeroom lock will not open | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 08:50:57 | 2020-03-25 11:30:00 | Pass | education storeroom replaced handle
MSA-DCS | WA3172565 | Kitchen - Bar Mixer (Robo Coup) is not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-04-03 12:00:00 | Fail | Kitchen Robo Coupe Stick Mixer faulty. Check mixer, replace faulty circuit boards, bad shaft & blade. Test & return to site.
MSA-DCS | WA3172726 | Gym, Stage light will not light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-08-04 13:30:00 | Fail | Replaced damaged gym stage lights.
MSA-DCS | WA3172916 | Unit 3, Cell A8 & A9- toilet space is leaking sewerage water from either above or below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-25 10:00:00 | Pass | Replace pan collar
MSA-DCS | WA3173242 | Kitchen- Stick blender wont turn cutting disk | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-04-03 10:30:00 | Fail | Robo Coupe Kitchen Stick mixer faulty. Remove unit for repairs. Dismantle, replace faulty cutter lead & tube. Assemble & test.
MSA-DCS | WA3173281 | unit 11 none of the cells have power but the switchboard is on | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 10:02:37 | 2020-03-25 14:30:00 | Pass | Attended site checked and found Unit 11 most of the power have been recovered after electrician checked the power issue. But the CMS Kiosk in A, B Wings area still not working. Further check located the problem to be the UPS problem. Rectified the problem and get CMS Kiosk back online.
MSA-DCS | WA3173385 | Staff room, light with loud buzzing sound (suspect ballast) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-30 14:00:00 | Pass | Repaired light.
MSA-DCS | WA3173393 | S O P - Lunch Room prisoners day room lock is losse and soon to fall off. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-03 13:00:00 | Fail | Replaced handles, modify/enlarge door plate handle holes.
MSA-DCS | WA3173413 | Rear staff entry door, security door not latching closed - photo to follow in email | Mandurah | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-27 09:30:00 | Pass | Door closer adjusted
MSA-DCS | WA3173436 | CCU, Cell 2- toilet is not flushing & possible blockage | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 12:10:00 | Pass | Flushing mechanism broken repaired
MSA-DCS | WA3173437 | CCU, Cell 3- no hot water | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 13:15:00 | Pass | Adjusted temp valve to correct temperature
MSA-DCS | WA3173480 | Unit 4- Cell B12- main cell window & door window are broken | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 11:24:40 | 2020-03-26 14:00:00 | Fail | MAIN WINDOW/ OBS WINDOW REGLAZED
MSA-DCS | WA3173501 | Turner, B Wing- 2x smashed top door window approx 1450x600 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-30 09:30:00 | Pass | DOOR WINDOW REGLAZED
MSA-DCS | WA3173502 | Turner, B Wing- 2x smashed Sash window approx 1450x450 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 11:00:00 | Pass | windows reglazed
MSA-DCS | WA3173516 | Reception Automatic Entrance Door - Remote Controls not working | Rockingham Justice Complex | SPA-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-04-23 19:00:00 | Fail | Technician attended the site of Rockingham Justice Complex Reception Automatic Entrance Door on 30/03/2020. Following full test and inspection of door components identified that the receiver was faulty, remotes not activating door. Removed faulty receiver and wired in new receiver. Supplied and coded 2 new remotes to suit new receiver. Carried out full test of operation ok.Technicians returned on site on 23/03/2020 and completed the following quoted works:" Please note: New Modernisation Upgrade Kit will be installed internally of the existing automatic door operator eliminating the need for entrance alterations"Removal of existing worn/faulty components."Supply and installation of new MUK Kit- Locking (Modernisation Upgrade Kit)."Supply and installation of 2 of IXIO DT1 safety sensors"Supply and installation of 2 x new trackwheel assembly"Supply and installation of 1 x floor guide"Supply and installation of 1mtr floor guide channel"Supply and installation of 1 x d
MSA-DCS | WA3173558 | Level 3, Light flashing on tap - may need filter changed | East Perth | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-27 13:48:00 | Pass | DIAGNOSED REPLACED ZIP FILTER
MSA-DCS | WA3173574 | New Cateen west- broken light switch & GPO | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 12:42:07 | 2020-05-04 15:00:00 | Fail | Repaired lights and power
MSA-DCS | WA3173609 | Unit 2 Office lights are faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-30 10:00:00 | Pass | Repaired light fitting
MSA-DCS | WA3173646 | gate house PC is not starting going into restart loop | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 13:30:49 | 2020-03-25 16:00:00 | Pass | Provided remote phone support to resolve multiple computer and communication faults after power surge. Restored ethernet network and workstations. Restored Workstation and perimeter detection. Tested OKJob Complete
MSA-DCS | WA3173653 | Stores The External Stores roller door wont go down. | Casuarina Prison | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 09:30:00 | Pass | Replaced safety beams
MSA-DCS | WA3173654 | Gym, South Entrance- smashed window 600x600 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 09:00:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3173658 | Paint shop- Vinyl floor is lifting (OSH issue) | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-04-28 11:00:00 | Fail | repaired vinyl
MSA-DCS | WA3173775 | Keywatcher doors are not catching to lock | Melaleuca Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 14:19:24 | 2020-03-25 15:45:00 | Pass | Checked and found Keywatcher on the right hand side need to be pushed hard to latching the lock. Rectified the lock alignment problem and tested it all ok.
MSA-DCS | WA3173838 | Entry camera, PTZ laminate is damaged | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 15:08:02 | 2020-03-25 15:31:00 | Pass | Replaced PTZ laminate in entry ptz due to lack of vision via cherry picker
MSA-DCS | WA3173841 | Entry Control- multiple duress transmitters require assist | Bandyup Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 15:09:55 | 2020-04-03 12:15:00 | Fail | Replaced 13 batteries to transmitters, reset alarms and tested operational, checked devices causing trnsmit failures operating correctly, system restored.
MSA-DCS | WA3173927 | Unit 3 Control room - cell call control panel - showing transit failure node 79 error | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Mar 2020 | 2020-03-26 00:00:16 | 2020-03-26 16:30:00 | Fail | Rectified and fixed cell call fault at Unit 3, job completed.
MSA-DCS | WA3173946 | Fire alarm- message error "common fault" | Boronia Pre-release | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 25 Mar 2020 | 2020-03-25 20:53:19 | 2020-03-25 20:08:00 | Pass | Attended site for a common fault. Once onsite I inspected FIP and no faults were present. I went through fault history and a detector on panel7 detector 126 had been in common fault but was now clear. Further investigation required by electrician as possible wiring fault25/3/20 KSAttended site and found panel normal checked history and found to be strobe unit on workshop in fault. Checked relay module and foundloose connection on loop input to module. Re terminated and left normal.Note spare modules on site if returns into fault, will need to be brought from workshop.
MSA-DFES | WA3173455 | engine room door No 3 rear roller door coming down in 8 secs should be 2 mins | CFRS Malaga | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | COMPFIN | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-26 15:30:00 | Pass | Technician attended the site of Malaga Fire Station Engine Room Roller Shutter on 25/03/2020. Found door would intermittently close after eight seconds on one cycle and not close on another cycle then close after three minutes on another cycle. An electrician to re-attend and investigate issue & sort problem.Technician returned on site on 26/03/2020. Noted door operations and found door automatically closing in eight seconds, and door stopping intermittently when reversed. Suspect PLC unit faulty or program is corrupted. Requires existing unit inspected by programmer on laptop in operation or new PLC program and fitted. Left door in working conditions.
MSA-DFES | WA3173550 | hallway - Water leaking from roof. Running down wall | DFES Regional Office - Belmont | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-06-09 15:30:00 | Fail | Works are now completed - Please see photos attached
MSA-DFES | WA3173554 | Ground Level - mens toilet not working - U/S | DFES Rescue Helicopter Base | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 16:24:00 | Pass | Replacing the toilet cistern
MSA-DFES | WA3173911 | 2nd second floor- Zip water unit is not working, no water | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-26 12:54:00 | Pass | No water on arrival. Checked filter and ran manual tests. Pumps and filter ok. Put emulator on system and it’s the tap head that is faulty. Will ring zip for a warranty call out
MSA-DTAG | WA3173234 | 1987, Lvl 4- Plant RoomA/C control board has failed to activate | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-25 10:00:00 | Pass | Attend site. Investigate AC 1,2,3 not running. Check for unit faults and found no active faults. Check fire relays and found to be energized. Check time schedule and found to be set correctly. Carry out power cycle on controller in plantroom and found once back online the units started. Found controller to have been offline. Check operation of units and found to be working as normal.
MSA-DTAG | WA3173483 | Bio-clean required to counter areas 2, 3 & 4 –see notes below | Central Law Courts | WSM-BR-SITE | Cleaning | Cleaning (CL) | OCS SERVICES PTY LTD | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 21:00:00 | Pass | job completed - Bio-clean required to counter areas 2 3 Et 4
MSA-DTAG | WA3173833 | Court 3 is extremely. No air flow at all. Feels like hot air is coming out | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 15:30:00 | Pass | Works completed.
MSA-DTAG | WA3173901 | Persons in all custody cells have been ill with flu like symptoms. | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Cleaning (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 21:00:00 | Pass | Work completed 26/03/2019 9 p.m. Cost of labour @ $100/hour including call out up to 5 hours for COVID/flu like symptoms
MSA-DTWD | WA3172453 | Block 3 metal fab welder in welding bay No12 not working | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-25 11:00:00 | Pass | Attended site and signed in. Located block 3 workshop. Found bay 12 welding outlet faulty. Investigated to no power from switchboard. Fuse blown. Replaced fuse with site supplied. Retested welder. All okay. Job complete
MSA-DTWD | WA3172516 | E Block E30 Kitchen Leaking spout | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 11:45:00 | Pass | Replaced spout and taps
MSA-DTWD | WA3172686 | C block fire panel fault recording on the system | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-05-19 10:50:00 | Fail | C block fire panel fault recording on the systemLocation:South Metro TAFE-Mandurah Campus (formerly Peel)Address 1:Education Drive GREENFIELDSAttended, further work required.Found sensor that’s not acceptable in power mains C block. Sensor is extremely high and near impossible to reach without further access or remove roof panels. We need to remount this sensor so access and maintenance can occur. This is the only sensor that we can’t see the fault light. As it’s facing up. TECHNICIANS ON SITE 29/05/2020FAULT FINDING DISCOVERED THAT THE FAULT WAS A RESULT OF TAMPERING: SENSOR HAD BEEN BEEPING AND SOMEONE HAD ATTEMPTED TO STOP IT AND OPENED THE UNIT. AS A RESULT THE ALARM WAS SET OFF.TECHNICIANS THEN INSTALLED NEW SENSOR-FAULT RESOLVEDCLEANED ALL SENSORS IN F BLOCK, RESET THE PANELRESET MAIN PANEL- ALL WORKING WELLALL COMPLETEDSafety is critical in gaining access due to the heightHeight problem as the cabinet does not give safe access. Panel fault iso
MSA-DTWD | WA3172867 | G block GG20 air con noisy unit | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-27 10:00:00 | Pass | Arrived on site signed in and checked in with Sharyn. Gained access keys gathered tools and equipmen. Checked ahu in plantroom, found belt loose belt in ok condition, readjust belt assembly tested all ok. Cleaned up work area, completed paperwork and signed out.
MSA-DTWD | WA3173060 | C Block, Room C101 - damaged paving around downpipe outside C101 entry | East Perth Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-09 09:20:00 | Fail | reinstalled pavers around downpipe outside room.
MSA-DTWD | WA3173140 | External lawn (between B & J blocks)- broken water pipe | Midland Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-28 12:30:00 | Fail | Repaired burst on main water line.
MSA-DTWD | WA3173156 | E block E201 replace lights not working | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-26 10:19:00 | Pass | Attended site. Signed in. Replaced faulty fluro and control gear to lights in classroom .tested all working properly .Job completed
MSA-DTWD | WA3173231 | I Block, Room I005.1- Toilet exhaus fan is faulty | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 07:38:00 | Pass | Replaced faulty exhaust fan and cabling in I5.001 job completed
MSA-DTWD | WA3173236 | A Block, Room A338- Damaged ceiling tiles | East Perth Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 25 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-27 15:00:00 | Pass | Arrived at site, inspected tiles to be replaced. Picked up materials, returned to site. Removed and replaced x15 ceiling tiles. Tidy area, vacuumed and packed away ladder. Disposed of old tiles at yard.
MSA-DTWD | WA3173374 | A Block, Open Office- replace fluro lights in a light fitting | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 09:40:00 | Pass | Attened site. Signed in. Replaced faulty fluro and ballast to light in A block open office and removed 1x tube from seperate light as it was too bright . Job completed
MSA-DTWD | WA3173555 | alarm system is not going into alarm when the code is entered into the keypad | Rockingham Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 08:00:00 | Pass | Attend site to investigate fault on not being able to arm and disarm F Block. Programmed F Block card holder for Dennis, tested, all working ok
MSA-DTWD | WA3173632 | U block U008 evap air con making a noise | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-06-29 16:00:00 | Fail | Arrived onsite. Gained access to evaporative cooler serving U008. Found fan bearing had failed. Found fan shaft to be worn from collapse and heavily corroded. Recommend replacing fan deck ( bearings, fan shaft, fan barrell, fan housing ). Will submit information for repair and information for replacement of evaporative cooler as discussed with Darren. 25.6.20. (8am - 4pm): Having connection issues with promap. Unable to login. Returned to site with parts. Gained access to Evaporative cooler serving U008. Locked out power supply. Disassembled fan assembly and commenced replacing components. Need to return to site to complete.
MSA-DTWD | WA3173639 | block E ground Cafe air conditioning not working | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 17:00:00 | Pass | Attended site, completed safety questions , setup exclusion zone from ladder, tied off ladder, accessed roof and unit, found solenoid not opening correctly , changed solenoid , running well after full test
MSA-DTWD | WA3173695 | Corridor leading between B & C Block -Room BG15 door has jammed shut due to faulty lock | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-25 15:20:00 | Pass | Room BG15 - Door lock jammed.Door opened and Lock replaced
MSA-DTWD | WA3173904 | L Block, upholstery workshop- One light circuit not working | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 14:45:00 | Pass | Attend site . Signed in. Inspected row of lights not working . Found cable to be cut , ran new feed between lights. Replaced faulty fluro lamps as well. Tested lights all working properly . Job completed
MSA-DTWD | WA3173905 | G Block, Room G16B exterior- wooden external door damaged | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-27 14:30:00 | Pass | Door out of square. Refixed door bracing and squared off. Door now square and operational
MSA-MRWA | WA3172346 | all lifts at the DAC have multiple faults | Don Aitken Centre MRWA Head Office | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 25 Mar 2020 | 2020-03-25 11:24:32 | 2020-03-25 10:13:00 | Pass | OWO Report - Completed but not chargeable
MSA-MRWA | WA3172964 | L8 Hallway – Flickering light please remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 10:17:00 | Pass | Replaced flashing light with a new one
MSA-MRWA | WA3173370 | L7 Male toilet urinal not flushing, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Mar 2020 | 2020-03-26 17:00:00 | 2020-03-25 12:23:00 | Pass | Cleared blocked urinal in level 7 LHS toilets.
MSA-MRWA | WA3173915 | L2, Room 237- LED panel not working please replace | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 25 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-26 11:47:00 | Pass | Attended site. Signed in. Replaced faulty electronic ballast to light on lvl 2 rm 237 as shown by site. Used parts supplied by site. Tested light all working properly .job completed
MSA-DCA | WA3174391 | shower taps are seized | Perth Concert Hall-Main Building-Ground Floor-Women's Toilet - Entry Foyer | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-27 09:00:00 | Pass | Replaced badly seized shower taps
MSA-DCS | WA3174204 | Unit 14 cell D04 shower blocked. Requires attention. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-27 10:30:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3174224 | CCU monitor 3 not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 08:10:30 | 2020-03-26 12:00:00 | Pass | Attended site checked and found CCU Monitors 3&4 not showing cameras correctly. Located the problem to be the EBI workstation display problem. Rectified the problem and check both monitors showing correctly.
MSA-DCS | WA3174226 | unit 9 cell B7 inspection window cracked | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-01 09:30:00 | Fail | replaced obs window
MSA-DCS | WA3174244 | Vegetable Preparation-replace cryvac 20 amp 3 phase plug/faulty/vegie prep | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-27 09:30:00 | Pass | Attended cool room, found faulty 3phase plug and socket, picked up parts and replaced and tested
MSA-DCS | WA3174256 | Unit 5, control - All call system down to the cells are not working | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 08:29:37 | 2020-03-26 11:15:00 | Pass | All Call for all Houses at unit 5 , reset the intercom handset and tested working. Job completed
MSA-DCS | WA3174257 | unit 2 D14 vinyl damaged | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-11-13 11:30:00 | Fail | NEW VINYL FLOOR LAID
MSA-DCS | WA3174259 | cleaning ws office air con not cooling | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 08:32:48 | 2020-04-20 10:30:00 | Fail | Arrived on site and signed in tools, isolated power and removed faulty fan motor and pcboard, fit new parts,turn on and tested all running ok at present.
MSA-DCS | WA3174269 | Reception area - Female toilet blocked | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 08:38:07 | 2020-03-26 15:30:00 | Pass | Cleared blockages to single wc pan. Adjusted flush mechanism. Tested operation.
MSA-DCS | WA3174273 | Urquart D wing kitchen-smashed window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 11:30:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3174274 | Admin air unit has faulty light on | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 09:00:00 | Pass | Arrived on site and signed in tools,checked over aircond found no fault present,check amp draws and pressures all ok, checked operation of duct heaters all working,checked cables no sign of wear.
MSA-DCS | WA3174279 | Psychology-Air con unit has fault light on & constant issues with power tripping | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 10:30:00 | Pass | Checked over aircond found unit running, breaker not tripped,isolated power checked all components and wiring,all ok,after speaking with electrician found that breakers have shunt trips on them for fire alarms, which could be causing breaker to trip.
MSA-DCS | WA3174281 | replace broken sleepers over road for rectic channel | Casuarina Prison | GMP-BR- HO | Paving & Roadworks | Paving (PR) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-02 14:30:00 | Fail | broken sleepers replaced
MSA-DCS | WA3174369 | Gate House -Require cctv footage from west sally port from 25/3/2020 0630-0740 hrs | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-26 16:03:00 | Pass | Downloaded dat as per security
MSA-DCS | WA3174371 | Unit 13 - Front Entrance-Patio lights outside of Unit not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-09-07 15:00:00 | Fail | Repaired and replaced various wall and bollard lights in unit 13 and 14 walkways.
MSA-DCS | WA3174373 | Lvl 1 - desk W1.83- Flickering light above desk | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 15:45:00 | Pass | Replaced failed lamps and starters
MSA-DCS | WA3174379 | B wing, cleaning store - Fluro light has come away form the ceiling and wiring is exposed | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-07 15:30:00 | Fail | Attended unit 1. Isolated damaged light, waited for pest technician to attend. Returned and replaced store light
MSA-DCS | WA3174434 | Staff Room- security grill lock isnt working | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 26 Mar 2020 | 2020-03-26 15:11:41 | 2020-03-26 13:05:00 | Pass | Grill Gate Lock on Staff Room - not working made new screw fixings and realigned
MSA-DCS | WA3174452 | Abattoir broken 3 phase cable | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-30 11:00:00 | Pass | Investigate and repair broken three phase cable in abattoir.
MSA-DCS | WA3174456 | Dairy packing machine 1 - faulty no power | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-30 13:00:00 | Pass | Investigate and repair fault on dairy packing machine 1
MSA-DCS | WA3174463 | ladies staff toilet, tap is shooting out water when it is turned on | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-27 11:00:00 | Pass | Complete
MSA-DCS | WA3174495 | Unit 6, B & D, Cell D1- Toilet cistern has fallen off the wall & leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-27 09:30:00 | Pass | Pickup parts, remove and replace broken cistern in plumbing duct
MSA-DCS | WA3174504 | unit 6 back of major water leak under road and concrete | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Pumps n Pipes | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 12:04:00 | 2020-04-01 14:00:00 | Fail | work excavcated on site today and finished and area made safe. WO completed
MSA-DCS | WA3174546 | Amenities, Backyard- Broken isolation water valves | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-05-05 09:00:00 | Fail | Dig up valves, remove and replace valves, backfill and reinstall access covers, cleanup.
MSA-DCS | WA3174567 | maintenance workshop ,construction store GPO damaged | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-03 15:00:00 | Fail | Picked up replacement parts. Re-installed damaged gpo in maintenance store.
MSA-DCS | WA3174571 | CCU cell 3 drains in the sink is blocked and flooding the cell | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 12:51:59 | 2020-03-27 10:40:00 | Pass | Cleared blocked drain.Had to use all drain rods and CCTV drain .All clear.
MSA-DCS | WA3174635 | kitchen potwash taps broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-27 12:00:00 | Pass | Replaced damaged orings and grub screw in vegi sprayer. Leak repaired.
MSA-DCS | WA3174636 | Mechanical W/S- Air Con not working | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-15 14:58:00 | Fail | System reached set point with out issue
MSA-DCS | WA3174638 | Kitchen - Brat pan tap is leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-05-14 10:30:00 | Fail | 27-3-20. Vegi sprayer needs replacing. Braf required. Hose is brittle, has holes in it and has been previously bandaid fixed. Stainless components bent and grub screw missing.
MSA-DCS | WA3174644 | Rear accommodation Kitchen- Air Con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 13:51:31 | 2020-04-14 14:35:00 | Fail | Further works required. BRA declined.
MSA-DCS | WA3174658 | INF (10) - HC1 Toilet in cell HC1 keeps running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-27 11:30:00 | Pass | Adjust cistern Inlet valve in plumbing duct
MSA-DCS | WA3174659 | Assessments building - water leaking from ceiling | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 14:12:33 | 2020-04-02 16:07:00 | Fail | Drain is now free flowing.
MSA-DCS | WA3174667 | Unir 10 B5 Floor waste blocked and floor flooding | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 14:18:57 | 2020-03-26 15:55:00 | Pass | Cleared blockage to FWG in cell
MSA-DCS | WA3174682 | Self Care, Unit 3- kitchen, tap is stuck open | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 14:38:59 | 2020-03-27 09:00:00 | Pass | Replaced damaged mixer tap with new one in kitchen.
MSA-DCS | WA3174724 | Lvl 8, Small kitchen TP8.1- Boiling water on filter tap is intermittenly producing boiling water. | Westralia Square | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-27 12:00:00 | Pass | Job to be resent to “water2water”
MSA-DCS | WA3174738 | Multiple PE Beam issues (22,14,13,11) | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 15:25:15 | 2020-04-08 18:23:00 | Fail | Zone 13 and 14 intermittently alarming, tested each PE beam in those stacks and, unable to align 3 PE beams, Removed anything in line of site.Replaced 3x Takex PE beams1x Seme stock used for 2nd PE beam in stack 132x Site stock used for 1st and 5th PE beam in stack 14All other zones working correctly
MSA-DCS | WA3174805 | U13 - Various damages please investigate and repair | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 26 Mar 2020 | 2020-03-27 03:12:19 | 2020-03-27 14:22:00 | Fail | Made safe vandalised basins and toilets in unit 3 D cells Had to leave site to allow forensics.Returned in the afternoon and finished investigation.Works to be completed on another work order under Midolo.
MSA-DCS | WA3174806 | U13 - Various damages please investigate and repair | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 23:25:33 | 2020-03-27 16:00:00 | Pass | Repaired & replaced multiple faulty lights in u3 after incident
MSA-DCS | WA3175552 | Lvl 8, Small kitchen TP8.1- Boiling water on filter tap is intermittenly producing boiling water. | Westralia Square | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-31 16:28:00 | Pass | Replaced tap heads and tap loom. Also replaced tap base seal and spider nut and fittings which are faulty. Very difficult to get to. Working fine now, normal operation
MSA-DCS | WA3185399 | Riot damage to plumbing to Units 2, 3 and 4 | Hakea Prison | GMP-BR-RC | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-20 11:27:00 | Fail | installed new basins and taps, adjusted pipework cells B6, D3 and D12. Claim Number:20/13004
MSA-DCS | WA3185404 | Riot damage to Electrics to Units 2, 3 and 4 | Hakea Prison | GMP-BR-RC | Electrical | General Electrical (EL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-17 13:17:00 | Fail | repaired all damaged electrical items. Ref # 20/13004
MSA-DCS | WA3185405 | Riot damage to Roof of Units 2, 3 and 4 | Hakea Prison | GMP-BR-RC | Roofing | Tiled Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-08-10 10:03:00 | Fail | Replaced all damaged roof sheeting
MSA-DCS | WA3185408 | Riot damage to Glazing in Units 2, 3 and 4 | Hakea Prison | GMP-BR-RC | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-17 13:06:00 | Fail | all windows reglazed and grills rewelded - claim # 20/13004
MSA-DCS | WA3185413 | Riot damage to Doors to Units 2, 3 and 4 | Hakea Prison | GMP-BR-RC | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-08-05 11:21:00 | Fail | Damaged doors replaced, locks installed, painted
MSA-DCS | WA3185415 | Riot damage to cells (general building) to Units 2, 3 and 4 | Hakea Prison | GMP-BR-RC | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2021-03-24 10:44:00 | Fail | BOILER VENT PIPES REPAIRED
MSA-DCS | WA3185418 | Riot damage to Air Conditioning Units to Units 2, 3 and 4 | Hakea Prison | GMP-BR-RC | Air Conditioning | Room Air Conditioners (AC) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-07-17 12:35:00 | Fail | repair damaged ventilation equipment
MSA-DFES | WA3174136 | main admin The security alarm box/siren is hanging off the wall on the Western end of the main admin | FESA RHQ - Forrestfield | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-26 14:00:00 | Pass | Refixed alarm box to the wall
MSA-DFES | WA3174299 | LT engine room door getting caught on structural beam cannot operate | Kensington (old) | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 17:00:00 | 2020-04-30 12:15:00 | Fail | Technician attended the site of 21 George Street, Kensington, WA to the engine room sectional door W22590 on 26/03/2020. Following a full test and inspection of door components found fault to be sectional door is damaged. Top section is bent and needs replacing plus top support for arm. Extra works required - quote to follow.
MSA-DFES | WA3174493 | Parade ground Flag poles on Applied Training Ground require replacement cleats, to tie off flags | FESA RHQ - Forrestfield | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-01 00:30:00 | Pass | Replaced damaged fixings
MSA-DFES | WA3174525 | Rear Engine bay door will not open electrically. | CFRS Murdoch | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-02 16:15:00 | Fail | Identified fault was the logic unit is broken. Replaced logic unit, programmed to suit. Tested okay
MSA-DFES | WA3174633 | Retrospective Work order - Operational Delivery & BA Service Area - Water coolers, water is cloudy | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 26 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-26 12:00:00 | Pass | DIAGNOSED ISSUE WITH FOUNTAIN REPLACED BROKEN PLV ON UNIT
MSA-DFES | WA3174681 | Retrospective Work order - EXTERNAL CHECK CARRIED OUT. NO OFFENCE DETECTED. ALL APPEARS SECURE. | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 11:45:00 | Pass | Job completed - EXTERNAL CHECK CARRIED OUT. NO OFFENCE DETECTED. ALL APPEARS SECURE. MONITORING ADVISED
MSA-DTAG | WA3174338 | Basement,custody Cell 2 & Custody office - light flickering | Perth Children's Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-27 08:01:00 | Pass | Attended site and signed In. Replace tubes in cell 2 toilet and replace Blown downlight lamp in office. All now working informed staff.
MSA-DTAG | WA3174345 | Basement, Custody Sallyport - Door not interlocking | Perth Children's Court | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 14:52:00 | Pass | Moved reeds to accomodate new door position if it happens again the door service company will have to attend and aline to doors correctly
MSA-DTAG | WA3174410 | Lift not functioning | Midland Courthouse | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 15:00:00 | Pass | Not chargeable
MSA-DTAG | WA3174702 | Level 4, Room 4.05 - Duress not working. We have 2 duress under the table , one not operational. | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-27 09:00:00 | Pass | Job Completed - Duress not working. Investigated duress, found one of them was active, duress's have been connected as series. Reset both and tested individually. Duress buttons are working
MSA-DTWD | WA3174253 | G block workshop stop button to grinder loose needs re tightening | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-26 10:00:00 | Pass | Attended site and signed. Located G block. Found e stop on machine to be loose. Dismantle machine and inspected. Tried to chase up a metal body e stop for better durability. Could not source locally in Perth. Made safe and repaired e stop on machine. Tested all okay. Job complete
MSA-DTWD | WA3174295 | T-COM security system - Alarm code not working | Rockingham Campus | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-26 13:00:00 | Pass | 26/03/2020, 1200-1315Attend site and add/remove alarm codes as required by client, test for client, all working when onsite.
MSA-DTWD | WA3174361 | A Block, room AG27 - appears to be moisture in the walls and therefore paint peeling. | Carlisle Campus | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-05-19 16:00:00 | Fail | Works are now completed and please see photos attached
MSA-DTWD | WA3174396 | Level 5, Roof Plant Deck - Both Chillers in alarm | Perth Campus B2 | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-26 15:01:00 | Pass | Attended site and signed in.Accessed chillers on b2 roof and found chiller 1 tripped on low economizer pressure or suction valve closed fault.Found chiller 2 tripped on exchanger temp sensor swapped fault.Reset faults and ran chillers up.Checked operation of chiller 1 and found suction valve opens and economizer pressure appears ok.Confirmed correct sensor connections on chiller 2.Carried out further tests on chillers and found all appear ok.Adjusted some parameters to help chillers cool building.Suspect chillers tripped on low load as the sensor fault can occur when the water temp entering is lower than the water temp leaving which has occured before.Monitored and found no other faults occured.Reported findings and left site.
MSA-DTWD | WA3174442 | L2 sth block S214 server room-Replace faulty CRAC unit with 73kW ChW CRAC unit-see notes | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-10-05 12:52:00 | Fail | WORKS COMPLETED AS PER BRAF server room-Replace faulty CRAC unit with 73kW ChW CRAC
MSA-DTWD | WA3174465 | Sliding widow from CSC to passageway wont open | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-26 16:00:00 | Pass | Site no longer require the modifications to the window- please invoice CTD - Email from site in docs
MSA-DTWD | WA3174469 | Lvl 7, Male toilet- Remote push button for urinal pushed through wall. Button missing | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 26 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-31 16:29:00 | Pass | Install new flush button
MSA-DTWD | WA3174513 | D Block, Room D17 Lecture Theatre- Light switch cannot be turned off | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 06:59:00 | Pass | Attended site and signed in. Replaced faulty switch in lecture theatre. Job complete.
MSA-DTWD | WA3174591 | Rooms Q010 & P023 - repair/replace door lock | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-26 15:15:00 | Pass | Serviced lock Q10 & tested with GMK. Service P21as reported incorrectly as P23. Replaced key as it has stopped working in this lock
MSA-DTWD | WA3174593 | Canteen toilets are slow to drain | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-31 16:18:00 | Pass | Unblocked toielts
MSA-DTWD | WA3174640 | cafeteria exteria door handle has fallen off will not be able to get in from the outside when shut | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 26 Mar 2020 | 2020-03-26 17:49:23 | 2020-03-26 14:50:00 | Pass | replace faulty door furniture
MSA-DTWD | WA3174720 | A block, G level, external - external toilet drain blocked | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 26 Mar 2020 | 2020-03-27 17:00:00 | 2020-03-27 10:30:00 | Pass | Carried out thorough investigation into possible blocked drains. Cleaned out relief gully and flushed thoroughly. Installed new grate.
MSA-DTWD | WA3174731 | Level 1, Main classroom - Power faulty, tripping. Check the power source/RCD to ensure all ok | Perth Campus B3 | GMP-BR | Electrical | Materials (EL) | AWB Co. | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 07:02:00 | Pass | Attended site and signed in. Inspected and tested power and rcd throughout building. Everything working. Job complete.
MSA-DTWD | WA3174747 | Lvl 3, Room 303- Mutlipe compact fluros are not working | Perth Campus B5 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 07:01:00 | Pass | Replaced faulty downlight globes and transformers. Tested all working correctly. Job complete.
MSA-DTWD | WA3174757 | Lvl 3, Staff Office- Reattach electrical skirting | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 07:00:00 | Pass | Resecured ducting cover that had come out of channel. Job complete
MSA-DTWD | WA3174771 | A Block, AG10B - Damaged skirtings | Carlisle Campus | GMP-BR | Carpentry | Joinery (CA) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 Mar 2020 | 2020-03-31 17:00:00 | 2020-04-28 11:45:00 | Fail | Damaged skirting replaced in A Block
MSA-DCA | WA3185497 | ** Retrospective work order** G Floor, Loss of power to ground floor fire pump room | State Library of WA-Main Building-Ground Floor-Fire Sprinkler Pump Room | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 27 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-27 12:02:00 | Pass | Lighting in the fire pump room had gone out under fault, seperated from known faulty circuit,
MSA-DCS | WA3174808 | External Perimeter Pump House - Pump came on. | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 04:10:05 | 2020-03-27 03:23:00 | Pass | Prisoners rioting and set fire in the laundry.DFES arrived and extinguished the fire using hydrants / hose reels which started the pumpsReset and refilled pumps.Checked sprinkler valve and noted it was not seated properly trued briefly to reseat but needs further attention. (Don’t believe this had anything to do with the incident/fire.Isolated zone 66 (sprinklers) and 36 (Vesda) where a unit fire or damage has been caused to alarm/fault this device. Further investigation is required to understand what is required.Large scale incident and wasn’t allowed to walk to unit incident area. (Unit 3 or 4)Pumps put back online and prison staff advised hydrants, hose reel and sprinklers are online.
MSA-DCS | WA3174849 | Perimeter cameras - PTZ 7,9 and 10 are not working. | Albany Regional Prison-Gatehouse | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 13:36:08 | 2020-03-27 10:16:00 | Pass | cameras down due to lightning strike, restarted & checked ok. job complete
MSA-DCS | WA3174908 | PTZ camera no: 157 is not working(SHU Camera) | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 10:23:55 | 2020-04-30 16:33:00 | Fail | Investigated camera fault, traced cables and repaired cable faults,Tested video signal and PTZ controls OK.Job CompleteParts: Consumables
MSA-DCS | WA3175051 | MCR pod gate house PDA screen fault is something is not connected- | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 12:13:40 | 2020-04-03 13:08:00 | Fail | Job to be invoiced at cost to date.
MSA-DCS | WA3175099 | external gardens Nicholson Rd end damaged sprinkler | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-31 09:00:00 | Pass | NO FAULTS FOUND AFTER FULL TEST AND INVESTIGATION
MSA-DCS | WA3175101 | Western Oval - by the smoking hut - retic solenoid is faulty | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-09 15:00:00 | Fail | FAULTY WIRING AND CONTROLLER FAULT, FIXED TESTED AND ALL OK
MSA-DCS | WA3175104 | Gardens compund - retic controller is faulty - not turning on | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-09 11:30:00 | Fail | FAULT IN WIRING, SYSTEM FIXED AND BACK ONLINE
MSA-DCS | WA3175109 | Market Gardens - Solenoid U6 constantly clogging up | Casuarina Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-31 11:30:00 | Pass | REPLACED FAULTY BROKEN SOLENOID
MSA-DCS | WA3175123 | Cabinet Shop, Front Entrance - main roller door damaged. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | UNIVERSAL DOORS | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-08 08:30:00 | Fail | repairs to cabinet shop door
MSA-DCS | WA3175133 | Unit 14, B & D ,Day room, Prisoner water fountain - Leaking quite bad | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-30 14:16:00 | Pass | Replaced bubbler cartridge
MSA-DCS | WA3175139 | MPU (8), West, SPU - Shower head between cells 2 & 3 is constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-27 14:30:00 | Pass | Remove and replace 1/4 turn spindle in plumbing duct behind shower.
MSA-DCS | WA3175142 | Unit 14 - Program Room East-the window next to the toilet in unit 14 B/D programs room does not lock | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-03 10:00:00 | Pass | RESET SASH/ LOCKING MECHANISM
MSA-DCS | WA3175144 | Unit 5, Cell C11 - Main lock is faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 13:32:00 | 2020-03-27 12:45:00 | Pass | Serviced lock
MSA-DCS | WA3175157 | gate house inner roller door jamming and not closing | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 13:44:12 | 2020-03-30 12:30:00 | Fail | 27/03/20 - 10:00amInspect roller door. Contact Supplier27/03/20 - 13:30pmAttend site with supplier.Perform temporary fix to roller door brake30/03/20Pick up / drop off scissor lift.Remove old break / bearing. Replace with new and test.OK
MSA-DCS | WA3175185 | control multiple monitor and keyboard faults | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 14:01:25 | 2020-03-31 15:25:00 | Fail | Replaced faulty power supply on monitor and repaired data comms fault and software issue.Tested OK.Job CompleteParts Used (SEME Stock):Power SupplyConsumables
MSA-DCS | WA3175187 | Jim's Office air con is leaking water - quite badly | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 27 Mar 2020 | 2020-03-28 10:03:56 | 2020-03-27 16:16:00 | Pass | Drain is free flowing
MSA-DCS | WA3175196 | unit 4 PRU communitcations and MSB server has strong burning smell coming from the cupboard | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 18:07:53 | 2020-04-17 14:00:00 | Fail | Power boards replaced which involved a system shutdown of the main security rack at PRU.
MSA-DCS | WA3175199 | unit 4 PRU control room, speakers for the alarm panel not working | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-06 13:30:00 | Fail | Sound for alarms redirected to monitor speakers making the bulking external ones redundant
MSA-DCS | WA3175236 | Unit 4, B wing, Cleaning cupboard. TAp fell off in cleaning cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-27 15:30:00 | Pass | Reinstall cleaners tap / spout in cleaners closet.
MSA-DCS | WA3175250 | Unit 2, 3 & 4 Please be on site at 2pm today to check all fire systems | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 27 Mar 2020 | 2020-03-28 10:45:49 | 2020-04-08 09:57:00 | Fail | 27/3/20 JN MSAttended site gym zone in fault, investigated zone found stairwell connecting laundry and gym had been set on fire during riot and multiple conduits and cables melted in roofspace. Tue 31stContinued to trace cable to assess damage
MSA-DCS | WA3175318 | Unit 9 Cell A3 Viewing glass is smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 27 Mar 2020 | 2020-03-28 11:18:32 | 2020-03-27 14:30:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3175363 | Unit 10 Cell B14 Viewing window is broken | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 27 Mar 2020 | 2020-03-28 11:39:32 | 2020-03-27 15:45:00 | Pass | WINDOW REPLACED
MSA-DCS | WA3175382 | gate house camera's 81 to 93 not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Mar 2020 | 2020-03-28 11:59:22 | 2020-03-30 11:00:00 | Fail | Replaced faulty power supply, job completed.
MSA-DCS | WA3175434 | Industries workshops - very low water pressure SITE COSTED | Wooroloo Prison Farm | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 16:43:01 | 2020-03-27 15:53:00 | Pass | Attended site,Investigated low water pressure to industries section of prison. Conducted testing at the boundary water meter and found pressie to be good at 550 kpa.Water to industries functioning well.
MSA-DCS | WA3175437 | Kitchen - Air con leaking on the roof A side dinning room. | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 27 Mar 2020 | 2020-03-28 12:45:22 | 2020-03-27 15:30:00 | Pass | Attended site. Evaporative system servicing A side dinning area leaking water. Applied tests and checks to find float valve to be stuck and not controlling water level. Loosend and adjusted float valve and water level. Tested operation. System operating correctly with no water leakage present.
MSA-DCS | WA3175439 | Unit 14, D4 - The join between the showerscreen and the tiled ledge it sits on has corroded away | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-05-28 15:00:00 | Fail | RE SEALD TILE LEDGE ON SHOWER SCREEN
MSA-DCS | WA3175456 | Lvl 1 - desk W1.83- Flickering lights above desk-this is not a duplicate | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-30 16:30:00 | Pass | Replaced failed lamps and starters
MSA-DCS | WA3175464 | Industries - please empty/flush main drain | Casuarina Prison | GMP-BR- HO | Waste Management | Waste Removal (WM) | Western Resource Recovery Pty Ltd | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-29 10:01:00 | Fail | Drains blocked
MSA-DCS | WA3175578 | Unit 14 - D2-The shower drain in cell D2 is blocking up. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-30 13:00:00 | Pass | Plumb sink to clear blockage, remove flow restrictor and install one quarter turn valve to adjust pressure
MSA-DCS | WA3175589 | Unit 14, D9 - shower blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-30 15:30:00 | Pass | Remove gratr, remove hair, moflo, plunge to no avail. Open plumbing duct and plunge 80mm drain to clear. Reinstall grate and test.
MSA-DCS | WA3175667 | Variuos lights faulty not working | Mandurah | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-31 15:30:00 | Pass | Repaired lighting in various areas as required.
MSA-DFES | WA3177742 | Retrospective work order do not attend-FRONT DOOR FOUND OPEN. STAFF ONSITE | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 27 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-27 22:05:00 | Pass | NTERNAL & EXTERNAL CHECK CARRIED OUT. FRONT DOOR FOUND OPEN. STAFF ONSITE. NO ID NAME OF MIKE IN UNIFORM,ADVISED TOM AND PATROL CLEARED TO DEPART FROM SITE
MSA-DTAG | WA3175581 | 1987 L4 plant room A/C 1 unit has failed to activate | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-05-06 14:00:00 | Fail | Cleaned butterfly valve
MSA-DTAG | WA3175602 | Lift not functioning | Midland Courthouse | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 27 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-30 10:45:00 | Pass | Not chargeable
MSA-DTAG | WA3175615 | Basement control room - Fault in FIP shows – “Level 4 Custody Vesda" | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 19:12:43 | 2020-03-27 17:00:00 | Pass | Attended site, fault on vesda level 4. Replaced vesda filter, cleared fault from FIP.
MSA-DTWD | WA3175136 | J & F block ground J110 & F204 . Cleaners sinks are blocked-see notes | Midland Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-31 10:39:00 | Pass | Cleared blockages in both cleaners sinks
MSA-DTWD | WA3175145 | FAULT ON T-COM ALARM PANEL | Rockingham Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-27 13:25:00 | Pass | 27/03/2020, 1300-1325Attend site and changed codes for J block as directed and test all working when on site
MSA-DTWD | WA3175351 | A & G block upstairs AF4 & Classroom above toolstore-new air con unit leaking | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 27 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-30 16:00:00 | Pass | Picked up water proofing paint from supplier. Arrived on site signed in. Checked in with Marty, gained access keys. Gathered required tools and equipment, cleaned down roof area of leaves and build up of grime cleaned down with solvent from van stock to remove oil on surface. Applied roof sealant, while drying removed panals off a/c 4 unit using rags, removed excess water from coil and fan area, left open to allow to dry. One painted area dry recoated area, Replaced panals on a/c 4. Cleaned up work area. Completed paperwork and signed out and removed all wast material off site and disposed of correctly.
MSA-DTWD | WA3175401 | Outside Ponds - Check pond pump is functioning correctly | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-31 11:45:00 | Pass | cleaned and flushed pump filter
MSA-DTWD | WA3175418 | Building/block 10, Level 1, room 10F90 - water leaking from air conditioner | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-30 10:30:00 | Pass | Traveled to site. Signed in. Located unit in room 10F90. Found drain blocked. Removed fascia and flushed drain with drain cleaner. Ran a cable snake up the drain. Drain now unblocked. Flushed multiple times. All ok.
MSA-DTWD | WA3175424 | Building/block 1, Level 1, Ladies toilet - Broken light fitting | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-31 15:15:00 | Pass | Attended site and signed in. Located level 1 ladies toilets. Removed old light fitting. Replaced with new led. Tested all okay. Job complete
MSA-DTWD | WA3175494 | B block, Room B2422 - Split system aircon is leakng water | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-30 15:00:00 | Pass | Attended site and investigated. Water found pooling in unit. Traced condensate system and found to have a 3 store fall with 2x under celling systems feeding into the same drain system meeting at a common T pice. Isolated each unit independently and flushed line. Screw couple fitted to allow flushing. Blockage was cleared from line. Please be advised that the fall at units is not very good. Tafe FMs have been advised that if water lak reoccurs condensate pump would be recommended to be installed. Both units working and drining condensate. Cleaning agent applied. Work area left tidy
MSA-DTWD | WA3175573 | A block L1 AF2.12 Light switch jammed on-see notes | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-30 14:00:00 | Pass | Replaced faulty light switch with new .job completed
MSA-DTWD | WA3175596 | B block, Level 3, B306 - faulty light sin B306 | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-30 14:01:00 | Pass | Repalced faulty light switch and fluros/control gear to lights in rmB306
MSA-DTWD | WA3175630 | Level 2, bookshop - Replace carpet front of the counter | Perth Campus B1 | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 27 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-30 14:00:00 | Pass | Replaced damaged carpet as requested by site
MSA-MRWA | WA3175117 | ground various Intercom very quiet, please attend and investigate-see notes | Traffic Operations Centre | GMP-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-27 14:45:00 | Pass | Determinate both rear intercoms, adjust volume onmaster station on L1, test all intercoms onsite, tested allok. Advised client to be mindful of master volume on L1.
MSA-MRWA | WA3175211 | Men's toilet, behind reception - Broken toilet seat please retify | Jandakot Depot | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 27 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-27 12:50:00 | Pass | Replaced toilet seat to male disabled WC behind reception
MSA-MRWA | WA3175646 | Southern internal lights are dimmed, please investigate & remediate to working order | Road Network Operation Centre (RNOC) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 0 | CLOSE | 27 Mar 2020 | 2020-03-27 19:35:35 | 2020-03-30 07:30:00 | Fail | Picked up access keys from don aitkens . Arrived. To site, signed in , tetsted power to lights which were half dim 240v present , . Advised Brendan that the lighting issue is with the Dali system. Site advised they have there own contractor to conduct repairs. Signed out , returned swipe card to don aitkens. Job completed
MSA-DCS | WA3175749 | Banksia Hill Detention Centre- roller door is not going down in gatehouse | Banksia Hill Detention Centre | GMP-BR- HO | Carpentry | Materials (CA) | AFD Contracting | 0 | CLOSE | 28 Mar 2020 | 2020-03-28 12:26:34 | 2020-03-28 10:30:00 | Pass | 28/03/20Reset breakers on roller door panel.Tested door several times.Gave instruction to current gate house staff.
MSA-DCS | WA3175795 | Hakea-Melaleuca Prison- kitchen dishwasher is leaking water from bottom | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 28 Mar 2020 | 2020-03-29 11:28:38 | 2020-03-28 14:32:00 | Pass | Reconnected loose washing machine drain.
MSA-DCS | WA3175807 | Bakery, fridge seal not working | Casuarina Prison-Kitchen | GMP-BR- HO | Equipment | Catering Equipment (EQ) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 28 Mar 2020 | 2020-03-28 17:09:49 | 2020-03-28 15:00:00 | Pass | Arrived on site and signed in tools,checked over freezeroom found control circuit breaker tripped,checked wiring all looks ok,reset breaker and tested unit all running ok at present.
MSA-DCS | WA3175821 | Kitchen - piolet light in bratpan number 2 is not working | Karnet Prison Farm-Stores | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 28 Mar 2020 | 2020-03-28 18:07:39 | 2020-04-07 12:30:00 | Fail | 28/03/20Called as requested to the bratt pan not going onto burner flame. Found the o/t tripped so reset tested thermostat. Unit will require both the o/t and the thermostat. Parts required1x o/t stat1x thermostat 29/3/20Make - Cleveland Bratt PanModel - SGL-40TR399Serial - 120123051Called to Ignition probe out again.Reset and tested all ok.7/4/20Installed parts in Bratt pan
MSA-DCS | WA3175894 | Freezer temp should -16deg but its 20 deg and alarm is going on | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Catering Equipment (EQ) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 29 Mar 2020 | 2020-03-29 12:34:51 | 2020-03-29 10:25:00 | Pass | Arrived on site and signed in, checked over freezeroom found down to -16 degrees, checked pressures all ok, no ice on indoor coil,reset alarm,by time finished carrying out checks room was down to -20,suspect they read temperature whilst room was in defrost mode.
MSA-DCS | WA3175897 | The fence isn't alarming when daily check is done. Only 3 zones are alarming. | Bunbury Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Mar 2020 | 2020-03-29 16:50:04 | 2020-04-24 13:00:00 | Fail | Replace D2-D3 IF module and tune both fences. Test ok.
MSA-DCS | WA3175927 | Wandoo Rehabilitation Facility- PTZ 5 camera located external not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 2 | CLOSE | 29 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-30 09:30:00 | Pass | Replaced boom lift
MSA-DCS | WA3175928 | Hakea-Melaleuca Prison- Plumbing issue | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 29 Mar 2020 | 2020-03-29 15:30:46 | 2020-03-29 13:49:00 | Pass | Repair spindle to basin clear blockage to shower
MSA-DFES | WA3203977 | Retrospective work order do not attend-EXTERNAL CHECK CONDUCTED, NO SIGN OF ANY DAMAGE | CFRS Midland | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 29 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-29 21:56:00 | Pass | EXTERNAL CHECK CONDUCTED, NO SIGN OF ANY DAMAGE, ALL APPEARS TO BE SECURE. CLEARED BY CHAD.
MSA-DCA | WA3176452 | Fan failure on unit FCU 8 | Art Gallery of WA - James St - Centenary Gallery Ground Floor - Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 16:30:00 | Pass | Attended call-out. FCU 8 humidifier, humidity, Fan Failure alarms. RA filters at 175kpa do. Replaced filters with spares on site. Humidifier 8 EF alarm. Confirmed water supplying to unit. Drained tank and monitored fill time. Reset alarm. Inspected SAF. No alarms or faults discovered at time of investigation.No further alarms.Closed job.
MSA-DCA | WA3177043 | Ground floor, east main building - vesda panel alarms, activate/alarming, have muted | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Security Office | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 19:46:57 | 2020-03-31 09:45:00 | Fail | Attended site and found system normal checked history log and found that the Vesda Reference detector had intermittently faulted a few times on the 27/3 but nothing since.Checked Vesda history log and found no entries to match.Left system normal
MSA-DCS | WA3176168 | Unit 12 C+D pod door frame. Door frame has come loose | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 07:06:17 | 2020-03-31 13:30:00 | Fail | 30/3/30 Attended site and assessed what repairs where required, new seal required31/3/20 Picked up new door seal and installed to pod door frame.
MSA-DCS | WA3176192 | Reception, Behind induction desk- Vinyl is lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Mar 2020 | 2020-04-03 17:00:00 | 2020-07-02 10:30:00 | Fail | damaged flooring removed & replaced
MSA-DCS | WA3176196 | Zone 2 & 8 in constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 07:25:16 | 2020-03-31 13:00:00 | Fail | Rectified anf fixed mx zone 2 and 8 ,job completed
MSA-DCS | WA3176206 | Eyre, A Wing- Urine room light faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-01 10:00:00 | Pass | Replaced lamps and starters, test ran ok.
MSA-DCS | WA3176208 | Eyre, B Wing, Cell B3- cell light faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-01 11:00:00 | Pass | Replaced lamp and starter, test ran ok.
MSA-DCS | WA3176210 | Eyre, C Wing, Cell C1- Obs light faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-01 12:00:00 | Pass | Replaced lamp, test ran ok.
MSA-DCS | WA3176211 | Gascoyne, Cell B6- cell light faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-01 12:30:00 | Pass | Replaced lamp and starter, tested ok.
MSA-DCS | WA3176216 | Jeelia, Cell A4- door sagging | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 30 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-02 09:45:00 | Fail | Replaced hinges & screws
MSA-DCS | WA3176218 | Jeelia, Awing laundry door dropped on lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 30 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-02 10:45:00 | Fail | replaced screws on hinge to realign cell door
MSA-DCS | WA3176231 | INF (10), disabled flexible shower hose has broken & has a leak | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-31 12:00:00 | Pass | Inspect shower, pick up new parts, install new shower head and hose.
MSA-DCS | WA3176233 | Gatehouse- Cameras 65,66,67 & 115 not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-30 16:04:00 | Pass | Sourced parts, attended site, repaired multiple camera faults and tested OK.Job CompleteParts used:Consumables
MSA-DCS | WA3176240 | Unit14, Cell B5- toilet base is very wet, appears to be a leak | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-29 10:00:00 | Fail | Remove and replace toilet and pan adapter. Clean up and dispose of rubbish.
MSA-DCS | WA3176243 | Unit 2, A Wing, Cell A11- window wont stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-03 13:30:00 | Pass | SASH RE-BALANCE- SPIRAL BALANCES RENEWED
MSA-DCS | WA3176265 | Unit 6 - D Wing The personal key lock can not be opened by key. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-03 11:00:00 | Pass | replaced hinges, door plate, lock and barrel. Adjust strike to suit.
MSA-DCS | WA3176266 | Back door of reception- door latch is broken | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 11:58:57 | 2020-04-01 13:45:00 | Fail | supplied & installed custom made strike
MSA-DCS | WA3176289 | Unit 1 - C Wing-Toilet Blocked C9. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-30 14:00:00 | Pass | Plunge toilet and test several times to clear blockage
MSA-DCS | WA3176302 | Unit 13, Power point of external wall on B/D side yard (BBQ AREA) socket is damaged & wires exposed | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-30 13:00:00 | Pass | Repaired damaged bbq gpo in unit 13
MSA-DCS | WA3176305 | Unit 6, B/D day room flickering light located just outside the officer's control room | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-30 14:00:00 | Pass | Attended unit 6. Damaged lights to be replaced in day room. Scaffolding required
MSA-DCS | WA3176312 | Unit 13, Cell A13- Blocked floor drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-31 08:00:00 | Pass | Remove grare, remove hair, moflo, rinse, plunge, reinstall grate and test
MSA-DCS | WA3176315 | Unit 7, A Wing- Vinyl floor is lifting in the kitchen area in four spots | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-10-25 09:15:00 | Fail | DAMAGED VINYL UPLIFTED & REPLACED
MSA-DCS | WA3176350 | Toilet Blocked C9.-Cell C05 - Light switch next to cell call coming off wall, needs to be re-secured | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-03 11:00:00 | Pass | Attended unit, unable to gain access due to lockdown. Returned and replaced damaged cell switch and gpos
MSA-DCS | WA3176362 | Reintegration office- A/C leaking water from indoor unit | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-31 11:30:00 | Pass | Found ac to have blocked drain, flushed drain thoroughly and now unit has no leaks
MSA-DCS | WA3176372 | Unit 2, lower landing office- A/C not cooling | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-31 13:00:00 | Pass | Found unit to be set incorrectly on remote control, changed to correct setting and unit now runs correctly.
MSA-DCS | WA3176379 | Unit 3, A wing kitchen- sink taps broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-02 09:00:00 | Pass | Supply and install new kitchen sink mixer
MSA-DCS | WA3176387 | Unit 2, Cell D55 & lower landing outside laundry- whirly birds faulty | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-05-04 14:15:00 | Fail | ATTENDED - NO FAULTY WHIRLYBIRDS LOCATED
MSA-DCS | WA3176408 | Internal walkway light not working | Boronia Pre-release | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-01 14:30:00 | Pass | Repaired pathway light and restocked site supply of lamps.
MSA-DCS | WA3176413 | Industries Admin W/S-Repair damaged sky lights on industries roof/Boot shop/Garments/VOC Skills | Casuarina Prison | GMP-BR-RC | Roofing | Rooflights and Skylights (RF) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 13:09:57 | 2020-05-29 15:02:00 | Fail | Replaced damaged skylights
MSA-DCS | WA3176415 | Manual trades store room - GPO broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-30 15:00:00 | Pass | Investigate and replace 2 broken gpo’s in manual trades store room
MSA-DCS | WA3176434 | Industries Administration, workshop - repair damaged/broken windows in Garments/Voc Skills/Textiles. | Casuarina Prison | GMP-BR-RC | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 13:21:52 | 2020-05-06 14:15:00 | Fail | windows have been replaced and tinted
MSA-DCS | WA3176439 | Industries Administration, workshop - repair/replace damaged air vent on Bootshop rood | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-06-04 10:13:00 | Fail | Repaired damaged air vents to roof
MSA-DCS | WA3176442 | Gymnasium-Repair damaged camera on Gymnasuim roof south side | Casuarina Prison | GMP-BR-RC | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 13:30:14 | 2020-04-06 08:30:00 | Fail | Replaced damaged camera laminated glass window with new, rectified and fixed the fault on communication link between the camera and gatehouse control room. Job completed.
MSA-DCS | WA3176444 | CCU(11), Cell D4- Camera over is damaged, unable to see anything in cell | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-09 15:00:00 | Fail | Travelled to site and replaced CCU camera in cell HD4. All replaced and tested ok. Job complete WV-CW504SE seme stock used.
MSA-DCS | WA3176455 | Unit 1, B Wing, Cell 9 hatch unable to lock barrel wont turn | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-05-06 10:00:00 | Fail | job completed repair require parts. Attend site replace lock and adjust hatch
MSA-DCS | WA3176480 | Boot shop - Workshop Repair damaged fire alarm light on roof at Bootshop | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-05-19 11:09:00 | Fail | replaced strobe with EWP
MSA-DCS | WA3176498 | Duress system 1 - tamper alarm transponder 4, blocks K, I West perimeter | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 09:57:47 | 2020-03-30 17:30:00 | Pass | Rectified and fixed the cover of TR2 B4 PT 3. Replaced the mdas receiver TR3 B7 PT0 ( site stock). Job completed.Site stock replaced with new
MSA-DCS | WA3176502 | Unit 4 PRU side security gate opened twice without authorisation | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 17:59:41 | 2020-03-30 18:15:00 | Fail | PRU automatic man gate has intermittent fault got stock and it doesn’t close, advice officer on site that the fault is coming from mechanical motor. To check and test by other contractor.
MSA-DCS | WA3176511 | Main gate inner sally port doors not operating correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 18:04:36 | 2020-03-30 15:00:00 | Pass | Locking pin not dropping properly due to mechanical problem, to be look after by other contractor. Job completed.
MSA-DCS | WA3176519 | Unit 4, Cell A15 & A14 - Buddy door lock is broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 14:08:13 | 2020-04-08 13:30:00 | Fail | suppled and installed replacement door including required hardware
MSA-DCS | WA3176525 | Laundry, office & day room & toilets - lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:10:51 | 2020-03-31 08:30:00 | Pass | Repaired lights
MSA-DCS | WA3176527 | Unit 3, D9 - broken light, off the ceiling | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:12:56 | 2020-03-31 14:30:00 | Fail | Repaired light
MSA-DCS | WA3176528 | unit 3, C3 - broken Lane window | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:13:57 | 2020-03-31 14:30:00 | Fail | reglazed window
MSA-DCS | WA3176530 | Unit 1, B4 - door window is broken. | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:15:32 | 2020-03-31 10:30:00 | Fail | reglazed window
MSA-DCS | WA3176531 | Unit 1, B8 - door window is broken | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:16:28 | 2020-03-31 09:30:00 | Pass | reglazed window
MSA-DCS | WA3176533 | Unit 1, B9 - blocked toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:17:27 | 2020-03-31 08:35:00 | Pass | No accessUnblocked toilet
MSA-DCS | WA3176536 | Unit 1, C9 - blocked toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:18:42 | 2020-03-31 10:17:00 | Pass | No accessUnblocked toilet
MSA-DCS | WA3176541 | Unit 1, B wing day room - Grille lock is jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:19:31 | 2020-03-30 12:45:00 | Pass | No fault found with lock, key issue
MSA-DCS | WA3176548 | Unit 3, C2 - toilets blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:21:27 | 2020-03-30 18:46:00 | Pass | Uninstalled and reinstalled toilet and used drain machine to unblock the sewer line.
MSA-DCS | WA3176567 | laundry, evaporative air con 2 & 3 leaking water and not running | Hakea Prison | GMP-BR- HO | Air Conditioning | Evaporative Coolers (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:23:00 | 2020-05-08 10:30:00 | Fail | Replaced pads damaged during prison riot.
MSA-DCS | WA3176577 | Reception toilet in shower area blocked toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:25:35 | 2020-03-30 15:25:00 | Pass | Unblocked toilet and shower
MSA-DCS | WA3176582 | Unit 10- C & D Wing Dayroom- Glass broken | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-14 14:30:00 | Fail | reglazed window
MSA-DCS | WA3176590 | Crises Care-Window rubber damaged | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:33:23 | 2020-04-01 11:00:00 | Fail | repaired window rubber
MSA-DCS | WA3176605 | Unit 9, B wing,Middle shower - glass loose in frame, beading damaged | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:42:29 | 2020-04-01 09:00:00 | Fail | Repaired window
MSA-DCS | WA3176630 | unit 9 B14 hinge Hinge damaged | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 10:51:41 | 2020-04-01 10:00:00 | Fail | replaced hinge - B13
MSA-DCS | WA3176640 | Health Corridor, Cleaning Store- Cold tap is faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-31 13:30:00 | Pass | Instal new taps to cleaners trough to allow for use of cleaners chemical station and washing Macheine at same time
MSA-DCS | WA3176653 | INF 10-SHU alley gate lock faulty.-see notes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 11:13:28 | 2020-04-01 15:30:00 | Fail | Attend site remove debris from concrete holes, file hole/strip in concrete with gap filler sikaflex, install floor mounted strike plate, weld stopper to drop bolt and service lock.
MSA-DCS | WA3176679 | Canteen- TV Aerial broken on the roof | Casuarina Prison | GMP-BR-RC | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-05-26 13:30:00 | Fail | Installed antenna to roof of Gymnasium to feed Canteen Area. New pole & conduit installed also.Tested signal strength, all working good.Job completed
MSA-DCS | WA3176685 | Industries Admin- Razor security wire to roofing to be repaired | Casuarina Prison | GMP-BR-RC | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 15:33:08 | 2020-03-30 12:00:00 | Pass | 30/03/20Personnel already on site for other works. Inspected.No works required.
MSA-DCS | WA3176780 | gate house control PDA system has crashed | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 16:16:58 | 2020-03-30 15:03:00 | Pass | Job complete
MSA-DCS | WA3176781 | Industries Administration - repair damaged early detection system on industries roof | Casuarina Prison | GMP-BR-RC | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 12:15:54 | 2020-04-07 16:00:00 | Fail | Replaced fence cabling on rooftop of industries building, tensioned cabling and tested each component functioning correctly and alarming correct. Zones F2 and F3 now fully operational.
MSA-DCS | WA3176827 | Reception Office- CCTV for auto gate enrty, no image on screen | Nyandi Training Academy | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-30 12:30:00 | Pass | Job complete
MSA-DCS | WA3176901 | Jasper A wing Smashed window approx 600x450 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-16 13:00:00 | Fail | RE GLAZED & SEC FILM INSTALLED
MSA-DCS | WA3176919 | Unit 4, Cell C15- Door window is broken | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 13:29:22 | 2020-04-01 12:00:00 | Fail | replaced obs window
MSA-DCS | WA3176921 | Laundry- no power to chemical pumps for washing machine | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 13:32:16 | 2020-04-01 08:30:00 | Fail | Replaced blown fuse
MSA-DCS | WA3176924 | Kitchen, slicing room- exhaust fan is not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-02 10:00:00 | Pass | Kitchen slicing room fan motor not working. Smashed terminal box. Replace with new box.
MSA-DCS | WA3176929 | Security Roof- TV aerial is broken | Hakea Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 13:36:37 | 2020-03-31 12:00:00 | Pass | Job completed - Repaired mounting pole and replaced antenna on roof. Tested good.
MSA-DCS | WA3176956 | Unit 1, hut 5 - Friction stay on window broken | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-06-09 09:45:00 | Fail | WINDOW STAYS REPLACED
MSA-DCS | WA3176966 | Printing Aread outside men's toilets near room 8I lights is flashing | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-30 17:15:00 | Pass | Replaced failed lamps and starters
MSA-DCS | WA3176973 | Require CCTV footage download 29/3/2020 multiple cameras | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-01 14:59:00 | Pass | See security for details, large footage download
MSA-DCS | WA3176974 | gardens dam pump isolator broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-06 11:00:00 | Pass | Investigate dam pump isolator. Source replacement. Manufacture and install new stand and install new isolator
MSA-DCS | WA3177019 | MPU - Camera M17 picture is poor quality | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 18:59:54 | 2020-04-01 12:00:00 | Fail | Contacted by site, cell is now available, attended MPU cell 17, removed paint sealed camera housing, and removed lense from imternal. Removed excess paint from housing face and sealer from rear, replaced camera lense for new and sealed. Sealed housing back in place with non pick and tested image good. No further action is required.
MSA-DCS | WA3177022 | Market Gardens-valve leaking in main garden near station 1-see notes | Casuarina Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-07 11:00:00 | Fail | excavated valve and repairs made to valve
MSA-DCS | WA3177038 | Unit 4 PRU side security gate opened twice without authorisation | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 23:34:28 | 2020-03-31 15:45:00 | Fail | 31/03/20Gate actuator and controller faulty (opening unexpectedly)Replaced actuator and controller.Tested - working well.
MSA-DCS | WA3177039 | Main gate inner sally port doors not operating correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 23:42:15 | 2020-03-31 16:15:00 | Fail | 31/03/20Fault reported with sallyport locking bolts and drive pins.Inspected operation and no faults found.
MSA-DCS | WA3177042 | C-13 Equipment room thermostate has changed to open | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 15:49:55 | 2020-04-08 19:22:00 | Fail | Tested room temperature and confirmed temperature is below 25 degrees Celsius.Adjusted and advised gate staff to keep for shut
MSA-DCS | WA3177066 | Unit 14, A wing - Vesda between A3-A4, battery showing faulty & chager fault | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 20:53:39 | 2020-04-01 14:58:00 | Fail | Call out to casuarina prison for battery/charger fault on Vesda PSU in unit 14. Checked PSU output and is only 23.9v. Batteries are also over 2years old. Recommend changing both PSU and batteries. PSU is NPS-5 Notifier PSU. And batteries are 12ah x 2. Vesda is located inbetweencells 3/4 in left hand wing and is in battery/charger fault.31/3/20 JN MSReturned to site fit new NPS-5 power supply, could not fit to existing cabinet as power supply is new model with different mounting points.Have got vesda temporarily working will need to return to fit new box.*Also when arrived on site 7/8 A/C PSU also failed - see WA31777571/4/20 JN MSFit new power supplies and 12Ah batteries in A/C 3+4. Vesda back up and running no faults on unit panel
MSA-DCS | WA3177080 | Unit 12, Cell C16 Blocked Shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-01 12:52:00 | Pass | Removed hair and food from drain
MSA-DCS | WA3177081 | Unit 1B - Camera 35 tamper alarm unable to clear | Wooroloo Prison Farm-Prisoner Accommodation Unit 1 Block 1 | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-29 15:53:00 | Fail | Repaired camera tamper 35 via cherry picker, tested operational.
MSA-DFES | WA3176575 | First floor Lobby - light is blown out | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 12:00:00 | Pass | Complete
MSA-DFES | WA3177007 | entry and male toilet lights not working | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-31 15:00:00 | Pass | ComepleteAttended site and located non working bathroom light, replaced globes all in working order, found non working outside light, replaced globes and all in working order, notified staff and signed out
MSA-DTAG | WA3176341 | Lvl 3, JSo Kitchen - Smell coming from the drain since Thursday or Friday last week. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-31 10:15:00 | Pass | Complete
MSA-DTAG | WA3176484 | 6 camera offline/not working - SAT-D001 SAT- D005 Sat D406 .BB offiline | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 30 Mar 2020 | 2020-03-30 13:46:40 | 2020-08-10 09:30:00 | Fail | job completed - Replaced and configured faulty PTZ. Tested PTZ, tested okay, all PTZ functions operating appropriately. Camera isrecording.
MSA-DTAG | WA3176494 | Level 9, Court 92 - Court door lock is not engaging when using the key | Central Law Courts | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-31 09:30:00 | Pass | Attend site to service and lubricate mortice lock
MSA-DTAG | WA3176634 | Level 10 - Lights not working x5 - lights out in 3 parts of Customer Service area. | Westralia Square | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-31 07:20:00 | Pass | Replaced faulty fluros and starters on lvl10 as shown by site. All working properly job completed
MSA-DTAG | WA3176662 | The intercom that is situated outside the Sallyport on the yellow pole isnt working, | Rockingham Justice Complex | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 15:45:00 | Pass | Found loose connection on back of external sally port intercom, re terminate and test, all ok
MSA-DTAG | WA3176795 | 1987 L4 plant room-Water leaking from cooling tower | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-31 11:00:00 | Pass | Attend site. Isolate chillers. Manually run cooling tower to test operation. Stop and start wate flow to tower. Found once tower had stopped, water started coming out of the fan barrels. This indicates that the water level in the tower is too high. Normall the excess water after shut down will drain out the overflow drain. Open up tower and check water level. Found level too high. Found shaft on float valve adjustment to have become loose allowing float to sit higher than normal. Readjust float valve to lower water level. Make sure adjustment on shaft is sucure. Carry out tests on tower. Tower now shutting off with no excess overflow. Deisolate chiller and test operation, working ok.
MSA-DTAG | WA3176984 | Lift not functioning.- this has been an ongoing issue | Midland Courthouse | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-31 10:15:00 | Pass | Not chargeable
MSA-DTWD | WA3176252 | Roof Plant, Both chillers in alarm | Perth Campus B2 | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 30 Mar 2020 | 2020-03-30 17:00:00 | 2020-03-31 12:30:00 | Fail | Elecmec attended to investigate the bms fault on both chillers
MSA-DTWD | WA3176346 | D block kitchen pipe under the sink tap will not turn off | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 11:45:00 | Pass | replaced leaking ministop underneath kitchen sink, cleaned up water in kitchen. Job required trip to galvins for a new valve.
MSA-DTWD | WA3176401 | E Block Aquarium room roof leak | Fremantle Campus (formerly WA Maritime) | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-29 15:30:00 | Fail | Works are now completed
MSA-DTWD | WA3176478 | House 803, Kitchen- Leaking Tap | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-30 17:30:00 | Pass | Job completed- Repaired kitchen tap
MSA-DTWD | WA3176481 | 876, Office- Leaking Tap | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 30 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-30 17:00:00 | Pass | Repaired leaking taps
MSA-DTWD | WA3176517 | Re glue skirting in corridors around level 4 | Perth Campus B1 | GMP-BR | Carpentry | Joinery (CA) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-31 11:45:00 | Pass | Glued down lifting sections of the carpet
MSA-DTWD | WA3176572 | E Block, E30 Kitchen- Water leak through light fitting | Bentley Campus | GMP-BR | Roofing | Tiled Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-31 16:15:00 | Pass | Sealed around power AC power switch. Leak resolved
MSA-DTWD | WA3176615 | In front of farm main meter - Burst water pipe | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-30 16:00:00 | Pass | Dug up & repaired burst water pipe
MSA-DTWD | WA3176835 | A block, ground floor, Male toilet - tap faucet split male toilets | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | Water (PD) | Techworks Plumbing | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-06 11:00:00 | Pass | Installed new basin mixer (MK2) and new cold water isolation under basins. New basin mixer posh Bristol MK2Hot water unit faulty, Mini stop installed onto unit.
MSA-DTWD | WA3177017 | C block cafeteria 2x damaged GPO's | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-01 15:30:00 | Pass | Attended site and signed in. Found gpos in kitchen to have extension cords running around the room and all over places. Advised to remove these cords and place gpos in places suited for appliances. Ran ducting around the walls and installed double gpos for freezers. Ran ducting along wall over to freezer and fridge. Installed double gpos for appliances. Replaced 20amp broken gpo with standard double for appliances. Swapped out circuit breaker to RCD for the old 20amp outlet. Tested all works okay. Job complete
MSA-DTWD | WA3177018 | E block kitchen E75 lights keep tripping out | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-07 11:45:00 | Fail | Attended site and signed in. Removed rangehood light cover. Disconnected and removed old faulty light fitting. Installed new led batten inside rangehood. Connected wiring. Refitted light cover. Tested light all okay. Job complete
MSA-DTWD | WA3177025 | L3 corridor west block Replace lights as required | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-02 11:00:00 | Pass | Attend site signed in . Replaced multiple fluros and starters out throughout level 3 west corridor and level 2 foyer as requested by site. Job completed
MSA-DTWD | WA3177032 | L2 corridor east block Replace lights as required | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 30 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-02 15:01:00 | Pass | Attend site . Signed in . Replaced multiple Fluros, starters and Pl lamps out throughout level 2 east corridor and main foyer as requested by site . Job completed
MSA-MRWA | WA3176459 | L2 kitchen Billi unit under bench closest to fridge is leaking, please remediate. | Road Network Operation Centre (RNOC) | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 30 Mar 2020 | 2020-03-31 17:00:00 | 2020-03-31 15:10:00 | Pass | Replaced front kit. All tested Billi Quadra Plus A401939158K
MSA-DCS | WA3177222 | Eyre block isolation valve unable to operate | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 31 Mar 2020 | 2020-04-06 17:00:00 | 2020-03-31 11:15:00 | Pass | Installed new tap and isolation valve to feed water to new water fountain
MSA-DCS | WA3177239 | Eyre, C Wing- Fridge electrical plug damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-01 13:00:00 | Pass | Shortened cord and replaced plugtop to fridge.Tested earth good and test ran fridge ok.
MSA-DCS | WA3177241 | Jeelia, C Wing- Vacuum lead is damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Mar 2020 | 2020-04-02 17:00:00 | 2020-04-01 13:30:00 | Pass | Reterminated cord to temove the damaged section . Test ran ok.
MSA-DCS | WA3177248 | Numerous inconsistency in keywatch. | Roebourne Regional Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Mar 2020 | 2020-03-31 15:40:37 | 2020-05-06 18:00:00 | Fail | Job complete
MSA-DCS | WA3177270 | MMU cell call system not working properly | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 08:07:48 | 2020-03-31 10:45:00 | Pass | Checked and found MMU office hard to hear the cell cell call in. Cell can hear office loud and clear. Further check located the problem to be the cell call console in office. Rectified the fault and tested all ok.
MSA-DCS | WA3177290 | Unit 14, D Wing, Cell D3- broken light switch | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-03 08:30:00 | Pass | Replaced damaged cell switch in unit 14 d3
MSA-DCS | WA3177293 | Unit 6, B Wing, Cell B7- Toilet cistern not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-02 08:00:00 | Pass | Replace badly corroded ball float inlet valve with new Inlet valve. The Ball float was jamming against the outlet valve.
MSA-DCS | WA3177310 | Unit 1 D5 door window chipped | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 08:15:38 | 2020-04-02 11:00:00 | Fail | OBS PANEL REGLAZED - WAS CELL D8, NOT D5
MSA-DCS | WA3177312 | Unit 6, A & C - Shower drains blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-03-31 16:00:00 | Pass | Use train machine to no avail. Pick up sewerjett from yard and get the sewer line from the manhole to clear blockage. This blockage was caused by a large corn cob followed by many T-shirts and cleaning products.
MSA-DCS | WA3177319 | Unit 2 B13 door window broken | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 08:20:31 | 2020-04-02 13:45:00 | Fail | OBS PANEL REGLAZED - FRAME REPAIRED
MSA-DCS | WA3177328 | unit 2 B13 sink smashed off wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 08:27:58 | 2020-03-31 13:20:00 | Pass | Replaced broken basin
MSA-DCS | WA3177339 | Unit 2 B13 door lock is jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 08:33:31 | 2020-03-31 13:00:00 | Pass | Serviced lock
MSA-DCS | WA3177373 | Unit 3, Pod 7- verandah lights faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 08:50:50 | 2020-03-31 14:00:00 | Pass | Replaced broken LED fitting
MSA-DCS | WA3177381 | Unit 10 A15 Medical hatch broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 31 Mar 2020 | 2020-03-31 13:11:09 | 2020-03-31 11:30:00 | Pass | replaced lock on hatch.
MSA-DCS | WA3177386 | Gate house, Pump House- VSD faulty on domestic water pump | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 09:12:54 | 2020-04-01 15:00:00 | Fail | Investigated faulty VSD found fan not working, returned and tested back up auto transformer.Disconnected old jacking pump.
MSA-DCS | WA3177390 | Gate house, Pump House- Domestic water pump faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 09:21:00 | 2020-04-01 13:30:00 | Fail | Inspect Pump House domestic pumps and try to figure out what is causing the problems.
MSA-DCS | WA3177425 | Duress system is offline, not working | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Mar 2020 | 2020-03-31 14:18:12 | 2020-03-31 12:45:00 | Pass | Checked and found MDAS system in gate control not working al all. Further check located the problem to be the power issue. Rectified the fault and and tidy up the cables. Tested all ok after.
MSA-DCS | WA3177470 | Unit 9 Cell B4 Medical hatch lock wont shut | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 31 Mar 2020 | 2020-03-31 14:50:24 | 2020-06-02 09:00:00 | Fail | Job completed - inspect hatch lock requires replacing. Onsite install lock hatch still unable to be correctly secured require replacementhatch. Attend site supply and install replacement hatch and custom made scar plates.
MSA-DCS | WA3177484 | gate house key watcher saying no key 15 but there is | Melaleuca Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 11:02:44 | 2020-03-31 14:00:00 | Pass | Locate key bunch #15 and test, ok and working as normal .job completed.
MSA-DCS | WA3177490 | Laundry - hot water heater not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 11:08:34 | 2020-04-03 15:20:00 | Fail | COMPLETED
MSA-DCS | WA3177496 | Fluro Tubes need replacing in archive room. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-24 11:30:00 | Fail | Repaired faulty lights in archives store room
MSA-DCS | WA3177501 | Textiles workshop ,staff toilet cistern not working . | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-03-31 11:19:00 | Pass | Remove and replace faulty Inlet valve
MSA-DCS | WA3177505 | Abattoir smoke oven elements not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-07 11:00:00 | Pass | Investigate abattoir oven. Source parts and replace damaged wiring.
MSA-DCS | WA3177545 | Unit 6 - A Wing Cell A7 toilet keeps blocking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-03-31 11:49:00 | Pass | Plunge toilet to clear blockage, test toilet several times
MSA-DCS | WA3177549 | Stores & External transprt workshop fluros need replacing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-17 16:00:00 | Fail | Replaced damaged lights in transport stores workshop.
MSA-DCS | WA3177567 | Garments - Office-lock needs repair /replacing on office door of garments | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 12:13:46 | 2020-04-02 11:45:00 | Fail | Job completed - replace damaged lock, external handle & Strike
MSA-DCS | WA3177574 | Garments - Lunch Room door is broken & beyond repair | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-06-24 09:42:00 | Fail | INSTALL NEW DOOR AND PAINT
MSA-DCS | WA3177636 | Unit 12 A6 toilet seat broken | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-01 13:54:00 | Pass | Replaced broken toilet seat
MSA-DCS | WA3177638 | Unit 12 staff kitchen electrical door does not lock when closed-see notes | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-08 16:45:00 | Fail | installed custom manufactured strike.
MSA-DCS | WA3177644 | Paint shop-Roller Door lock Jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 13:18:42 | 2020-04-01 10:00:00 | Pass | Repaired roller door lock
MSA-DCS | WA3177669 | Sallyport External Door not functioning correctly- as notes below | Melaleuca Prison | GMP-BR- HO | Building | Automatic Doors (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 13:48:50 | 2020-03-31 15:01:00 | Pass | Test the systems to night mode , all working ok . Job completed
MSA-DCS | WA3177687 | unit 2 control room door not locking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 14:10:03 | 2020-04-01 11:00:00 | Pass | Serviced lock
MSA-DCS | WA3177689 | Kitchen #3 oven digital display not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 09:38:56 | 2020-04-02 10:40:00 | Fail | Found out someone had poured a bucket of soapy water over the lid of oven. PCB now failed. Install new pcb to unit. Tested ok
MSA-DCS | WA3177743 | external light pole #11 globe cover needs replacing | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-30 10:30:00 | Fail | Replaced light covers
MSA-DCS | WA3177757 | Unit 14 A Wing Cell 7 & 8 , C Wing 7 & 8 - Fire system is not working | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 16:20:46 | 2020-04-01 13:46:00 | Pass | Faults on panel due to faulty power supply - replaced PSU and batteries and all ok on departure
MSA-DCS | WA3177761 | Microphonics Inner zone 9 & Outer zone 12 & 13 unable to reset | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 16:34:45 | 2020-05-02 12:38:00 | Fail | Re terminated couplers Tested resistance and confirmed all working with controller
MSA-DCS | WA3177767 | Unit 12 Internal door in A & B Wing not closing | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Mar 2020 | 2020-03-31 20:59:20 | 2020-03-31 19:15:00 | Pass | Attended site.Checked EBI System in Unit 12.Checked electric strike on door in A/B wing.Reseted power to electric strike.Tested.All ok at departure
MSA-DCS | WA3177773 | Zone Fault in Perrimeter Alarm | Casuarina Prison-External Area | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-06 11:30:00 | Fail | System left under test, tamper alarms returned and latched over weeknd, tested microwave G1 now operating correctly, tamper switch in G1 bypassed from microwave and run directly to switch, tested now operating correctly. Inner defence zone C1 is no longer gulse activating, zone E2 currently operating corectly.
MSA-DCS | WA3177775 | MCR Gatehouse - MDAS Monitor - Crisis care (TR-09) low battery. | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-01 14:00:00 | Pass | Attended crisis care unit (TR09) removed and replaced 7ah 12v battery for new, removed alarms and checked all ok.
MSA-DCS | WA3177776 | MCR - Reception - Supervisory point node12- reception (bell isolate and SHU AZF115 in abnormal statu | Casuarina Prison-Prisoner Reception, Visitor Centre, Prisoner Accommodation | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-01 12:56:00 | Pass | 1/4/20 JN MSInvestigated multiple isolations on panel - Bell isolated for unknown reason and SHU zone isolated. Checked history to fault find, checkedoperation of Bell after reset all operated correctly
MSA-DFES | WA3177478 | Dryer Room 2- light sensor is not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 17:00:00 | 2020-03-31 17:30:00 | Pass | COMPLETED
MSA-DTAG | WA3177261 | Custody Near the Strip search room- intercom is making a buzzing noise. | Joondalup Courthouse | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 31 Mar 2020 | 2020-04-02 17:00:00 | 2020-03-31 14:30:00 | Pass | System working correctly after reboot
MSA-DTAG | WA3177392 | 1903 ground lift car 1 out of service-see notes | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-01 12:45:00 | Pass | Not chargeable
MSA-DTAG | WA3177639 | isolate FIP and assist Australian HVAC on Saturday 4 April from 07.00am – 16.30pm | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-04 12:00:00 | Pass | Attended site to isolate FIP and assist Australian HVAC, investigated FIP due to ancillaries not working since panel upgrade. Relay boards do not work as intended, will require a quote to change out. Programme update will be required.
MSA-DTAG | WA3177642 | Lvl 10- Power points and ports in one of the marriage rooms are not working | Westralia Square | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-01 10:45:00 | Pass | Attended site. Met with marriage reception. Had to wait for ceremony to finish. Found data points wanting to be used. Wrongly labelled and not working. Can not identify at this time. Found 2 ports in cupboard. Patched in at server. Tested with IT. All okay. Job complete
MSA-DTAG | WA3177666 | Custody Camera on outside of sallyport faulting | Perth Children's Court-Courts 1 to 6-Basement | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-21 09:29:00 | Fail | Bypassed camera multiplex and plunged straight into recorder (camera 5). As issue could be with multiplex, advised client will order new camera in mean time. Will follow up next week to see if issue comes back, if it does will install the new camera that is on order.Follow up, spoken with Anthony and he has advised camera has stopped dropping out, therefore issue is with multiplexer, as these are no longer available only step would be to upgrade system to new. Camera is recording and viewable. Job closed
MSA-DTAG | WA3177675 | Ground floor Registry - Counters 8, 9 & 10 require infectious disease clean | Central Law Courts | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | OCS SERVICES PTY LTD | 1 | CLOSE | 31 Mar 2020 | 2020-04-01 17:00:00 | 2020-04-01 21:30:00 | Fail | infectious disease clean for court room 8, 9 &10
MSA-DTWD | WA3177257 | Remove graffiti from bench seat rear courtyard | East Perth Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 31 Mar 2020 | 2020-04-06 17:00:00 | 2020-04-01 12:10:00 | Pass | REMOVAL OF GRAFFITI FROM BENCH SEAT REAR OF COURTYARD
MSA-DTWD | WA3177619 | D Block - D19 Two door freezer keeps icing up | Bentley Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-01 12:00:00 | Pass | Found condensate drain has been damaged. Repaired drain pipes and cleared out drain. Started unit and waited to reach setpoint. Checked and found all ok.
MSA-DTWD | WA3177622 | A Block AG27 Split System AC is leaking water | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-01 12:00:00 | Pass | Travelled to site signed in. Located room Ag27 found split system had been leaking. Checked and flushed drain all ok. Found that the pipework had been poorly since installed. Stripped the insulation and reinsulated.
MSA-DTWD | WA3177637 | G Block, GG01- Feesh Air fan not working | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-14 08:00:00 | Fail | Accessed room GG01 located Fresh air fan. Would recommend a sub contractor electrician to attend to run a new power circuit so that it is separately wired to the Air-conditioning. Sub Contractor Elecmec attended and carried out repair works and ran new power supply to fresh air fan. Fan now works independently from Air-conditioning.
MSA-DTWD | WA3177645 | A Block, AF18 Staff Room- Water inlet tap is leaking & corroded | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | Water (PD) | Techworks Plumbing | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-04 15:22:00 | Pass | Replaced corroded water tap, installed mini stop tap / valve under sink as it was also corroded. all tested OK.
MSA-DTWD | WA3177658 | bench grinder will not stay on running | Naval Base | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-09 11:30:00 | Fail | Attended site and signed in. Removed old control system from grinder. Rewired and installed new complete control system to grinder, tested operation of each button correctly. Tested all okay. Job complete
MSA-DTWD | WA3177712 | North West Corner E Block - External- PA Speaker not working properly | Carlisle Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 2 | CLOSE | 31 Mar 2020 | 2020-04-03 17:00:00 | 2020-04-02 10:00:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro TAFE - Carlisle Campus, Bank Street, Carlisle WAWork Order Number: WA3177712Call out Date: 31/03/2020Target finish: 03/04/2020Original information: North West Corner E Block - External- PA Speaker not working properlyAttended site:Date:2/4/20Start Time:8.00Finish Time:10.00Techs on Site:2Works Carried Out: Located faulty speaker outside E block in assembly area. Replaced horn speaker and tested, all OK
MSA-DTWD | WA3177724 | L1 B162 faulty 3 phase cable for the E-6 machine in the photography darkroom | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-07 07:29:00 | Pass | Attend site. Signed in . Inspected cabling to E6 machine. Disconnected from isolater as requested by site. Job completed
MSA-DTWD | WA3177728 | L1 B162 faulty cord on film dry | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 31 Mar 2020 | 2020-04-07 17:00:00 | 2020-04-07 07:30:00 | Pass | Attend site. Signed in. Inspected faulty plug top on machine in B162. Replaced with new.p and tested. All working properly.Job completed
MSA-DCA | WA3180097 | front of the building cafe window smashed | His Majesty's Theatre-Theatre Building-Ground Floor | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 17:00:00 | 2020-04-06 11:15:00 | Fail | ATTENDED SITE 01/04/20, SECURED BROKEN GLASS WINDOW WITH 2SQM OF SECURITY, GLASS ON ORDER + 2 MEN TO COMPLETE WORKS - ETA 06/04/20Repair fix panel window used 6.38 clear laminated and used black silicone one plus double sided tape complete****SPOKE WITH REESE WITHEY AND HE ADVISED TO CLOSE OFF WORKS AS COMPLETE - NO TINTING REQUIRED****
MSA-DCA | WA3180347 | The automatic button for the disabled toilet close to Black Swan’s Office is not working. | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 2-Female Toilet LF and Baby Change | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-02 08:59:59 | Pass | Replaced faulty push button to toilet as necessary (had to leave site to source switch) returned door to service and checked over and tested.
MSA-DCS | WA3179792 | Zone 3 - Microwave unable to be reset and It's in alarm mode. | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Apr 2020 | 2020-04-01 10:26:22 | 2020-04-01 08:00:00 | Pass | Attended site and reset zone3 microwave set. All relays tested and operating ok. Realigned set and retested. All tested and working ok. Job complete
MSA-DCS | WA3179794 | Pod - Fire panel is showing unit 4 fault L1455Z1 | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 01 Apr 2020 | 2020-04-01 10:28:33 | 2020-04-01 09:58:00 | Pass | Unit 4 VESDA L14 S5 Z1 replaced filter & batteries
MSA-DCS | WA3179814 | Unit 11, A Wing, Cell 4 has a blocked sink | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Apr 2020 | 2020-04-03 17:00:00 | 2020-04-01 15:20:00 | Pass | Removed food and unblocked sink
MSA-DCS | WA3179822 | WWTP Rear Pond- 80mm water meter not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-22 10:00:00 | Fail | COMPLETED
MSA-DCS | WA3179824 | Gate Control Room, Cardex system is not working (no signal) | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Apr 2020 | 2020-04-01 11:20:54 | 2020-04-01 10:00:00 | Pass | Power cycle KVM , monitor back to normal operation. Job completed
MSA-DCS | WA3179862 | West Admin Building, Security & HR- Air Con not running | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 07:52:16 | 2020-04-01 13:02:00 | Pass | System is running
MSA-DCS | WA3179863 | West Admin Building, Security- CCTV Footage Required from 26/3/2020 Critical Incident | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 07:57:15 | 2020-04-01 16:07:00 | Pass | Downloaded data as per security, converted and provided to security dpt.
MSA-DCS | WA3179870 | Unit 14, D Wing, Cell D5 light switch needs refixing to the frame | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-03 10:00:00 | Pass | Replaced damaged cell switch in unit 14 d5
MSA-DCS | WA3179883 | Unit 14, both bottom landings (A/B) no night lights | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-06 11:30:00 | Pass | Investigated unit 14 night lights. Found and replaced faulty contactor in switchboard
MSA-DCS | WA3179901 | Supply 10 cubic meter skip bin for defective equipment | Casuarina Prison-Stores | GMP-BR- HO | Waste Management | Environmental Services (WM) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 01 Apr 2020 | 2020-04-08 17:00:00 | 2020-05-06 10:13:00 | Fail | two skip bins supplied and picked up.
MSA-DCS | WA3179913 | Pre-release unit- Camera 65 PTZ, PRU not working | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 08:36:05 | 2020-04-03 12:00:00 | Fail | Footage reviewed and cabling checked. At this time quality is not degraded enough to warrant an upgrade.
MSA-DCS | WA3179914 | Pre-release unit- PRU , PA system is not working | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-01 13:30:00 | Pass | Looked into issue and discovered client had reported the voip phone system not serviced by SEME. Emailed security infrastructure to inform them.
MSA-DCS | WA3179916 | Visits Male Prisoner toilet is blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-06 14:00:00 | Pass | Dig up and repair broken sewer pipe. Remove tree roots.
MSA-DCS | WA3180011 | dairy pasturising room wash down tap leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-03 14:15:00 | Pass | Repair leaking pipe work in pasteurising room at the dairy.
MSA-DCS | WA3180026 | Unit 7 H8 Coach roach infestation coming from door frame | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-07 12:00:00 | Fail | Carried out a service for cockroaches in unit 7. There were reports of cockroaches located in cell H8. Residually Sprayed in front of all cell doors and sprayed all plumbing ducts.
MSA-DCS | WA3180053 | kitchen Fault description 2 x Three Phase isolators damaged for cooking bells-see notes | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 10:49:38 | 2020-04-02 10:49:00 | Pass | Replaced 2 broken isolators
MSA-DCS | WA3180137 | Unit 1 B3 Flush Water Leaking internally from the S/S Toilet Pan-see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 11:57:39 | 2020-04-02 11:53:00 | Pass | Unable to complete job due to escort not available. Unblcoked sewer line and toilet
MSA-DCS | WA3180143 | unit 1 B9 blocked toilet - Need Drain Machine | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 12:02:00 | 2020-04-02 09:04:00 | Pass | Unblcoked toilet and sewer line full debris
MSA-DCS | WA3180159 | L1 D2 Damaged Lino Flooring | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 12:17:59 | 2020-05-01 16:15:00 | Fail | Removed damaged flooring, supplied and installed new vinyl
MSA-DCS | WA3180180 | Flickmixer tap has split in spout – leaking water | Boronia Pre-release-AP21 - Prisoner Accommodation House 12 and 13-Ground Floor-House 13 - Kitchen Area | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-02 09:00:00 | Pass | Attended site. Unable to carry out work due to lack of ataff. Attended site. Replaced kitchen sink mixer.
MSA-DCS | WA3180185 | INF (10), office - the ceiling aircon ducts blowing hot in unit 12(sop) & SO office in Health centre | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 12:45:55 | 2020-04-02 14:15:00 | Fail | Condensers have been disconnected by other contractors, possibly due to construction. They will be required to reconnect.Units not running
MSA-DCS | WA3180261 | Reception, office - water foutain coutinues to leak from spout and from lower flexible hose fitting | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-07 10:30:00 | Fail | Replaced cross threaded plastic fitting with brass fitting. Replaced faulty tap and replaced restricted filter. All ok.
MSA-DCS | WA3180275 | CCU (11), C5 - cell alarm not working | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 14:23:34 | 2020-04-01 15:45:00 | Pass | CCU Cell call C5 failed to operate when tested, repaired cell intercom and tested fully operational.
MSA-DCS | WA3180329 | Office kitchen ants in office-kennel building rabbit holes under building | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-07 14:00:00 | Fail | Carried out a service for ants and rabbits at Hakea Prison DDU. Applied ant gel and residually sprayed the internal perimeter of the kitchen. There were reports of rabbits holes under one of the sheds, if problems get worse may have to set up some rabbit traps in the future. Please allow up to two weeks for ants to spread chemical amongst all nests.
MSA-DCS | WA3180331 | INF (10), the whole unit - repair flood lights in infirmary | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-03 13:30:00 | Pass | Repaired faulty lights in infirmary
MSA-DCS | WA3180385 | Infirmary - water leak from ceiling in various areas, causing electrical swtiches to go of | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 01 Apr 2020 | 2020-04-01 19:45:38 | 2020-04-01 15:46:00 | Pass | Domestic water pump controllers failed allowing the system to over pressurize causing a fitting to fail above the Infirmary.
MSA-DCS | WA3180386 | Infirmary - water leak from ceiling in various areas, causing electrical swtiches to go of | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 01 Apr 2020 | 2020-04-01 19:50:11 | 2020-04-02 16:00:00 | Fail | Isolated water logged circuits in infirmary. Returned and drained water and repaired damaged lights.
MSA-DCS | WA3180422 | Zone 10 Perimeter - contestant tamper alarm SITE COSTED | Banksia Hill Detention Centre | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Apr 2020 | 2020-04-01 20:21:17 | 2020-04-01 19:00:00 | Pass | Attended site and investigated the fault.Found corroded wire on microwave transmitter in zone 10.Reterminated wire and conducted test.All back to normal and operational
MSA-DCS | WA3180492 | Wooroloo Prison Farm - Unit 2B - Fire alarm fault | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 21:40:39 | 2020-04-02 10:58:00 | Pass | L3S30 in unit 2B in maint fault. Replaced detector, fault cleared and removed isolation. FIP normal at time of departure
MSA-DCS | WA3648047 | Multiple PTZ cameras malfunctioning, firmware version issue | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 Apr 2020 | 2020-04-07 17:00:00 | 2020-10-02 12:12:00 | Fail | As per report
MSA-DFES | WA3180142 | 1st Floor, Disabled toilet - Toilet seat broken | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 17:00:00 | 2020-04-03 08:15:00 | Fail | Supply and fit new disabled toilet seat in ground floor toilet
MSA-DFES | WA3180238 | Ceiling outside station officers dorm needs repair after water leak | CFRS Fremantle | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 17:00:00 | 2020-04-09 13:00:00 | Fail | Damaged ceiling patched and painted
MSA-DFES | WA3180324 | Fire fighter toilets - between dorm 3 & 4 is not working due to leak | CFRS Osborne Park | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 17:00:00 | 2020-04-02 09:18:00 | Pass | Servicing toilet cistern
MSA-DFES | WA3181183 | Retrospective work order do not attend-EXTERNAL CHECK CONDUCTED | CFRS Midland | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 01 Apr 2020 | 2020-04-01 17:00:00 | 2020-04-01 04:55:00 | Pass | EXTERNAL CHECK CONDUCTED, ALL APPEARS TO BE SECURE. CLEARED BY MAX AT MONITORING.
MSA-DTAG | WA3180167 | Basement, custody centre, Cell 1 - blood around body cell. | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 17:00:00 | 2020-04-01 17:00:00 | Pass | Job completed.
MSA-DTWD | WA3179818 | B Block, Room B102.3- Burst hot water system | East Perth Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-01 13:30:00 | Pass | Carried out replacement of hot water storage unit. Commissioned and tested operation.
MSA-DTWD | WA3179866 | A Block, Room A218- Door handle is not functioning | East Perth Campus | GMP-BR | Building | Doors (BU) | ADVANCED LOCK & KEY | 3 | CLOSE | 01 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-01 14:44:00 | Pass | Re-fix handle to A218 door and lubricate
MSA-DTWD | WA3179943 | A block, room A19 - RCD constantly tripping | Murdoch Campus-Block A | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-02 14:15:00 | Pass | Attended site and signed in. Located A block, investigated fault on B1. Found to be outside water pump for toilets. Isolated and advised staff. Go ahead to replace pump. Emptied water tank. Accessed pipe fittings and disconnected. Removed pump from tank. Picked up replacement pump. Fitted piping to new pump. Installed into tank. Connected to power. Tested operation of toilets on rain water. All okay. Job complete
MSA-DTWD | WA3180084 | block 6 L1 6CF1 Multiple broken light fittings | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-02 15:15:00 | Pass | Attended site and signed in. Located 6CF1. Found half fluros not working. Replaced 10x tubes and starters. All lights working correctly. Tested all okay. Job complete
MSA-DTWD | WA3180087 | Block 13 ground 13G1 Broken support stumps | Thornlie Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-03 12:00:00 | Pass | Replaced corroded steel building stumps with new and re-levelled
MSA-DTWD | WA3180089 | Block 13 ground 13G1-Broken steps | Thornlie Campus | GMP-BR | Carpentry | Staircases, Balustrades and Handrails (CA) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-03 14:30:00 | Pass | Remove damaged tiles and filled with motar as discussed with client
MSA-DTWD | WA3180188 | Block 6 ground metal fab 2-Flashing LED panel in oxy bay | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 01 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-21 15:30:00 | Fail | Attended site and signed in. Located oxy bay. Replaced faulty led panel light. Tested all okay. Job complete
MSA-DTWD | WA3180200 | Block 6 L1 6CF1 broken power point | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 01 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-06 08:30:00 | Pass | Attended site and signed in. Located block 6 classroom. Found gpo behind unit broken. Replaced mounting block and refitted gpo. Tested all okay. Job complete
MSA-DTWD | WA3180282 | Level 2, CRAC units - replace broken belts in CRAC unit | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 17:00:00 | 2020-04-02 10:00:00 | Pass | Returned to site and replaced vbelts on second crac unit.Confirmed both belt drives on crac units working correctly.
MSA-DTWD | WA3180301 | D block, ground level, S/Service - the air con is not working FCU 3 & press button | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 01 Apr 2020 | 2020-04-02 17:00:00 | 2020-04-17 08:00:00 | Fail | Attended site, gained access to D block. Moved required desks out of the way to safely set up ladder and investigate faulty Fan Coil Unit #3. Facilities reported damaged switch button, went to pick up replacement part and returned to site and Replaced damaged innotech start and stop switch. Further tested unit to find that the control fuse has blown. This is due to the fact that the fan motor has tested down to earth. Fan motor has lost power due to old speed controller that is installed into the MSSB. We have bypassed and removed the switch as it is not necessary to operation. Will submit a quote to replace the faulty Fan motor and to upgrade the control fuse to a circuit breaker to improve efficiency. Attended site, removed fan and took deck to totaline for sizing, braf submitted Attended site fitted new fan motor but circuit breaker hasnt arrived yet so need to be booked in to return once part is in Type of fuse cant be replaced by cb but checked amp draws and still running
MSA-DTWD | WA3180319 | Exteriror driveway - remove graffiti on the plant room walls drive entrance | East Perth Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 01 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-02 11:00:00 | Pass | REMOVAL OF GRAFFITI FROM PLANT ROOM WALLS DRIVE ENTRANCE
MSA-MRWA | WA3180342 | ground level toilets - LG - Urinal float intermittenlty faulting | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-03 13:05:00 | Pass | Replaced faulty inlet valve
MSA-MRWA | WA3180379 | Level 2, kitchenette - L2 - replace switch mechanisms in double GPO | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Materials (EL) | AWB Co. | 2 | CLOSE | 01 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-03 08:30:00 | Pass | Attend site and signed in. Replaced faulty DGPO in L2 kitchen. All now working. Informed staff of job completion
MSA-DCA | WA3181068 | Back of Polly Cafe, tap is leaking and top rounded out | Perth Cultural Centre Precinct | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-03 12:30:00 | Pass | Replaced with new tap
MSA-DCS | WA3180684 | ISU, Staff Kitchen- Water filter not working | Banksia Hill Detention Centre | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 02 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-03 08:54:00 | Pass | Replaced uv lamp
MSA-DCS | WA3180710 | Maintenance workshop- 7 pin light switch has sparked | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 07:36:15 | 2020-04-02 11:30:00 | Pass | Replaced switch mechanisms
MSA-DCS | WA3180853 | Unit 2 - D Wing-Blocked sink in unit 2 cell D05 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-02 10:00:00 | Pass | Punch sink, remove trap in duct but unable to clear. Install new trap.
MSA-DCS | WA3180883 | ODP, Rm 1 Sentence Planning Computer Port# 31 is loose and keeps falling out of it's socket | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 08:30:00 | Pass | Re installed damaged data point in ODP room 1
MSA-DCS | WA3180999 | Level 8 - Office RM8.B flickering light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 09:19:28 | 2020-04-02 13:00:00 | Pass | Replaced failed lamps and starters
MSA-DCS | WA3181000 | Cameras 101,103,104,105,107,115 & 117- not showing picture | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 09:25:01 | 2020-04-02 18:00:00 | Pass | Job completed - cameras not showing picture. Investigated cameras in Indigo, found Live Stream 1 connection failed,had to re-establish connection on each camera individually. All cameras are now back on line.Job completed.
MSA-DCS | WA3181023 | Unit 2 outside lower landing hot water not heating | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-06 15:00:00 | Pass | Investigate issues with hot water unit. Remove and clean inline strainers. Test and confirm it was operational and working correctly. Hot...
MSA-DCS | WA3181082 | Bakery - Internal freezer is not getting to a negative temp | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 10:20:35 | 2020-04-02 13:00:00 | Pass | Found evaporator coil iced up, fans still running. Checked outdoor unit and found breaker for defrost heater tripped. Reset breaker and forced on defrost. Defrost operational. Defrosted ice and test ran unit, all ok.Informed that door was found open in the morning and there was also a power surge yesterday.
MSA-DCS | WA3181097 | Unit 13 - B & D cleaning store sink drain pipe has come adtrift and requires reattaching | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-08 12:00:00 | Fail | Pick up parts, remove and replace damaged plug and waste and 50mm trap.
MSA-DCS | WA3181105 | Unit 2 - D Wing Cell D03 sink blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-02 11:00:00 | Pass | Plunge sink to clear blockage and test.
MSA-DCS | WA3181172 | Control room - Gallagher energise fence controller battery low – A3 outter area | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 10:52:03 | 2020-04-09 15:05:00 | Fail | Gallagher energised fence controller batteries supplied and replaced in C1 and D1, removed alarms and load tested ok.
MSA-DCS | WA3181222 | Unit 11 Cell C05 – no water coming from taps in cell sink, shower works fine | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-02 14:02:00 | Pass | repaired leaking tap
MSA-DCS | WA3181229 | Unit 11 Cell C11 – shower dripping continuously | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-02 16:22:00 | Pass | Replaced faulty spindles and repaired shower
MSA-DCS | WA3181238 | Stores - Faulty electrics | Casuarina Prison-Stores | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-14 11:00:00 | Fail | Repaired faulty electrics in programmed store. Disconnected remote access to roller doors.
MSA-DCS | WA3181282 | Unit 14, D1 - replace broken sprinkler head | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Sprinkler Systems (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 02 Apr 2020 | 2020-04-02 16:12:29 | 2020-04-02 16:00:00 | Pass | On arrival found a broken sprinkler head in unit 14Removed broken sprinkler head and installed new oneRefilled sprinkler installationCleared fip
MSA-DCS | WA3181321 | Unit 2, C Wing - Grille jamming and not opening | Casuarina Prison | GMP-BR- HO | Building | Security Doors (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 12:30:07 | 2020-04-02 15:30:00 | Pass | Job completed - Travel to site. Inspect Unit 2, C wing grill. Close limit found to be loose and plunger head broken. Replaced switch. Test operation, all okay
MSA-DCS | WA3181331 | vocational skills office - repair damaged brickwork under window in front of VOC skills workshop | Casuarina Prison | GMP-BR- HO | Building | External Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-10-08 11:02:00 | Fail | REMOVE DAMAGED BLOCKS AND SUPPLY NEW
MSA-DCS | WA3181352 | Vocational Skills, Lunch Room - electrical GPO faulty in kitchen. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-07 08:30:00 | Pass | Replaced damaged gpo in voc skills.
MSA-DCS | WA3181382 | Unit 3, D Wing, Yard Door- Lock jamming up | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 13:14:30 | 2020-04-21 13:15:00 | Fail | Installed lock
MSA-DCS | WA3181385 | Cell 4D - faulty power - not staying on | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-03 12:00:00 | Pass | Investigate power issue, no issue evident
MSA-DCS | WA3181387 | Unit 3, B Wing, Day Room- Lock jamming up | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 13:17:53 | 2020-04-03 12:30:00 | Pass | Serviced lock
MSA-DCS | WA3181511 | Sallyport - the gates are very noisy - the gates are getting progressivly noisy and need some oil | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | AFD Contracting | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 09:45:00 | Pass | 08/04/20 - 09:45Sam Groenveld (AFD) spoke to Senior Officer Josh Mongoo (Roebourne) and discussed the issue. Senior Office Josh Mongoo is happy that this is a normal noise that occurs in that environment and confirmed the work order can be closed out.The work order has been marked as field complete.There are no costs to date.Can you please close out this work order.
MSA-DCS | WA3181570 | BR-external zones 11 & 12 not activating | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 10:40:00 | Pass | Repaired and recalibrated multiple perimeter faults and recalibrated multiple zones.Tested OKJob CompleteParts used:Consumables
MSA-DCS | WA3181614 | Level 8, outside RM8.W - Flickering light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 16:29:53 | 2020-04-03 09:45:00 | Pass | Replaced failed lamps and starters
MSA-DCS | WA3181632 | East Perimeter Microwave Temper/Alarm | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 19:53:22 | 2020-04-03 12:00:00 | Pass | Zone 18 external microwave in constant alarm. Microwave power and alignment voltage ok. Shorted alarm wires to test cable and SM input. Traced fault to cable issue. Repaired cable, tested ok back to Hakea control.
MSA-DFES | WA3181482 | Please attend to rectify the gate alignment when opening & closing – limiters need adjusting | O'Connor Fleet Storage | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 17:00:00 | 2020-04-03 16:00:00 | Pass | Braf submitted
MSA-DTAG | WA3180677 | Hay Street, Lvl 3, Male toilet- Urinal is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Apr 2020 | 2020-04-02 17:00:00 | 2020-04-02 15:15:00 | Pass | Complete
MSA-DTWD | WA3180736 | Block 6, Cabinet Making, Workshop 6D31- problem with power supply to CNC machine | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-06 15:05:00 | Pass | Attended site and signed in. Investigated machines. Needs power altered to run machines. Will need braf to continue. Job not complete
MSA-DTWD | WA3180856 | P Block, Admin- Alarm panel showing low battery | Joondalup McLarty Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 17:00:00 | 2020-04-03 13:30:00 | Pass | Dang Nguyen (02/04/2020) - Work NoteAttend site, was advised door would be unlocked but it was notDang Nguyen (03/04/2020) - Work NoteAttend site, replaced 2x low batteries on DGP 1 & 16, all working ok
MSA-DTWD | WA3180896 | B Block, Library - Student printer station lock is faulty | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-07 09:30:00 | Pass | Repaired door locks B Block - Library
MSA-DTWD | WA3180974 | BLD 826 - electric smoke alarm faulty | Muresk Institute | GMP-BR | Electrical | Materials (EL) | Damian Rak Electrical Pty Ltd | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 17:00:00 | 2020-04-02 11:30:00 | Pass | Replaced faulty smoke alarm
MSA-DTWD | WA3180986 | C & J Compound, south perimeter fence - break i, mesh fench cut | Mandurah Campus (formerly Peel) | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 02 Apr 2020 | 2020-04-03 17:00:00 | 2020-04-02 15:00:00 | Pass | Replaced 3 metre bay of damaged chainmesh fencing
MSA-DTWD | WA3181026 | Vehicle Body Building Faulty 3 phase power points in Material shed | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-06 11:00:00 | Pass | Attended site and signed in. Located block 6 material shed. Removed old 3 phase outlet. Installed 3 phase RCD, new 5 pin 10amp outlet. Installed extra 5 pin 10amp outlet for new saw. Tested and labelled outlets. Job complete
MSA-DTWD | WA3181031 | Vehicle Body Building 3 lights not working in Material Shed | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-06 13:30:00 | Pass | Attended site and signed in. Located block 6 material shed. Found 2x lights out. And poor lighting over saws. Replaced tubes and starters in lights out and replaced fittings over saws. Tested all okay. Job complete
MSA-DTWD | WA3181051 | A block A 354 Power outlet is broken. | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-17 09:10:00 | Fail | Replaced with gpo with neon indicator. Job completed
MSA-DTWD | WA3181151 | Level 2 A Block A 202 stairs Twin tube flouro light burnt out | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-07 14:25:00 | Pass | Attend site. Replaced faulty light fitting with new led in staircase .job completed
MSA-DTWD | WA3181159 | Childcare back door has a faulty door lock | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-06 09:25:00 | Pass | Job completed
MSA-DTWD | WA3181356 | A Block, Room A001 - repair/replace cabinet locks | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-03 10:30:00 | Pass | Replaced cabinet lock
MSA-DTWD | WA3181456 | B block, level 2, B209 - re tube lights not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 02 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 10:33:00 | Pass | Replaced multiple lights out to B209
MSA-DTWD | WA3181565 | C block, West end entry door to customer service is damaged, needs repairing/replacing | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 02 Apr 2020 | 2020-04-07 17:00:00 | 2020-05-25 16:00:00 | Fail | Works are now completed and tinting applied
MSA-DCA | WA3182303 | RO unit in fault-Please contact Pey-Sue on 0466 522 796 for site access | Shipwreck Galleries-Main Building-Ground Floor-Plant Room - In Front of Lift | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-03 16:30:00 | Pass | Attended site. RO plant in fault. Applied tests an checks. Investigation found pump electronic pressure switching module U/S. Returned to site with replacement parts. Removed pump and expansion tank. Removed pressure control and wired in new pressure control module. Reassembled pump and carried out rust treatment to pump base. Carried out air bleed of system. Tested operation. System operating correctly.
MSA-DCA | WA3182422 | chillers are out investigate mechanicle faults | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-03 14:44:00 | Pass | Travelled to site and signed in.Accessed chillers and found all stages tripped on low differential pressure fault.This fault is from low differential pressure of the refrigeration circuit.Found the cause of this is from the cooling tower fans running on constantly causing very low condensor water temps which causes a low differential pressure.Manually turned the fans off and reset the chillers.When i arrived the condensor water temps were at 15 degrees.After the chiller were running with fan off the temps raised to 30 degrees.Spoke to bms tech and advised him of my findings and advised him to investigate why the fans are running on.Had to leave site for a priority 0 at state records so i could not monitor until he had rectified issue.
MSA-DCA | WA3182635 | CRAC unit in fault-see additional notes | State Archives Repository Dianella-Main Building-Ground Floor-AC Plant Room | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 0 | CLOSE | 03 Apr 2020 | 2020-04-03 17:36:22 | 2020-04-03 16:17:00 | Pass | Attended site and found humidifier on fault.Reset and found fault occured again.Found drain valve not opening when required.Removed humidifier bottle and drain valve and cleaned drain valve.Greased internal components of drain valve and confirmed operation.Reassembled humidifier and ran unit up.Confirmed operation of drain valve and humidifier.
MSA-DCS | WA3181692 | Master control room - Personal duress alarm cannot be reset | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Apr 2020 | 2020-04-03 09:30:11 | 2020-04-03 16:39:00 | Fail | Sourced parts, attended site, repaired duress computers but noted these computers are obsolete and are being replaced on another job (WA3182518).This job is complete
MSA-DCS | WA3182133 | Unit 7, C Wing, Cell C10- toilet is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-03 11:00:00 | Pass | Adjust cistern outlet assembly in plumbing duct.
MSA-DCS | WA3182136 | Unit 3, B & D, Cell B03- Vent above sink is leaking water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 13:00:00 | Pass | No leak was found and no cause or evidence of a leak could be found.
MSA-DCS | WA3182142 | Unit 1, B Wing, Cells B9 & B10- Pipes between cells leaking in the water closet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-03 12:00:00 | Pass | Replace cracked Inlet valve in plumbing duct
MSA-DCS | WA3182144 | SHU (9), Cell B3 on East Wing- Obs light are faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 15:00:00 | Pass | Repaired faulty lights in SHU cell b3Waited access for cell
MSA-DCS | WA3182150 | Unit 3, Control Cell Call console has no volume on the cell call system | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-03 12:30:00 | Pass | Reset cell call system from gatehouse server room. All reset and tested volume levels for correct operation. Contacted unit 3 and was advised that volume level was all ok. Job complete
MSA-DCS | WA3182203 | Damaged VSD in pump house | Casuarina Prison | SPA-GR | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-05-29 10:30:00 | Fail | Replaced faulty VSD in pump house for domestic water supply.
MSA-DCS | WA3182230 | unit 13 replace faulty solenoid valve on reticulation | Casuarina Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-29 09:57:00 | Fail | Found 2 damaged solenoids not one, both replaced
MSA-DCS | WA3182231 | Unit 2, A & B Day Room- Blocke drain floor waste | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 08:23:23 | 2020-04-06 09:30:00 | Fail | Attended site for blockage to floorwaste gully. Unable to access due to benchtop being direct on top of waste. Will reattend on Monday.Attended site. Used chemicals to clear blockage. Flushed through to clean and test operation.
MSA-DCS | WA3182252 | Unit 1, urinal is blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-14 14:00:00 | Pass | COMPLETED
MSA-DCS | WA3182260 | Unit 13 - A & C Cell C03 basin is leaking permenantly appears to be rear where the pipes attached | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-06 15:30:00 | Pass | Remove and replace 1/4 turn spindle in plumbing duct
MSA-DCS | WA3182308 | Unit 7, A Wing- Leaking water pipe in roofspace | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-03 10:00:00 | Pass | Remove salty water meter and install new pipe work as water meter is not required.
MSA-DCS | WA3182310 | Unit 2 - D3 Blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-06 10:00:00 | Pass | Plunge Basin to clear blockage and test
MSA-DCS | WA3182312 | Unit 3, C Wing, Cell 06- toilet not flushing correctly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-06 11:00:00 | Pass | Adjust Inlet valve in plumbing duct and test
MSA-DCS | WA3182315 | Unit 1, B Wing, Cell B6 - Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-06 08:00:00 | Pass | Plunge Basin to clear blockage and test
MSA-DCS | WA3182345 | Unit 6, B wing - Main cell door lock is faulty. 3 out of 4 keys will not operate the lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-09 12:30:00 | Fail | Job completed - remove edge capping, remove main lock, service and weld up lock in maintenance workshop. Re install main lock and edge capping and re fit strike plate.
MSA-DCS | WA3182362 | Control room -one of the main monitor screens is turning black intermittently | Boronia Pre-release | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 10:10:37 | 2020-04-08 12:30:00 | Fail | Attended site and replaced monitor 1 with new HDMI extender set. All replaced and tested working ok. Job complete
MSA-DCS | WA3182416 | 4x Twin 36W Fluro lights not working | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Kitchen Store Room | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-14 12:00:00 | Pass | REPLACED FITTINGS
MSA-DCS | WA3182425 | Edvoc 1- No essential power | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 11:05:10 | 2020-04-03 13:00:00 | Pass | Reset em stop
MSA-DCS | WA3182443 | Murchison, Cell A03 - Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-08 12:30:00 | Pass | Replaced broken switch
MSA-DCS | WA3182523 | Unit 1, Cell A5 - Broken GPO | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-06 15:00:00 | Pass | Investigate and replace gpo and plug top in unit 1 cell A5
MSA-DCS | WA3182530 | WWTP drum washer pump not working, no power | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 13:00:00 | Pass | Investigate wwtp drum washer. Found fault in foot pedal and wiring. Source parts. Replace damaged foot pedal and wiring.
MSA-DCS | WA3182531 | Unit 3 - Control Room-TRANSMIT FAILURE NODE:8 NETWORK ERROR | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-06 15:41:00 | Pass | Unit 3 indicating transmit failure node 8, found system indicating network error, tested operating correctly, removed network errors and checked system comms correct. No further action is required.
MSA-DCS | WA3182540 | Unit 4, PRU - houses A to D - Gallagher coms are offline | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 12:18:05 | 2020-05-01 12:00:00 | Fail | Repaired as per work notes.
MSA-DCS | WA3182542 | Unit 4, PRU - intercom offline, PAU side gate | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-06-02 13:14:00 | Fail | Additional checks into faulty intercom unit completed and a serial number discrepancy on the server device table was found. This error was amended and the unit is now full functional. A replacement intercom has been supplied onsite as a critical spare part.
MSA-DCS | WA3182543 | Unit 4, PRU - Mutiple cameras signal lost | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-10-02 12:08:00 | Fail | Completed under LVM Work Order WA3307324
MSA-DCS | WA3182554 | L4 room 4.5 (6) located near Procurement flickering light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-07 13:00:00 | Pass | Repaired lighting in room 4.5
MSA-DCS | WA3182559 | Unit 5, B wing - first hand basin in B wing shower block is loose to the wall | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-03 14:00:00 | Pass | Remove Basin, Tighten Basin bracket, reinstall Basin and fc11 around Basin.
MSA-DCS | WA3182564 | Unit 5, B wing, Last shower on the left - tap wont does not shut off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-03 15:00:00 | Pass | Remove and replace one quarter-turn shower spindle in plumbing Duct
MSA-DCS | WA3182571 | Unit 3, A & C Day Room- Flooring ripped & bubbling | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-09-29 14:30:00 | Fail | DAMAGED FLOORING UPLIFTED & REPLACED
MSA-DCS | WA3182590 | Perimeter - permitrax is faulty | Bandyup Prison | SPA-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Apr 2020 | 2020-04-03 16:50:20 | 2020-04-20 15:25:00 | Fail | Microwave set replaced for new, tested microwave operating correctly, micriwaves alligned and alarms cleared.
MSA-DCS | WA3182602 | Termite activity in skirting – under window | Boronia Pre-release-AM06 - Prisoner Accommodation House 1 and 2-Ground Floor-House 2 - Bedroom 1 | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-06 11:30:00 | Pass | Treated for active termites in skirting of ground floor - House 1 and bedroom 1 in House 2
MSA-DCS | WA3182639 | New Kitchen - Air Con not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 13:39:45 | 2020-04-03 16:10:00 | Pass | System VSDs reset after power surge
MSA-DCS | WA3182649 | Unit 1 C9 Broken Light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 14:00:06 | 2020-04-03 15:30:00 | Pass | Repaired light
MSA-DCS | WA3182650 | Kitchen, Loading Dock Fridge- Broken light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 14:00:49 | 2020-04-08 12:00:00 | Fail | Replaced damaged lights in cool room
MSA-DCS | WA3182651 | Unit 4, Cell D8- Broken light switch | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 14:04:03 | 2020-04-03 15:30:00 | Pass | Replaced light switch
MSA-DCS | WA3182652 | Unit 1, D9 - CCTV Camera flickers on and off & has a scratched cover | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 14:01:38 | 2020-04-20 12:50:00 | Fail | Checked Unit 1 camera, camera found recordings OK, checked workstation OK. Installed replacement network switch at gatehouse to better accommodate network traffic.Camera lens scratch is being repaired on Job WA3202563.Parts Used:1 x Network Switch2 x SFP's
MSA-DCS | WA3182653 | Unit 1 B10 Toilet Loose And coming Away From The Wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 14:03:31 | 2020-04-03 16:08:00 | Pass | Removed old silicone and re siliconed base and floor
MSA-DCS | WA3182686 | Unit 13, A & C, Regithermic oven - has a blockage in the drain pipe | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 03 Apr 2020 | 2020-04-04 14:41:16 | 2020-04-06 14:00:00 | Fail | Remove & clean blockage. Refit drain & test ok
MSA-DCS | WA3182736 | Control Room Gatehouse DCP desk screen control 2 screen is fading out to grey & shaking, not clear | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-05-26 22:34:00 | Fail | Returned monitor to site stock.Replaced keyboard, mouse and speaker
MSA-DFES | WA3182211 | Rear engine room door, rail is bent and needs repair | Kensington (old) | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 03 Apr 2020 | 2020-04-06 17:00:00 | 2020-05-12 11:30:00 | Fail | 06/04/202-the RH vertical track bent, hit by fire truck. Door jammed in closed position. Unjammed door and opened it as per station officer's request.Left door in open position and motor isolated. New track required.12/05/2020. Removed damaged guide. S&I new guide and straightened brackets. Carried out full test of operation, all ok.Full test and inspection of door components completed prior to leaving site.
MSA-DTAG | WA3182630 | Staff Entrance Door difficult to open door | Perth Children's Court | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-07 09:00:00 | Pass | DOOR ASSESSED, IN WORKING ORDER
MSA-DTAG | WA3182693 | Special Clean required in cell 1 – Accused wipe/spit nasal secretions over the cell floor and walls | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 03 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-03 22:00:00 | Pass | Cleaned cell
MSA-DTAG | WA3182700 | Ground level, Custody Cell 2 - lock only opens and closes with the key. | Midland Courthouse | GMP-BR-HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 03 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-06 09:00:00 | Pass | job completed - adjust hinges and service lock.
MSA-DTAG | WA3182716 | Bio clean Cell 1 - Accused person has suspected COVID-19 | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 0 | CLOSE | 03 Apr 2020 | 2020-04-03 19:44:12 | 2020-04-06 08:40:00 | Fail | Job completed as per work order
MSA-DTWD | WA3182070 | A Block, G Floor, Next to A009(external stairwell)- Broken external door lock | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 0 | CLOSE | 03 Apr 2020 | 2020-04-03 11:04:38 | 2020-04-03 08:50:00 | Pass | Job completed - replaced lock to stairwell by A009
MSA-DTWD | WA3182076 | Level 1, A Block, West Male- Toilet flush button is not working | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-16 11:30:00 | Fail | Complete
MSA-DTWD | WA3182092 | E Block, Room E204- Lights not working | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 03 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 13:59:00 | Pass | Inspected lights to E204. All working g fine .job completed
MSA-DTWD | WA3182215 | Carpark 2 walkway at block 10 White ant infestation in trees | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-08 10:00:00 | Pass | Carried out a service for termites at Thornlie Tafe. Located three trees termite activity in the back carpark Drilled and injected all three trees and injected around the base of the trees.
MSA-DTWD | WA3182244 | Block 1 1G31 Windows won’t stay open | Thornlie Campus | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-15 14:30:00 | Fail | Installed new window sashes, windows now operating correctly
MSA-DTWD | WA3182299 | A block, ground level, emergency stairwell - central external emergency door jamming in door frame | Joondalup Kendrew Campus | GMP-BR | Building | Doors (BU) | M Construction (WA) | 1 | CLOSE | 03 Apr 2020 | 2020-04-06 17:00:00 | 2020-05-12 12:41:00 | Fail | Job complete
MSA-DTWD | WA3182500 | Room B19 metal covered bench top that is rusted and needs repairing. | Murdoch Campus | GMP-BR | Furniture | Outdoor Furniture (FU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-09 14:30:00 | Fail | Repairs to benchtop carried out
MSA-DTWD | WA3182689 | A block L2 lift lobby plant room fcu not working | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-06 16:00:00 | Pass | Attended site, gained access to FCU. Isolated unit andsafely locked out isolator. Found that 2.5 amp fuse hasblown. Went to wholesaler to get new fuse. Replaced andtested for a while. Tested with amp clamp when unit wasin operation and it pulled 0.2 amps which leaves 0.5 ampsfor the unit to operate safely. Tested again andre-fitted cover to unit.All operational
MSA-MRWA | WA3182570 | Ground, Compactus area - flickering light please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 2 | COMP | 03 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-06 08:47:00 | Pass | Replaced the tube with a new one
MSA-DCS | WA3182846 | All kitchen security cameras are frozen | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Apr 2020 | 2020-04-04 15:09:19 | 2020-04-04 12:15:00 | Pass | cameras are under warranty with Honeywell. Advised staff & PFM to contact Honeywell to rectify fault
MSA-DCS | WA3182909 | Hakea-Melaleuca Prison - Unit 11 - Cell A1, 2, 15 and 16 and C5 - Blocked toilet | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Apr 2020 | 2020-04-05 16:06:08 | 2020-04-05 15:23:00 | Pass | Cleared blockage to unit 11, investigate issues to pump pit
MSA-DTAG | WA3183159 | Retrospective WO - 1903, Basement, Security office - Cameras are offline due to power outage | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 04 Apr 2020 | 2020-04-04 11:14:29 | 2020-04-04 18:00:00 | Fail | All systems down due to electrical works on site. UPS rebooted but PC needs to physically be turnedon. Rebooted everything, Custody Basement & Entry Security. Tested all good
MSA-DCS | WA3182957 | West Kimberley Regional Prison- Unit 1- House 2- Ups failure- fire door not secure | West Kimberley Regional Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Apr 2020 | 2020-04-05 16:44:44 | 2020-04-19 15:26:00 | Fail | Found controller had lost its configuration, reloaded correct software and tested inputsConfirmed all operation
MSA-DCS | WA3183000 | Banksia Hill Detention Centre- SITE COSTED Blocked tolet in cell B1 in Yeeta unit | Banksia Hill Detention Centre | WSM-BR-SITE | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 05 Apr 2020 | 2020-04-05 16:51:35 | 2020-04-05 14:05:00 | Pass | Unblock WC
MSA-DCS | WA3183038 | Bandyup Prison - Unit 1B - Blocked drains causing sewage overflow. | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 05 Apr 2020 | 2020-04-05 19:42:39 | 2020-04-05 17:50:00 | Pass | COMPLETED
MSA-DCA | WA3183327 | Door underneath new museum access ramp/opposite State library Pond - Key has snapped off in barrel. | Perth Cultural Centre Precinct | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-05-06 09:35:00 | Fail | Gain entry to door underneath new museum ramp and install temporary key barrel. Need to return when parts arrive from factory.Installed Kaba cylinder and supply 2x registered Kaba keys
MSA-DCA | WA3183496 | AHU 5-fan motor shaft is moving in and out please investigate | Perth Concert Hall-Main Building | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-30 12:00:00 | Fail | LVM job raised
MSA-DCA | WA3184020 | Tap continuously running water -see notes | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 1-Male Staff Change | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 11:10:00 | Pass | 1/4 turn taps constantly leaking. Unable to repaired. Replaced taps in both sinks with normall taps(no 1/4 turn with ceramic spindles)
MSA-DCA | WA3184033 | Studio Underground corridor SU Dressing Room #7 Tap continuously dripping water | State Theatre Centre (Heath Ledger Theatre) | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 09:02:00 | Pass | Rewashed taps in #7 (both sinks)
MSA-DCS | WA3183126 | Need locksmith to fix a key barrel in the key room | Wooroloo Prison Farm-Staff Office | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 06:47:40 | 2020-04-07 13:00:00 | Fail | Cell Lock Unit 3 /34 Damaged New Cell lock fitted
MSA-DCS | WA3183147 | Front gate, prison side door - door closer arm broken SITE COST | Hakea Prison | WSM-BR-SITE | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 11:04:05 | 2020-04-06 10:45:00 | Pass | replaced door closer arm
MSA-DCS | WA3183181 | Health Centre, room 4 & 5 - sinks not draining | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-09 09:00:00 | Fail | Unblocked outside drain
MSA-DCS | WA3183183 | Visits, toilet - drain is clogged | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-09 13:10:00 | Fail | unblocked toilet
MSA-DCS | WA3183185 | Unit 13, tea room - Light in hallway between tearoom and control not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 09:30:00 | Pass | Investigated faulty light in unit 13. Picked up replacement parts, repaired and test fitting
MSA-DCS | WA3183191 | Unit 5, D wing - shower lights not working (keeps tripping) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-08 11:30:00 | Pass | Repaired faulty lights in unit 5 d wing
MSA-DCS | WA3183247 | Unit 6, B & D Wing, Cell D03- Toilet is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-06 14:30:00 | Pass | Replace faulty Inlet valve and install a 20 mm stainless steel wrap on a badly corroded leaking pipe
MSA-DCS | WA3183251 | Jeelia, A wing - Drains blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-09 11:05:00 | Pass | Unblocked several drains in a wing
MSA-DCS | WA3183253 | INF (10) - toilet in the prisoner disabled bathroom is loose at the base. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 14:30:00 | Pass | Remove loose toilet and reset toilet pan to the floor.
MSA-DCS | WA3183256 | Garments - water leaking in prisoner toilets from cistern | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-06 09:00:00 | Pass | Adjust cistern push button assembly in plumbing duct
MSA-DCS | WA3183257 | Unit 5 Cell A14 GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-06 15:30:00 | Pass | Replaced broken gpo
MSA-DCS | WA3183259 | Unit 4, C Wing, Cell C06- toilet cistern continues to run | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-06 13:00:00 | Pass | Remove and replace faulty Inlet valve in Cistern
MSA-DCS | WA3183263 | Unit 4, B & D - knobs on Regi oven broken/looose | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 09:05:00 | Pass | Fit 2 new knobs to unit
MSA-DCS | WA3183270 | Bakery, workshop - Berto dough Mixer ceased operation | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-15 14:45:00 | Fail | 15/04/2020 - Called as requested to the mixer ceasing. Found the spiral belt loose so made good tested all ok.
MSA-DCS | WA3183275 | Unit 13, A & C - floor lifting, tripping hazzard. | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-06-22 10:26:00 | Fail | SUPPLY AND INSTALL NEW STUDDED RUBBER FLOORING
MSA-DCS | WA3183277 | Unit 13, A Wing, Cell A11- hand basin is draining very slowly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-08 13:31:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test
MSA-DCS | WA3183278 | Unit 3, B wing, cell B09 - hand sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-06 12:00:00 | Pass | Plunge sink to clear blockage and test
MSA-DCS | WA3183279 | Unit 14, Cell A1 - Blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-08 09:00:00 | Pass | Plunge Basin to clear blockage and test
MSA-DCS | WA3183282 | Unit 14, Cell D05 - Wash basin tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-08 10:00:00 | Pass | Remove and replace 1x quarter turn spindle in plumbing duct.
MSA-DCS | WA3183284 | Unit 1, B13 - Blocked toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 08:22:38 | 2020-04-06 12:15:00 | Pass | Clear blockage to unit 1 b13
MSA-DCS | WA3183335 | Unit 5, Passage- 2x Broken lights | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 10:00:00 | Pass | Replaced faulty lamps and left spares onsite
MSA-DCS | WA3183338 | Unit 3, Cell B10- Outside of cell broken light switch | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 09:00:00 | Pass | Replaced faulty light switch
MSA-DCS | WA3183345 | Gate house, kitchen - hot water urn over flowing (eletrical fault) | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-09 10:30:00 | Pass | Repaired urn
MSA-DCS | WA3183347 | Unit 1, A8 - broken GPO | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 08:50:58 | 2020-04-08 08:00:00 | Fail | Replaced damaged GPO and tested cell
MSA-DCS | WA3183376 | Unit 3 cell 68 – Door handle is stiff to turn and the tongue doesn’t fully retract | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 13:50:00 | Pass | Unit 3 /68 - Cell lock is stiff and difficult to operate New lock fitted - keyed to prisons key system
MSA-DCS | WA3183405 | Gascoyne, A4 - toilet seat damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-09 12:15:00 | Pass | Replaced damaged toilet seat
MSA-DCS | WA3183414 | Jeelia, A wing - Airial face plates damaged and faulty for all cells | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Sapio Pty Ltd | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-21 10:30:00 | Fail | Job completed - Replaced Jeelia A-Wing Units TV Points and cable leads. All tested OK.
MSA-DCS | WA3183436 | Level 8, 8.53 - flickering light globe | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 14:00:00 | Pass | Repaired lighting near W8.53
MSA-DCS | WA3183444 | ISU, D Wing- Shower lock is jammed and wont open SITE COST | Banksia Hill Detention Centre | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 13:44:42 | 2020-04-06 11:15:00 | Pass | replaced lock.
MSA-DCS | WA3183471 | Unit 4, PRU House A, B C & D- offline | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 17:58:41 | 2020-04-06 11:30:00 | Pass | Fibre modems reset but did not resolve issue. Optic fibres for Ethernet and camera 42 repatched to exclude suspected fibre fault. After 5 minutes communications restored and both Ethernet and camera 42 online. Fibre testing to be completed later on another job and potentially some hardware upgrades will follow.
MSA-DCS | WA3183473 | Control Unit 15 & 16- offline | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 18:02:05 | 2020-04-06 12:30:00 | Pass | Issue resolved and confirmed after fibre repatching to avoid suspected fibre fault which is to be further investigated on a different work order.
MSA-DCS | WA3183490 | Outcare - The Whole Unit-Resett door lock faulty. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 10:00:00 | Pass | Job completed - On site replace latch, spindles and handles with scar plate to cover existing holes
MSA-DCS | WA3183498 | unit 5, C wing - the porcelan component of toilet is cracked, may require full replacement | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-14 10:00:00 | Fail | Remove and replace cracked toilet, alter pipework to suit. Clean up and dispose of rubbish.
MSA-DCS | WA3183502 | Unit 1, D wing - reading light flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 08:30:00 | Pass | Repaired faulty lights in unit 1 d wing
MSA-DCS | WA3183518 | Cyrenian House - sink, no water | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 10:32:34 | 2020-04-06 13:56:00 | Pass | Serviced faulty valves isolating cyrenian house.
MSA-DCS | WA3183538 | Laundry - Dryer #5 not working properly | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 10:49:12 | 2020-04-06 14:10:00 | Pass | Drum rubbing against front cover. Dropped rear of drum so drum moves backwards when running. Test OK
MSA-DCS | WA3183541 | Recreation - Basketball & Oval lights timing needs to be changed to an earlier time | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 09:30:00 | Pass | Reprogrammed timers for oval and court lights
MSA-DCS | WA3183546 | Cabinet shop - panel saw not working properly | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Power Tools (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 09:30:00 | Pass | Panel saw faulty. Check saw & controls. Found limit switch full of dust, changed switch. Ran cycle, all working correctly.
MSA-DCS | WA3183549 | Unit 1 POD 3 Kitchen & Bathrooms exhaust fans not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-09 10:30:00 | Pass | Replaced 7x exhaust fans in ablutions block
MSA-DCS | WA3183554 | Orchid Pump Irrigation settings not working properly | Wooroloo Prison Farm | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-05-15 10:00:00 | Fail | Orchid Pump system faulty. Check control panel & valves. Service solenoid valves & flow valves. Repair outlet from relief valve. Adjust valve opening times for each filter. Report to staff.
MSA-DCS | WA3183564 | Perimeter, Various- Multiple night lights been reported not working (zone6-8-11-17) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-21 11:00:00 | Fail | Repaired perimeter lights
MSA-DCS | WA3183566 | various units pathway-Multiple pathway lights are not working (lenard-turner-skate park area) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-05-13 12:30:00 | Fail | Repaired lights
MSA-DCS | WA3183604 | control room monitor 55 coming up with faults not working-SEME on site | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-07 11:42:00 | Pass | Investigated CCTV display issues reported by officers, found monitor 55 and failed and rear video-wall computer was not functioning correctly.Sourced replacement display and replaced monitor 55. Repaired software faults with rear video wall computer. Tested OkJob CompleteParts used:Wisenet 19" display (PFM/Prison Stock)Prison stock replaced with new
MSA-DCS | WA3183635 | Unit 5, C wing - fire system pipe leaking in ducking (40/50mm pipe) | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-16 07:00:00 | Fail | drained down system - Replaced leaking pipework - refilled system and check leak, all ok
MSA-DCS | WA3183642 | OPD, toilet - handle lock broken | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-09 14:00:00 | Pass | Job completed - replacd handle, face plate screws and install dor stop
MSA-DCS | WA3183645 | ground near back door & conference room-Intercom outside is corroded & needs replacing-see notes | Rockingham Justice Complex | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 15:15:00 | Pass | Checked intercom unit and little bit of weathering evident. Checked cable and copper is all OK. Reterminated cabling & tested. All in working order.
MSA-DCS | WA3183675 | Front Gate & Inner sallyport doors not functioning correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 12:16:00 | 2020-04-06 17:00:00 | Pass | 06/04/20Tighten bolts on limit switch mount
MSA-DCS | WA3183712 | Unit 9 Cell B5 Lock is broken, prisoner is stuck in the cell | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 16:26:57 | 2020-04-08 14:45:00 | Fail | Replace personal lock parts required. Return and supply and install replacement hinges
MSA-DCS | WA3183714 | Gate House - Control Room-Microwave D4 constantly alarming | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 15:30:00 | Pass | Rectified issue with transmitter end, repaired and fully alligned utiliaing two technicians for allignment
MSA-DCS | WA3183828 | Yeeda, Cue- Smashed window on entry door (approx 600x600) | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 11:30:00 | Pass | reglazed
MSA-DCS | WA3183829 | SOG Base - blocked male toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 13:16:02 | 2020-04-06 14:45:00 | Pass | Cleared blockage to male WC
MSA-DCS | WA3183838 | Bakery, Workshop - freezer keeps tripping out | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 13:20:40 | 2020-05-27 11:09:00 | Fail | Replaced fuse system is now running but will require new heaters asap.27/5/2020,isolated system and replaced heaters.
MSA-DCS | WA3183869 | Unit 3 Abultion near cell 50- lights not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-09 12:30:00 | Pass | Replaced 4x weather proof LED battens in adlutions block
MSA-DCS | WA3183870 | from medical centre through out site rat infestation-see notes | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 13:35:43 | 2020-04-07 01:00:00 | Pass | Carried out a service for rodents at Hakea Prison Medical Centre. There were reports of rodents located throughout the medical centre. Installed four fully baited rodent stations throughout. Will inspect and replenish the stations once a fortnight.
MSA-DCS | WA3183932 | Macerators in fault, pump 2 in overload alarm. Effluent tank at limit | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 13:56:52 | 2020-04-08 16:30:00 | Fail | job had 3 faults with the 1 job
MSA-DCS | WA3183942 | Unit 4, J Block, Isolated block- shower taps leaking into wall | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 14:20:44 | 2020-04-08 14:00:00 | Fail | Carried thorough investigation into leak causing water damage to cabinets. Replaced spindles to 3 x shower sets. Unable to isolate water to unit 4. Had to isolate entire prison.Recommend locating and replacing valves to all units.
MSA-DCS | WA3183963 | Unit 4, PAU Fence cowling/alarming - fault not showing at main gatehouse | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-15 10:55:00 | Fail | All field modules reset and alarms settled. If continues new product to be tested will recommended
MSA-DCS | WA3183969 | Unit 4, PAU alarms only showing at the main gate - fence zone 3,7,8,9&10 always in alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-14 13:00:00 | Fail | Unit 4 alarms checked in both MED and PRU control rooms and functioning. Some zones were shunted and it is possible some confusion or miscommunication has occurred.
MSA-DCS | WA3184009 | DDU- Bee hive near gutter closest to carport | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-07 15:00:00 | Pass | Carried out a service for bees at Hakea Prison DDU. There were reports of bees located in the gutter. Upon further inspection bees were located and thoroughly dusted.
MSA-DCS | WA3184115 | unit 1 emergency prisoners have smashed plumbing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 20:24:11 | 2020-04-07 16:00:00 | Fail | Assess damage after Riot. Pick up all materials required. Make all repairs required to get the unit operational
MSA-DCS | WA3184124 | Zone 8 Cowling alarm activate and Zone 16 fence alarm not activating | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 21:11:34 | 2020-04-06 20:30:00 | Pass | Zones 1 and 16 failed to operate during zone testing, zone 16 required calibration, calibrated and tested ok, zone 1 required cabling adjustment, adjusted functioning correctly. Zone 8 has been fulse activating tested no lonher fulse activating checked registering the correct 1Mohm at controller reset controller and tested fully operational.
MSA-DCS | WA3184135 | Melaleuca - Control Room - Sally Port outer external door is flashing red on screen as not secure | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Apr 2020 | 2020-04-07 01:23:44 | 2020-04-07 01:00:00 | Pass | Afterhours callout . Attended site and found sallyport door showing open when door was closed. Investigated and found to be an interlocking issue when system was in night mode access only. Reconfigured interlocking groups and reset system. All tested and working correctly . Door showing sealed. Job complete
MSA-DFES | WA3183951 | ground information rescourses door is coming off the frame | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-07 10:00:00 | Pass | Resecure door frame to free up door operation
MSA-DFES | WA3183953 | ground information rescourses door mech handle is not securing shut | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | SONTEC WA PTY LTD | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-07 10:10:00 | Pass | 7/4/20 - Dylan ParslowFound spring inside mortice lock broken.Replaced spring and tested.All working ok.Approved by Brendan Ryan
MSA-DFES | WA3184760 | Retrospective work order do not attend : EXTERNAL CHECK CARRIED OUT-see note | VFRS Mandurah | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Securex Security Systems & Services | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-06 11:27:00 | Pass | EXTERNAL CHECK CARRIED OUT. DOOR FOUND UNSECURE. UNABLE TO SECURE AS NO KEYS HELD FOR SITE. NO PERSONS FOUND ONSITE. MONITORING ADVISED AND CLEARED PATROL FROM SITE - BEN
MSA-DTAG | WA3183207 | Control room - Cameras are down, no visual | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 11:48:54 | 2020-04-06 10:00:00 | Pass | Job completed - Attended site. No SAT cameras at Control Room Level 10. Optic switch offline, reset switch and checked, all OK
MSA-DTAG | WA3183213 | Control room - unable to open doors remotely via unison | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 11:53:58 | 2020-04-06 10:30:00 | Pass | Unable to open doors at SAT from Level 10 DMJC.Reset optic fibre switch, all ok.
MSA-DTAG | WA3183387 | Intercom not working again - continuously beeping noise | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-06 11:00:00 | Pass | Reset network switch
MSA-DTAG | WA3183545 | **Retrospective work order** No power in court rooms 6 & 7 due to outage | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 0 | CLOSE | 06 Apr 2020 | 2020-04-06 10:00:00 | 2020-04-06 09:00:00 | Pass | Restored power to courts 6 and 7 and fixed lighting near court 2
MSA-DTAG | WA3184054 | L1 male toilet Internal toilet door - Wall panel on the top hinge to the door has cracked. see note | Midland Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-06-08 08:45:00 | Fail | REPLACE 3 TILES TO ALLOW DOOR TO CLOSE PROPERLY
MSA-DTAG | WA3184110 | L8 court 82-The door return has come off the secure entry door | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-07 08:15:00 | Pass | DOOR CLOSER RE-INSTALLED
MSA-DTWD | WA3183177 | Level 2, FIP Panel - Fault on FIP Panel | Perth Campus B5 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 06 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-06 10:00:00 | Pass | Attended site 6th April FIP in alarm Replaced D38 detector / smoke and base addressableReset FIPall good on leaving site
MSA-DTWD | WA3183367 | T block, level 1, room T 110 - door not locking door frame not alighning | Joondalup McLarty Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-06 13:30:00 | Pass | Attend site Locate T block and door Inspect door Door has large gap on leading edge Mortice latch is sitting above striker plate opening in frame by 15mm Different colour perspects on door indicates door may have been used from another location hence the latch sitting so high above striker plate hole Got tools Spread top hinges to bring door downMoved a bit Still need to drop door 10mm to get it to latch and be lockable Remove door from hinges Mark and chisel out hinge edge Rehang door and fix to hinges Test door Door is latching correctly and lockable Clean up Fill out paper work
MSA-DTWD | WA3183644 | T Block, Sewer Pump has a fault | Murdoch Campus | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 06 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-09 14:59:00 | Pass | break up and pump down waste
MSA-DTWD | WA3183980 | Level 4, Plant Room- Chiller staging fault | Perth Campus B2 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 16:29:00 | Pass | Chris Spadak. Attended site and carried out investigation. 7/4/20. Chiller stage B fault reset for oil pressure alarm. Monitored operation.Chiller 1 flow faults active, switch checks and was ok, PO raised for Icon logic controls to attend and investigated fault with chiller staging. 9/4/20Returned to site with Icon logic. Rectified staging control issues on chillers. Tested all stages and completed paperwork
MSA-DTWD | WA3183984 | Level 2, CRAC Unit - Operation fault | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-05-01 16:09:00 | Fail | Traveled to supplier an collected new filters. Traveled to site found parking signed in and collected keys. Completed SWMS doc gained access to comms room and removed and replaced old filters. Checked for air flow through the 2 crac units. All ok. Old filters removed from room.
MSA-DTWD | WA3183988 | Plant room, level 1, carpark - Lock to Transformer room WP00089 code appears jammed | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 06 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-08 11:35:00 | Pass | Check lock to transformer room 0 Site to organize Western Power to open as room is high voltage
MSA-MRWA | WA3183242 | Level 7, room 721 - Flickering light, please remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 06 Apr 2020 | 2020-04-06 17:00:00 | 2020-04-06 09:45:00 | Pass | Replaced tube with new
MSA-MRWA | WA3183673 | L1 SiPass Server not operating as required, please attend and remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | General Electrical (EL) | Siemens Ltd | 1 | CLOSE | 06 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-06 14:50:00 | Pass | Trish has found that she can see the recently added cardholder records when logged in on one sipass machinebut not another.Logged in to card printing sipass machine and also the server machine. Completed audit trail report.Can see where Trish has added the new record a few times earlier today.Found that the search being performed was not showing records that don’t already have a card number allocated.This search type is selected from a drop box of items. This must have changed after the sipass crashthat occurred in the past few days.Selected a different search type that shows all records and the recently added records are now visiblefor Trish.
MSA-DCA | WA3184255 | Heating water pump 1 is leaking water heavily. | Collection and Research Centre Welshpool-Bulk Wet Store-Ground Floor-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 07 Apr 2020 | 2020-04-07 17:00:00 | 2020-04-17 11:30:00 | Fail | Completed repair works as per approved BRA and as per attached work logs. System operating correctly.
MSA-DCA | WA3184669 | External door to courtyard, door is catching frame will not close - Security issue | Art Gallery of WA - James St - Centenary Gallery | GMP-BR | Building | Doors (BU) | ICS Australia | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-07 16:00:00 | Pass | Door not closing. Planed door down to fit.
MSA-DCS | WA3184192 | The inner Visitors air lock door in Gate house is not connecting with the lock to secure it. | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 07 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 13:45:00 | Pass | inspected door no fault found.
MSA-DCS | WA3184202 | Zone 13 TX Tamper Open Circuit. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-08 18:26:00 | Pass | Disconnected tamper circuit and used resistor and confirmed alarm has cleared, connected first PE beam in stack of 5, found corrosion on the back, Replaced cable and tamper switch from 5M of 6 core from van stock Alarm now sealed.Tested by removing cap and confirmed alarm activated
MSA-DCS | WA3184205 | Camera 6 Failing. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Apr 2020 | 2020-04-15 17:00:00 | 2020-06-25 16:30:00 | Fail | Job complete
MSA-DCS | WA3184208 | MDAS No Network Connection | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 14:07:00 | Pass | 12vdc power supply failed for network switch.Replaced with power trans 12vdc 3 amp from van stock.Tested communiactions and confirmed operation
MSA-DCS | WA3184209 | EC 14 Tamper Open. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-07 16:00:00 | Pass | Construction in progress,Tested tamper switch and confirmed operational
MSA-DCS | WA3184266 | Bakery freezer lights are tripping out circuit breaker on switchboard .turning off freezer | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 07:55:05 | 2020-04-07 10:30:00 | Pass | Replaced faulty lights in bakery freezer.
MSA-DCS | WA3184276 | Unit 3 Cell B11 Bottom bed panel broken & pushed in | Hakea Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 08:09:45 | 2020-05-01 11:00:00 | Fail | NEW PANEL INSTALLED
MSA-DCS | WA3184294 | Security Area - Issue with live camera feed in the Board room with the laptop & Board Room keyboard | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-14 15:30:00 | Pass | Found Laptop PC now unable to see cameras from a number of units. Suspect IP range for Keywatcher changed (primary use of laptop). Accessed cameras on the system not visible to the laptop and opened the subnet mask to provide the required access. Confirmed all cameras in GLU visible to Indigo laptop workstation.
MSA-DCS | WA3184306 | Unit 1, B Wing shower- light is broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 08:32:16 | 2020-04-07 14:00:00 | Pass | Repaired faulty lights in unit 1 showers
MSA-DCS | WA3184312 | Unit 1, Control Room- Windows broken | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 07 Apr 2020 | 2020-04-07 12:36:45 | 2020-06-30 15:00:00 | Fail | windows re glazed
MSA-DCS | WA3184317 | Unit 1, B Wing Cleaning Store- Lights damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 08:42:51 | 2020-04-07 11:30:00 | Pass | Repaired faulty lights in unit 1 store
MSA-DCS | WA3184325 | Unit 1, B & D Dayroom- Pantry light damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 12:00:00 | Pass | Repaired faulty lights in unit 1 day room
MSA-DCS | WA3184331 | U2, H1 C4- loose reed switch | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-19 18:20:00 | Fail | Checked all rees switches in unit 2 ans re-secured them
MSA-DCS | WA3184333 | U2 H3- external cell call not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-19 22:11:00 | Fail | Cell call had visible water damage.Replaced and resealed CI-CC used from site stock
MSA-DCS | WA3184334 | Cameras 226,203,51,47 &45 not functioning | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-19 15:50:00 | Fail | Camera 226 open job WA3089039Camera 45 open job WA2876755Checked cameras found them online on Maxpro, but offline on Indigo,Found encoder rack showing power low alarm.Replaced 2x Sinpro IV-11X00026-02 from site stock
MSA-DCS | WA3184338 | Unit 1 check fire service for damage/check sprinkler system | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Sprinkler Systems (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 08:52:15 | 2020-04-14 10:22:00 | Fail | Checked over the fire system to make sure it was fully operational after the valves had been tampered with
MSA-DCS | WA3184340 | Unit 1, A Wing - Safe cell Camera is faulty | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 08:53:39 | 2020-04-07 15:30:00 | Pass | Electrical power had been shut off due to prisoner disturbance yesterday. All U1 cameras offline. Restarted Indigo and powered up the cameras. Plugged keyboard, monitor and mouse directly into the Indigo workstation to log into Control Centre and setup the camera view screen. Tested ok.
MSA-DCS | WA3184354 | Control room - No picture on cameras 46, 47, 48, 49, 50, 65, 66, 67 | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 09:04:43 | 2020-06-24 14:55:00 | Fail | Reported multiple cameras not working in admissions area. Traced fault to analog fibre modem link between admissions and gatehouse.Parts are no longer available for analog system. Installed digital encoders in admissions area to enable local viewing and recording at the gatehouse. Officers in the gate control room and view cameras on EBI/DVM system.Analog system is being upgraded to digital during a project currently in progress.Job CompleteParts used:SEME StockAXIS Blade encoder chassis2 x Four chanbnel AXIS Blade encoders P7224
MSA-DCS | WA3184363 | Unit 1 - Day Room Dayroom power points damaged/repair/B/D Dayroom | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 09:09:03 | 2020-04-07 12:30:00 | Pass | Replaced damaged gpos in unit 1 day room
MSA-DCS | WA3184396 | PRU P2 multiple intercoms off line - SEME on site | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-06-18 14:02:00 | Fail | job to be invoiced at costs to date
MSA-DCS | WA3184448 | SOG base admin air con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 09:50:52 | 2020-04-08 16:11:00 | Fail | Installed new time clock
MSA-DCS | WA3184481 | Bakery - Workshop-The Sortoriva dough mixer is squeeling and shuddering. | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 09:59:02 | 2020-04-22 15:30:00 | Fail | 15/04/20 - Called as requested to the mixer noise. Found the deflect cap loose will require a special Allen key to remove the cover trim , glue then reassemble. 22/4/20 - Altered deflection cap and glued.
MSA-DCS | WA3184494 | Recreation Gym- fans not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 15:00:00 | Pass | Replaced ceiling fan in gym
MSA-DCS | WA3184580 | Reset Building Demountable toilet-Toilet bowl seal leaking when flushed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 10:30:02 | 2020-04-07 13:45:00 | Pass | Removed toilet replaced pan rubber reinstalled toilet
MSA-DCS | WA3184583 | Unit 3 A Wing Showers main drain blocked water going into yard | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-14 13:30:00 | Pass | Drain machine to unblock
MSA-DCS | WA3184600 | kitchen loading dock Lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-05-06 15:00:00 | Fail | Repaired lights
MSA-DCS | WA3184603 | Unit 9 Cell D14 Inside light switch is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 10:35:29 | 2020-04-07 15:00:00 | Pass | Repaired light switch
MSA-DCS | WA3184607 | Unit 1, Cell B6- Main lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 10:34:58 | 2020-04-08 11:00:00 | Fail | replaced lock.
MSA-DCS | WA3184610 | Blast chiller 2 Blast Chiller not switching off. Switch brocken | Hakea Prison | GMP-BR- HO | Refrigeration | Chiller (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 10:38:20 | 2020-04-20 12:10:00 | Fail | Isolate power,fit new on/off switch to blast chiller, turn power on and tested all running ok at present.
MSA-DCS | WA3184611 | Kitchen drain adjacent to lock up freezer constantly blocking & smelling | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-14 11:10:00 | Pass | Drain machine to clear blockage
MSA-DCS | WA3184620 | unit 2 A11 Lino lifting on floor | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-09-17 14:15:00 | Fail | DAMAGED SECTION REMOVED & REPLACED WITH NEW
MSA-DCS | WA3184662 | unilt 4d TV anntenia faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 11:11:57 | 2020-06-03 12:30:00 | Fail | Re-route all TV cables away from electrical cabling and run higher in roof. Re-crimp ends and test, signal strength is strong.Job completed.
MSA-DCS | WA3184677 | WWTP - E-Stop faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-14 12:30:00 | Pass | Investigate faulty e stop. Source parts and replace. Also replaced faulty indicator lamp.
MSA-DCS | WA3184678 | Gardens, faulty power points | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-14 15:00:00 | Pass | Disconnect and make safe damaged powerpoints.Replace damaged powerpoints on repaired wall.
MSA-DCS | WA3184681 | ABBS - Damaged power leads | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-07 15:00:00 | Pass | Investigate three phase power lead. Source parts and repair
MSA-DCS | WA3184687 | Kitchen, Cool Room 5 - No power | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 11:32:35 | 2020-04-09 15:00:00 | Fail | Cool room tripping faulty solenoid - AAS to replace
MSA-DCS | WA3184691 | Unit 14, A & C , Cell A1 - Bed light had fallen from wall | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 08:30:00 | Pass | Reinstalled damaged light in unit 14 A1
MSA-DCS | WA3184695 | Unit 2, C Wing, Cell C5- Hatch lock not locking, can open & close but not lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-05-21 10:00:00 | Fail | Replaced hatch lock
MSA-DCS | WA3184733 | reporting off brooml-change locking barrell in admin comms room to security key-see notes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-17 10:30:00 | Fail | Replaced lever pack keyed to SEC key.
MSA-DCS | WA3184843 | Unit 5 - Office-air con unt leaking onto orientation officer and computer area | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 13:00:00 | Pass | Cleared drain, tested flow, all ok
MSA-DCS | WA3184845 | Unit 2, Recreation Yard- Blocked drain | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 13:35:34 | 2020-04-08 09:15:00 | Pass | Drain machined blockage ( food clothes rubbish )
MSA-DCS | WA3184848 | Perimeter zone 8 is continuously activating | Wandoo Rehabilitation Facility | SPA-BR | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 07 Apr 2020 | 2020-04-07 17:35:15 | 2020-04-30 09:30:00 | Fail | Calibrate and test Zone 8 outer fence Senstar cable. All in good working order.Job completed.
MSA-DCS | WA3184858 | Vocational Skills - Broken GPO | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-08 13:00:00 | Pass | Replaced damaged gpo in voc skills
MSA-DCS | WA3184882 | Unit 2 - D Wing-Basin tap leaking and basin drain leaking onto floor creating a slip hazard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-09 10:30:00 | Pass | Remove basin, bracket and waste pipe. Remove broken plug and waste and replace with new. Reinstall basin and seal with FC11.
MSA-DCS | WA3184903 | ISU, Cell A02- Power points not working (burning smell) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-08 11:30:00 | Pass | Replaced broken gpos
MSA-DCS | WA3184905 | Murchison, B Wing- Urn constantly trips | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-08 10:30:00 | Pass | Repaired urn
MSA-DCS | WA3184982 | kitchen Big Oven next to salad table bent frame | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 15:35:00 | 2020-04-08 11:05:00 | Pass | Found lower inner baffle bent out of shape. Straighten and adjust baffle panel.
MSA-DCS | WA3185048 | zone 8 cowling | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Apr 2020 | 2020-04-07 22:26:08 | 2020-04-14 11:30:00 | Fail | Attended site and retested zone 8 cowling. All tested and working ok, no false activations occurring. Job complete
MSA-DCS | WA3185051 | the smoke alarm is going off in unit 12 C,D wing Cell 9,10 | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 18:25:56 | 2020-04-07 20:15:00 | Pass | 7/4/20 JN MelaleucaUnit 12 C/D 9+10 in fault. Pipe 2 at 40%, vacuumed pipe 2 to raise airflow level but only raised by 20% as there was no access to cell due to lockdown. Fault clear on FIP all ok.
MSA-DFES | WA3184564 | G Floor, Kitchen- Large Commercial Fridge is leaking from the bottom | DFES Cockburn Emergency Services Complex | GMP-BR | Refrigeration | Refrigerators (RE) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-07 13:00:00 | Pass | Attend site. Access kitchen and check water leak coming from skope 2 door fridge. Isolate and pull fridge out to access rear. Found water leaking of rear. Further investigation found drain to be blocked not allowing the water to the evaporation tray. Clear drain and found leak to stop. Further checks of this unit found the condenser coil to be partially blocked. Clean condenser coil and dust from around components. Dirty coil causes high pressures that can cause compressor valves to burn out. Recommend this fridge have at least 3 monthly maintenance inspection. This will ensure the fridge continues to run for a long time.
MSA-DTAG | WA3184377 | Registry ground-error dynamic battery fail on data gathering panel 1 being reported | Mandurah Courthouse | GMP-BR-HO | Security | Monitoring (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-08 13:45:00 | Pass | 8/4/20 - Dylan Parslow, Joshua ParkReplaced faulty battery in DGP 1 and tested.
MSA-DTAG | WA3184498 | near non-contact interview rooms Bad smell; possibly dead rodent in this area | Rockingham Justice Complex | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-08 09:40:00 | Pass | 2 Odour bags placed in Interview Room
MSA-DTAG | WA3184628 | Magistrates Chambers Shelving wall bracket is loose – Chambers 11.3 | Central Law Courts-Main Building-Level 11 | GMP-BR-HO | Carpentry | Materials (CA) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-08 13:45:00 | Pass | refixed bracket
MSA-DTAG | WA3184672 | Lvl 3 & 5, Staff & Public Toilets-Several soap dispensers have become detached from the wall | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-08 14:30:00 | Pass | refixed soap dispensers
MSA-DTAG | WA3184965 | 1903 CCTV control room Restrict CCTV view to Downstairs CCTV Room and Concierge-see notes | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-08 16:00:00 | Pass | Job completed - Attended site. Restrict CCTV View as they can see Custody Cameras. Logged in as S Foyer Operator with preprogrammedrestrictions to cameras. Configured user as required.
MSA-DTWD | WA3184271 | Tower Block, Level 3- Flickering light to be replaced | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-07 15:16:00 | Pass | Attended site and signed in. Located level 3 tower. Found light to have cover and tubes taken out. Replaced tubes and starters as required. Tested all okay. Job complete
MSA-DTWD | WA3184488 | A Block, Room A217- Sink tap in kitchen sprays over bench | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-08 11:00:00 | Pass | Complete
MSA-DTWD | WA3184616 | T, U & V block workshops- Fluros not working | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-05-14 15:30:00 | Fail | Attended site and signed in. Located scissor lift and lights out, replaced all tubes out, found many fittings still not working and found burnt out and broken fuse holder internal of fitting. Repaired all fittings, replaced ballasts as required. All lights okay and working. Job complete
MSA-DTWD | WA3184707 | A Block, A156a Stairwell exit door- External door will not lock | Leederville Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-08 10:55:00 | Pass | Repair lock & fit T strike to make lock latch correctly
MSA-DTWD | WA3184728 | B Block, Level 1- Room B019- Air Con is very noisy | Munster Campus (ACEPT) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-07-07 16:00:00 | Fail | Attended site. Removed the ceiling tiles found the evap blower assembly needs replacing , parts on order.
MSA-DTWD | WA3184865 | fire pump investigate issue with JACKING Pump | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-07 15:47:00 | Pass | Call Out, found that the pump was running isolated pumps, invetergate all hydernts & hose reels around campus found no caurse for the pumps to start, found that the jacking pump was not working,found the cause the jacking pump had been isolated ? reset jacking pump, stated pumps check all pressure gauges, pumps are now back on line.start time: 13.30finish time: 15.47
MSA-DTWD | WA3184968 | Various Locations - Repair breaks in paving around campus | Joondalup Kendrew Campus | GMP-BR | Paving & Roadworks | Paving (PR) | M Construction (WA) | 2 | CLOSE | 07 Apr 2020 | 2020-04-14 17:00:00 | 2020-06-22 10:36:00 | Fail | Job complete
MSA-DTWD | WA3184974 | B Block, Garden outside entry at ground level - Remove dead palm tree limbs | Bentley Campus | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 1 | CLOSE | 07 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-14 14:45:00 | Fail | Works compelted.
MSA-MRWA | WA3184327 | G, G19 – Light flickering please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 07 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-07 10:00:00 | Pass | Replaced tube with new
MSA-DCA | WA3185384 | Ground floor window has been broken. | Art Gallery of WA - James St - Administration Block (Block A) | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-14 14:59:00 | Fail | ATTENDED SITEMADE SAFE BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS 1-640 X 470PLUS SAFETY FILM 1-1120 X 500 AND SILICONERETURNED LATER DATE TO REGLAZE5.38 CLEAR LAMINATED SAFETY GLASS1-1166 X 810PLUS SILICONE AND PUTTY USED
MSA-DCS | WA3185138 | Gate house control room - 2 camera on displays not showing | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 07:08:44 | 2020-04-08 10:57:00 | Pass | Kntrol room reported 2x cameras are failing to display, cameras are displaying correctly and have recently been changed for new, old cameras must be kept in list for a extended period of time for recording purposes. Cameras currently are highlighted in list as removed and have been sent to the bottom of list to prevent confusion, the discriptor has now been changed to say 'removed do not report'. Cameras functioning correctly.
MSA-DCS | WA3185162 | Education, room 4 - aircon leaking/ spraying water | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 08 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-15 10:30:00 | Pass | Replaced solenoid and tested operation. All ok.
MSA-DCS | WA3185280 | SHU, East wing, B3 - Obs light of cell is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 13:30:00 | Pass | Repaired faulty lights in SHU east wing
MSA-DCS | WA3185285 | Unit 4 - east - water leaking from Aircon. amount of water is more then condensation | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 09:30:00 | Pass | Cleared drain and tested flow. All ok
MSA-DCS | WA3185300 | Generator - AC power lost to generator (fault 26) battery voltage out of limits | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-08 10:15:00 | Pass | Reset battery out ot of range alarm and checked batteries charged and charger operating.This fault occurs whenever there is a mains power supply interuption to the control panel/genetator ie. A power failure .
MSA-DCS | WA3185422 | medical centre air con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 09:32:14 | 2020-04-08 15:45:00 | Pass | Repairs are already commenced under other job number
MSA-DCS | WA3185426 | Assessments, female toilet - lighting not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-09 09:30:00 | Pass | Tested light in female toilet in assessment working on arrivale
MSA-DCS | WA3185427 | CCU entry door Not closing and locking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 09:38:00 | 2020-04-08 12:15:00 | Pass | completed, not a locking issue
MSA-DCS | WA3185450 | Unit 10, A9 - Medical Hatch Lock Wont Open | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 09:44:48 | 2020-07-01 16:00:00 | Fail | job completed - 08/04/2020 - temporary repairs made to secure hatch. Needs replacement.On site 01/07/2020 - supplied and installed replacement hatch
MSA-DCS | WA3185457 | Poultry Shed- No power to lights in the shed | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-08 15:00:00 | Pass | Investigate tripping lights in poultry shed. Traced fault to faulty light. Repaired light.
MSA-DCS | WA3185460 | Unit 7, H20 - toilet not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 09:54:54 | 2020-04-09 10:30:00 | Fail | Repaired but don’t know how long it will last was going to get new cistern but couldn’t get escort to return and fix so will be completed on the 9/04/20
MSA-DCS | WA3185467 | Unit 10, C & D wing - Hot water urn over flowing, electrical fault | Hakea Prison | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 11:30:00 | Pass | Repaired urn
MSA-DCS | WA3185468 | Reception- lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 12:00:00 | Pass | Repaired reception lights
MSA-DCS | WA3185470 | Unit 6, A winf, day room - light has water in it | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 10:02:05 | 2020-04-09 08:30:00 | Pass | Disconnected and dried light Reconnected and tested once dry
MSA-DCS | WA3185474 | unit 9, B9 - broken cell door hinge | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 10:05:09 | 2020-04-09 08:30:00 | Pass | replaced hinge
MSA-DCS | WA3185476 | Karakin, Cell A08- Toilet not flushing | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-14 10:17:00 | Pass | Replaced faulty solenoid valve
MSA-DCS | WA3185479 | Unit 7, F wing, cleaning cupboard - sink coming off the wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 10:08:37 | 2020-04-08 16:00:00 | Pass | Reattached trough to wall
MSA-DCS | WA3185500 | CCU, all - Crackling sound from light switch panel. | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 10:27:06 | 2020-04-08 14:00:00 | Pass | Replaced faulty switch mechs
MSA-DCS | WA3185535 | Unit 4, C wing Showers - drains blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 10:45:21 | 2020-04-09 08:12:00 | Pass | Unblocked drain
MSA-DCS | WA3185540 | Unit 2, A11 - Cell has no water, broken tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 10:48:29 | 2020-04-09 09:18:00 | Pass | Replaced water supply / installed new pillar tap
MSA-DCS | WA3185542 | Unit 5, C13 - cell back window broken | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 10:50:24 | 2020-04-15 11:30:00 | Fail | regazed the broken window
MSA-DCS | WA3185544 | Unit 1 - B & D regi oven door is damaged/replace | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 10:51:37 | 2020-06-04 09:54:00 | Fail | Oven door has broken inner & outer glass. Repaired door at workshop after finally receiving the back ordered parts. Return Door & Hinges back to stores on 4/06/20
MSA-DCS | WA3185557 | Metal work shop, office - electrical control panel in office has faulty switch | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 10:30:00 | Pass | Replace faulty switch mechs in Metal workshop
MSA-DCS | WA3185560 | Unit 1, B15 - brken GPO | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 11:00:05 | 2020-04-08 15:00:00 | Pass | Replaced damaged gpo
MSA-DCS | WA3185593 | Unit 1, Cell A7- Toilet is not flushing | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 11:45:00 | Pass | Fitted new outlet washer and fitted new inlet valve
MSA-DCS | WA3185669 | Unit 13 - A & C-spout in the sink is leaking causing water to pool on the floor. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-09 08:00:00 | Pass | Investigate unit for leaking spout as no location was supplied. Kitchen and both A/C laundries are fine. No-fault-found.
MSA-DCS | WA3185694 | Gate house, blocked drain in the crit | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 12:25:05 | 2020-04-09 09:30:00 | Pass | Plunge both basins and floor waste. Moflo floor waste, rinse and test.
MSA-DCS | WA3185717 | Abattoir 12 leaking water and steriliser valves boning room and slaughter floor - see notes | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Apr 2020 | 2020-04-17 17:00:00 | 2020-05-06 15:15:00 | Fail | COMPLETED
MSA-DCS | WA3185729 | Unit 4, A2/A2 - Buddy door damaged | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 12:50:12 | 2020-06-16 09:30:00 | Fail | NEW DOOR HUNG & PAINTED
MSA-DCS | WA3185778 | Unit 1, D10 - camera lens damaged | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 13:28:02 | 2020-04-08 16:00:00 | Pass | Lens scratched by prisoner. Removed and replaced with site spare. Image clear at U1 control.
MSA-DCS | WA3185792 | L1 Room 1.B faulty light above workstation desk1.10 | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 13:36:55 | 2020-04-08 16:00:00 | Pass | Repaired lighting at W1.10
MSA-DCS | WA3185826 | BR unit 1 all camera's have gone down | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Apr 2020 | 2020-04-08 18:06:05 | 2020-04-08 17:34:00 | Pass | Sourced parts, attended site, traced problem to faulty PSU. Replaced PSU and tested OK.Job CompleteParts:1 x 24VDC PSU (SEME Stock)
MSA-DCS | WA3185853 | Laundry- Commercial dryer is not working- error "sale switch fault" | Karnet Prison Farm | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 14:44:33 | 2020-05-06 11:52:00 | Fail | New sail switch clip required, new contactor and aux contact for contactor, clean burner tubes on dryers
MSA-DCS | WA3185857 | Unit 1, Cell A07 - toiliet blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 12:48:00 | Pass | Unblocked toilet shower basin removing hair food
MSA-DCS | WA3185859 | Unit 1, Cell A16 - Sink and shower blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 14:03:00 | Pass | Unblocked sink and shower food and hair
MSA-DCS | WA3185864 | Front gate, main prison -front and inner sally port gate, won’t open and close properly | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | AFD Contracting | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 14:55:31 | 2020-04-09 12:15:00 | Pass | 09/04/20Hired scissor lift.Install new limits on outer doors drive bolts (locking pins) actuator.
MSA-DCS | WA3185873 | Boiler house office door lock damaged x2 | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-30 13:00:00 | Fail | supply and install lock. Require door closer as old closer unserviceable. Return supply and install door closer and blocker plate.
MSA-DCS | WA3185908 | Female & Disabled Toilets- water leaks as per below | Walcott Centre (Central West Metro ) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 10:01:00 | Pass | COMPLETED
MSA-DCS | WA3185910 | Unit 4 - main vehicle & pedestrian access gates wont open | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 15:53:29 | 2020-04-10 10:08:00 | Fail | Test Mains power to gate and no power observed. Identify unlabelled circuit on essentials chassis 1 and reset.
MSA-DCS | WA3185943 | L9 kitchen TP 9.2 light is flashing on zip filter change | Westralia Square | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-14 11:45:00 | Pass | Filter replacement only. Reset counters. Asset capture
MSA-DCS | WA3302393 | RETROSPECTIVE Workorder Donot attend-No recording on CCTV system | Walcott Centre (Central West Metro ) | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 08 Apr 2020 | 2020-04-16 17:00:00 | 2020-07-09 16:00:00 | Fail | Found no UPS on network and security equipment.
MSA-DFES | WA3186247 | Retrospective WO - VOLUNTEER FIRE SERVICES ROLLER DOOR OPEN, FIREFIGHTERS RETURNED AS I ARRIVED | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 22:29:00 | Pass | VOLUNTEER FIRE SERVICES ROLLER DOOR OPEN, FIREFIGHTERS RETURNED AS I ARRIVED. DOOR SECURED AND PANEL SHOULD HAVE BEEN ROLLED BY CAREER FIREFIGHTER RICHARD PEARCY, #30494. OPS NOTIFIED AND MONITORING CONTACTED. BEN AT MONITORING NOTIFIED. CLEARED FROM SITE.
MSA-DTAG | WA3185632 | Ground level, female public toilets - the first toilet has a crack in the bowl | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Apr 2020 | 2020-04-17 17:00:00 | 2020-06-18 11:31:00 | Fail | Completed Used toilet seat and fixing kit from van stock: $84.50
MSA-DTAG | WA3185635 | Levell 5, court 53 - No power to JSO bench in Court 53 | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-09 11:03:00 | Pass | Job complete
MSA-DTAG | WA3185642 | Level 8, Court 82 - Door closer arms have separated | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 13:15:00 | Pass | replaced door closer arm
MSA-DTAG | WA3185683 | L6 security monitoring PCs in the staff area have logged-see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 14:00:00 | Pass | Job completed - Attended site. Level 6 Monitoring PC's in Staff Area has logged out. PC's have lost connection to Milestone Server.Time Sync issue, manually adjusted time rectified problem.
MSA-DTAG | WA3185896 | Governers lane & Terrance Rd- Gas Leak | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 08 Apr 2020 | 2020-04-08 19:43:00 | 2020-04-08 17:50:00 | Pass | Unable to see any damage around the gas meter. No evident leaks around it either. Unable to gather more info. Walked around the building and couldn’t see any gas pipe damaged. Gas Valves at the gas meter on on ny arrival on site.
MSA-DTWD | WA3185272 | A block, ground level, zone 17 - repair fault to A block zone 17 | Joondalup Kendrew Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 08 Apr 2020 | 2020-04-08 17:00:00 | 2020-04-08 10:20:00 | Pass | Attended site due to FIP showing issuesReplaced 2 x detectors due to these being 1991 and causing the issue Needed to be replaced with newReset panelAll good on leaving site
MSA-DTWD | WA3185286 | G Block Room G25 window has been smashed | Rockingham Campus | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 17:05:00 | Pass | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-778 X 1104PLUS SILICONE
MSA-DTWD | WA3185526 | 19Ab Exposed earth wire in the wall of B153 | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 08 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-17 09:14:00 | Pass | Removed cable as no longer required
MSA-DTWD | WA3185564 | C block Evaporative air con not working in Cafeteria | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 08 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-09 15:30:00 | Pass | Repair completed 10:30am to 3:30 pmBy Trent JacksonAwaiting returnof signature slip via email due to covid 19
MSA-DTWD | WA3185611 | T, U, & V blks retic pipe broken near pump station near G block | Rockingham Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 14:45:00 | Pass | Locate broken PVC pipe under a small tree, redirect pipe around tree
MSA-DTWD | WA3185613 | C block, rooms CG51,16 & 17 - need to have locks re-keyed | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 10:15:00 | Pass | Rekey Rooms CG51,16 & 17 C Block
MSA-DTWD | WA3185698 | Block 6, Metal Fab 2- Water leak in oxy welding bay above LED light | Thornlie Campus | GMP-BR | Roofing | Tiled Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-16 16:00:00 | Fail | Repairs have been completed will need to wait for rain to confirm if works have been successful in resolving the leak
MSA-DTWD | WA3185836 | Level 1, Main room - Failure in the local controller for the AC Systems | Perth Campus B3 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 08 Apr 2020 | 2020-04-17 17:00:00 | 2020-05-19 11:25:00 | Fail | SIGN IN COMPLETE TAKE5 ASSISTED CHRIS V WITH ROOF ACCESSAND INTIAL FAULT DIAGNOSIS. INCORRECT SIZED TRANSFORMERAND FAULTY CABLING AND TEMERMATIONS. RECITIFED BY CHRIS V. FURTHER FAULT FINDING REQUIRED. TESTED MOMENTARY ENABLE SWITCH-OK. CHECKED RESISTORS HAS CONTROLLER ENABLES ARE DRY CONTACTS OK OPEN AC 1 INPUT ON CONTROLLER AND AC 1STARTED. OPEN AC2 INPUT AND UNIT WOULD NOT START. AC2 ENABLE INPUT FAULTLY. BRAF WILL BE SUBMITTED TO RE PROGRAM ONE OF THE SPARE INPUTS TO BE THE AC 2 ENABLE
MSA-MRWA | WA3185309 | Level 1, west end - flickering light | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 09:00:00 | Pass | Replaced tube with new
MSA-MRWA | WA3185317 | Level 5, west end - flickering light in passage way | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 09:36:00 | Pass | Replaced tube with new
MSA-MRWA | WA3185323 | Level 4, room 4.68 - unmount PC monitors and place them onto stands at desk | Don Aitken Centre MRWA Head Office | GMP-BR | Furniture | Office Furniture (FU) | MR - Handyperson - PFM | 1 | COMP | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 11:33:00 | Pass | Attended twice arms didn’t fit the screens and was told to leave it for the occupants
MSA-MRWA | WA3185482 | L3 kitchenette L3 – hot water urn constantly dripping please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 08 Apr 2020 | 2020-04-09 17:00:00 | 2020-04-08 16:44:00 | Pass | Replaced faulty tap. All ok
MSA-DCS | WA3186162 | Vegetable Preparation, Workshop, Potato Rumbler - the on & off switch needs repairing | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-14 13:00:00 | Pass | Reinstalled damaged isolator on a potato rumbler, returned and disconnected for maintenance
MSA-DCS | WA3186165 | Unit 1, B & D, Day room - large bubbles in the floor. They are a big trip hazard | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-09-08 13:30:00 | Fail | DAMAGED FLOORING REPLACED
MSA-DCS | WA3186168 | Unit 3, Control room - aircon appears to be full of dust which is effecting staff health | Casuarina Prison | WSM-BR-SITE | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-14 13:45:00 | Pass | Unit has been sufficiently cleaned using pressure sprayer and all dust has been removed
MSA-DCS | WA3186181 | Gate house, PMD2 metal detector - Activating all the time, even when no traffic | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 08:11:32 | 2020-04-21 12:58:00 | Fail | Investigated fault, built and installed replacement control panel to allow staff to reset and and control pat down/search alarm buzzer/alarm.Tested OKJob Complete Parts Used:Consumables
MSA-DCS | WA3186186 | West Chaplains Office - RCD faulty, will not reset | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 08:19:29 | 2020-04-09 12:00:00 | Pass | Tested and reset RCD , located faulty appliance
MSA-DCS | WA3186190 | Kitchen, Coolroom No 5 - tripped out. Overtemp showing on nLCD | Hakea Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 08:24:07 | 2020-04-09 14:46:00 | Pass | Replaced lsv no more earth leaks detected by sparky
MSA-DCS | WA3186203 | Camera 24 is not operational | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Apr 2020 | 2020-04-09 16:33:19 | 2020-04-09 14:09:00 | Pass | Checked indigo system and confirmed encoder card is operational. Attended EC9 found fuse had blown, Replaced and tested PTZ function All working
MSA-DCS | WA3186204 | Unit 2, Cell A10, blocked sink | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 09 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 15:10:00 | Pass | Unblocked sink and shower food and hair
MSA-DCS | WA3186206 | Pedestrian gate intercom has failed | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Apr 2020 | 2020-04-09 16:35:49 | 2020-04-09 14:11:00 | Pass | Replaced Aiphone intercom unit from site stockIntcom button had broken
MSA-DCS | WA3186249 | Unit 1, Control Kitchen- Zip hot water system faulty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 08:59:00 | Pass | Working fine no fault found - ADVISED SITE THAT ACTUAL HOT WATER SYSTEM MAINS SUPPLY WAS ISSUE - PLUMBING NOT WATER FILTER
MSA-DCS | WA3186272 | Control - Fire Panel is showing faults | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 09 Apr 2020 | 2020-04-09 13:43:44 | 2020-04-09 12:36:00 | Pass | Attended site for fault on fire panel. When arrived found unit 12 vesda c/d 9/10 in airflow fault. Cleaned sampling point and vacuumed out pipe work all back to normal working condition when left
MSA-DCS | WA3186274 | unit 2 cell A9 officers key has snapped off in lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 09 Apr 2020 | 2020-04-09 13:48:57 | 2020-04-09 11:30:00 | Pass | removed broken key from lock
MSA-DCS | WA3186300 | Industries Administration - Office-repair and test panic duress button in employment officers office | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-15 14:00:00 | Pass | Installed flush box and reinstated duress button testedbfully operational, metal shop is taking care of ground cable cover.
MSA-DCS | WA3186306 | Kitchen - faulty dishwasher injectors | Karnet Prison Farm | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 10:00:00 | Pass | Kitchen Dishwasher faulty. Check machine & controls. Repairs needed to soap injector. Service is provided by soap agent. Report to kitchen staff & maintenance.
MSA-DCS | WA3186310 | Lenard A wing-Pantry door is split and needs replacment | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-06-26 14:15:00 | Fail | Door replaced
MSA-DCS | WA3186322 | Unit 3, D wing - sinks in showers wwaste pipes coming away form wall | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-05-07 15:00:00 | Fail | Repair Basin waste pipes in the shower blocks.
MSA-DCS | WA3186377 | Make good damaged shelving to PFM store | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-14 13:00:00 | Pass | shelving repaired
MSA-DCS | WA3186386 | education zip water urn not working-Eco boil Z019031806006 | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 11:14:01 | 2020-04-14 10:29:00 | Fail | Thermal overload reset and tested A40191224C Econoboil Zip system had tripped thermal overload - unfilled/filled, tested ok reset - attended as failed after leaving and opened up unit - completely scaled up inside replaced element and installed new capex asset maxiflow filter scale system which will assist in reducing scale (if serviced routinely) and assist in extending life of asset.
MSA-DCS | WA3186413 | Unit 6, D8 - the main lock on cell is hard to turn with keys, seems partially seized | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-15 12:00:00 | Pass | replaced hinges and lock, remove edge capping, remove main lock, service and reinstall.
MSA-DCS | WA3186420 | Medical centre - Blocked toilet | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 11:33:02 | 2020-04-09 15:15:00 | Pass | Cleared blockage to wc. Adjusted flushing mechanism. Tested operation.
MSA-DCS | WA3186438 | Unit 14 - D Wing partial drain blockage in cell D1. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-16 08:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3186545 | unit 7, H4 - GPO falty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 12:49:28 | 2020-04-09 15:00:00 | Pass | Replaced damaged gpo
MSA-DCS | WA3186554 | Main Admin, Fire panel - Sprinkler valve,plumbing issue | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 12:54:18 | 2020-04-09 15:20:00 | Pass | Issue not plumbing related. Industry manager advised
MSA-DCS | WA3186589 | Viists tamper for MDAS | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-09 14:24:00 | Pass | Made enclosure damaged,Removed enclosure and replaced with site stock .Tested mdas alarms and confirmed tamper has cleared
MSA-DCS | WA3186623 | Farm water leak near jump sheds | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 13:46:57 | 2020-04-17 13:00:00 | Fail | COMPLETED
MSA-DCS | WA3186642 | Unit 5 cell 14 cell call not audible lights come on but cannot hear | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 13:58:31 | 2020-05-01 07:33:00 | Fail | 30/4 Removed call point re terminated cables. Cleaned up and re installedTested and confirmed ok
MSA-DCS | WA3186670 | Admin - faulty lights | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-14 10:00:00 | Pass | Investigate and repair faulty lights in admin
MSA-DCS | WA3186672 | Program room 8 - broken switch and plate | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-14 11:30:00 | Pass | Investigate and replace broken switch and switch plate in program room 8
MSA-DCS | WA3186675 | Unit 4, day room - faulty mixer tap at sink | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-22 11:00:00 | Fail | COMPLETED
MSA-DCS | WA3186681 | unit 1 over head wires hanging to low | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-09 16:30:00 | Pass | Investigate power lines with western power on site. No issues found
MSA-DCS | WA3186764 | unit 8 CD regi oven keeps tripping out | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 09 Apr 2020 | 2020-04-10 16:43:17 | 2020-04-11 14:00:00 | Fail | Reset oven
MSA-DCS | WA3186778 | Pat alarms -Communication failure ,Network fail and dail box as well | Banksia Hill Detention Centre-Block K Stores | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-10 10:45:00 | Pass | Collected parts and attended site for afterhours callout. Found MDAS transponder in Karakin block had been turned off at GPO. Re powered GPO and tested and all back online and working ok. Replaced 1x 7ah battery. Job complete
MSA-DFES | WA3186218 | Bathroom & Kitchen has ant infestation | CFRS Joondalup | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 09 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 10:00:00 | Pass | Carried out a service for ants to Joondalup fire station. Ants were nesting within the wall cavities and tracking out into the kitchen and bathroom via cracks to the tiles. Used seclira internally as well as spraying external walls and entry ways using firponil. After 2 weeks it is essential that all these tiles get re caulked in order to eliminate entry ways for ants in future.
MSA-DFES | WA3186473 | Security alarm activating on front bay when staff off station | CFRS Midland | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 09 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-09 15:00:00 | Pass | 09/04/2020, 1445-1500Increased shunt time on zones 20 and 21, to 135. Also increased entry time to 70seconds. May have to look atrelocating pirs on bays as chains could be setting them off, or replacing with DT
MSA-DTAG | WA3186097 | Level 1, DPP Kitchen & First office on left when you walk in - Power points not working | Perth Children's Court | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 09 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-14 12:00:00 | Pass | Job complete
MSA-DTAG | WA3186278 | 1903, Mitchell JA chambers - The plastic holder for the air conditioning remote control has detached | Supreme Court | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-14 15:00:00 | Pass | REMOTE HOLDER RESECURED
MSA-DTAG | WA3186284 | Ground, custody - Internal custody bail door is sticking and sometimes not engaging | Midland Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-14 10:30:00 | Pass | 14/4/20 - Dylan Parslow, Joshua ParkMomentry switch faulty.Repaired spring in switch and tested, working correctly.If switch fails again in the future, recommend replacement.
MSA-DTAG | WA3186346 | Door three - door arm needs repairing | Rockingham Justice Complex | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-15 08:45:00 | Pass | DOOR CLOSER SLIDE ARM REPLACED
MSA-DTAG | WA3186363 | The J in the Justice is coming loose off the building | Rockingham Justice Complex | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-07-03 11:30:00 | Fail | DAMAGED LETTERS - J, A, M, M, X REMOVED, REPAIRED & RE FIXED
MSA-DTAG | WA3186480 | custody CCTV cameras not recording-Sapio on site | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 09 Apr 2020 | 2020-04-14 17:00:00 | 2020-05-29 15:00:00 | Fail | Job completed - Collect NVR from supplier and attend site. Installback into rack. Re-connect and re-install applicable database path rules. Bring online and begin recording tasks. Test andrecommission. De-commission loan unit and return to Indigo
MSA-DTAG | WA3186707 | Level 3, Public toilet - Male cubicle toilet is blocked, toilet adjacent to Courts 10 & 11 | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-14 07:53:00 | Pass | Unblocked rhs cubical in male’s toilet (court 10/11)
MSA-DTAG | WA3186723 | custody Please re-attach smoke detector in custodial search room-see notes | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 08:00:00 | Pass | Reinstalled smoke detector in strip search room and detector working all fine and ok now.
MSA-DTWD | WA3186121 | Brick bay landscape, C17 - External taps x2 and water pressure faulty | Murdoch Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 09 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-09 16:44:00 | Pass | Replace taps
MSA-DTWD | WA3186143 | North, D block, ground level - smashed entry door(fully glazed) & 2x Smashed black stairwell windows | Joondalup Kendrew Campus | GMP-BR-RC | Building | Doors (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 09 Apr 2020 | 2020-04-09 17:00:00 | 2020-06-03 14:10:00 | Fail | ATTENDED SITE, TEMP GLAZED 2X SPANDREL PANELS AND SECURE BROKEN GLASS TO DOOR WITH SECURITY FILM AND MEASURED FOR REPLACEMENTS RETURNED TO SITE AT LATER DATE AND REGLAZE 3X PANELS 6MM CLEAR TOUGHENED PAINTED 1 – 826 X 8031 – 826 X 780 6.38 CLEAR LAMINATED SAFETY GLASS 1 – 1318 X 701 – POLISHED ALL TINTING SUPPLIED AND FITTED TO MATCH 1 – 1318 X 701
MSA-DTWD | WA3186200 | External Brick saw compund, C17 - two cracked power points & relocate to a higher location | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 09 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 09:00:00 | Pass | Attended site and signed in. Located bricklayers cutting shed. Found low gpos in wet zone. Removed and relocated to mark positions by site. Ran conduit on outside of wall and installed gpos. Tested all okay. Job complete
MSA-DTWD | WA3186299 | Building 10, level 1, 10F94 - Faulty door closer and hinges. | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 11:30:00 | Pass | Door hinges adjusted and new door closer installed
MSA-DTWD | WA3186333 | Level 5, roof plant - Chiller 2 - Circuit B - Oil Pressure fault | Perth Campus B2 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 14:00:00 | Pass | Attended site and rechecked equipment for further faults. All ok no further issue with chiller has occurred.
MSA-DTWD | WA3186383 | T block, room T026 - glass sliding door is faulty | Murdoch Campus | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-09 13:45:00 | Pass | On inspection, found ext opti combi sensor is faulty as it is self actuating.Replaced faulty sensor, tested and adjusted, all ok.
MSA-DTWD | WA3186416 | M block M002.9 leaking toilet in the Staff Mens Toilet | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-15 09:15:00 | Pass | Repaired leaking cistern
MSA-DTWD | WA3186555 | block 10 ground 10G3 office Broken light fitting | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-28 13:19:00 | Fail | Attended site and signed in. Removed old light fitting from office. Installed 2 x new battens. Tested all okay. Job complete
MSA-DTWD | WA3186608 | E block exterior Trip hazards on the concrete footpath at the front of E Block | Bentley Campus | GMP-BR | Paving & Roadworks | Concreting (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-05-19 15:30:00 | Fail | Works are now completed - Please see photos attached
MSA-DTWD | WA3186609 | B block Room B2220 – Carpet near entry is damaged – Trip hazard | Bentley Campus | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-28 10:15:00 | Fail | Carried out repairs to the carpet as requested by site
MSA-DTWD | WA3186614 | E block E37 Walk in Freezer - Isolator switch on roof unit is faulty -see notes | Bentley Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 09 Apr 2020 | 2020-04-16 17:00:00 | 2020-05-07 10:30:00 | Fail | Job completedAwaiting return of signature slip via email due to covid 19
MSA-DTWD | WA3235374 | Building 8, level 1, Door to block 10 - Door hinges loose on door frame.Stripped threads | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 09 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 16:00:00 | Pass | Removed door from and drilled out and rethreaded hinge mounts, resecured frame and rehung door. Adjusted door striker
MSA-DTWD | WA3509133 | Retrospective work order - Level 2 - Lost communication to access system | Perth Campus B4 | GMP-BR | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 0 | CLOSE | 09 Apr 2020 | 2020-04-09 21:47:00 | 2020-04-15 14:38:00 | Fail | INVESTIGATED FAULT ON PC COMMS RELATING TO BUILDING A.CHECKED CONTROLLER END AT REMOTE BUILDING. FOUND ZENTA TO HAVE NOACCESS TO NET ROUTER.TRACED CABLE GOING FROM ZENTA CONTROLER TO NET ROUTER IN LOCAL COMMSROOM. FOUND CABLE DISCONNECTED BY IT. INFORMED DAVE GAFF.RECONNECTED CABLE CONFIRMED NETWORK ESTABLISHED BETWEEN INET PC ANDREMOTE BUILDING A.INFORMED SITE CONTACTED ON DEPARTURE
MSA-MRWA | WA3186256 | ground courtyard Reticulation pipe split and leaking please remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 1 | CLOSE | 09 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-15 18:15:00 | Fail | Dom ,repair split irrigation pipe 9/4 5.30 till 6 call out plus half hour labour plus parts $22Dom replace bypass leaking battery operated controller.15/4 Dom 5.30 till 6.15 call out + 45 minutes Supply irrigation controller + battery + fittings $105
MSA-DCS | WA3186791 | Unit 2 Female Yard, Cell 4-10 and 4-11 and ops room - Main Cameras not working | Roebourne Regional Prison | GMP-BR- HO | Building | General Building (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Apr 2020 | 2020-04-11 01:48:59 | 2020-04-10 12:00:00 | Pass | Contacted site and advised power had gone out. Re called site in the morning and site had advised that all cameras are back online and operational. Reccomend installing UPS system to unit offices CCTV equipment
MSA-DFES | WA3186807 | Perth FS - Sliding front glass door stayed open and not closing properly. | CFRS Perth | GMP-BR | Electrical | Materials (EL) | AWB Co. | 1 | CLOSE | 10 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-10 10:00:00 | Pass | Dorma required to replace sensor
MSA-DCS | WA3190835 | Front door Biomatrix is not working and lost communication with control room | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Apr 2020 | 2020-04-12 07:21:35 | 2020-04-11 15:45:00 | Pass | Afterhours callout. Attended site and found turnstyle not communicating. Reset relays and network switch . Tested voltage on relays and switch . All voltage tested ok, tested turnstyle functions from control room. All tested and working ok. Job complete
MSA-DCS | WA3190844 | Unit 1-C16-Blocked Toilet | Hakea Prison-Unit 1 | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 11 Apr 2020 | 2020-04-11 12:50:27 | 2020-04-11 17:40:00 | Fail | Replaced faulty cistern. Unblocked toilet. Unable to get escort-job delayed.
MSA-DCS | WA3190855 | SITE COSTED Broken viewing glass broken Unit 9-cell C10 | Hakea Prison | WSM-BR-SITE | Carpentry | Materials (CA) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 11 Apr 2020 | 2020-04-11 13:41:44 | 2020-04-11 13:00:00 | Pass | Replaced glass
MSA-DCS | WA3190866 | Casuarina Prison- fault in the personal duress system in the | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-14 15:30:00 | Pass | Investigated 8 faults showing on the MDAS computer in Gate Control. All faults listed are related to Building construction / demolition or earth works on site. Referred to Seme Management for escalation to PFM
MSA-DCS | WA3190889 | Hakea Prison-unit 4 power keeps tripping | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 11 Apr 2020 | 2020-04-11 16:49:32 | 2020-04-11 17:00:00 | Fail | Repaired gpo and reset power
MSA-DCS | WA3190896 | unit 8 - ovan not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 11 Apr 2020 | 2020-04-12 15:40:52 | 2020-04-30 13:00:00 | Fail | repaired oven
MSA-DCS | WA3196276 | Hakea-Melaleuca Prison - Lock issues | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 1 | CLOSE | 12 Apr 2020 | 2020-04-13 08:04:21 | 2020-04-14 15:15:00 | Fail | replaced hinges.
MSA-DCS | WA3196282 | Unit 1 - B wing - Blocked drains in the sinks SITE COSTED | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 12 Apr 2020 | 2020-04-12 13:38:28 | 2020-04-12 13:37:00 | Pass | Unblcoked rhs of B wing in u1-drains full of bed sheets
MSA-DCS | WA3196296 | Unit 7, Cell H-9, intercom in cell not working SITE COSTED | Hakea Prison | WSM-BR-SITE | ICT/Audiovisual | Hardware / Equipment (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Apr 2020 | 2020-04-12 17:17:26 | 2020-04-12 17:00:00 | Pass | Cell xall unit 7 found full of toothpaste, cleaned cell call point, cell call point is now audible.
MSA-DCS | WA3196302 | Hakea-Melaleuca Prison-Unit 2- cell door B14- door jammed | Melaleuca Prison | GMP-BR- HO | Carpentry | Materials (CA) | AAA Ability Locksmiths | 1 | CLOSE | 12 Apr 2020 | 2020-04-13 14:23:14 | 2020-04-14 14:15:00 | Fail | replaced faulty personal lock.
MSA-DCS | WA3196305 | Unit 5 Cell D3 the toilet flushing is not working SITE COSTED | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 12 Apr 2020 | 2020-04-12 19:26:33 | 2020-04-12 18:15:00 | Pass | Temporary repair was made and the maintenance manager is happy with the repair made and does not wish that we change the cistern at this time.
MSA-DCS | WA3204186 | Controller 3-is faulty and its not receiving any communication | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 14:29:00 | Pass | Replaced network switch and 48v power supply along with patch leads and tested operational, mounted supply and switch along with cabling. All ok.
MSA-DFES | WA3196306 | Warning strobe lights not working, door number 3 | CFRS Rockingham- TO BE DECOMMISSIONED Rockingham FS-Main Building | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 0 | CLOSE | 12 Apr 2020 | 2020-04-12 19:35:47 | 2020-04-12 19:31:00 | Pass | Warning Strobe would flash red / green rather than stay red until the door went up and then go green, tested voltage to relays and all was OK, Garage door contractor needed to be engaged to install new latching relay and set paramters on lighting control
MSA-MRWA | WA3196310 | Materials Engineering Branch - Alarm sensor tripped in the Admin area. | Materials Engineering Branch | GMP-BR | Security | Guards (SE) | MCS Security Group | 0 | CLOSE | 12 Apr 2020 | 2020-04-12 22:17:59 | 2020-04-23 13:25:00 | Fail | Docket sent 23.04.20
MSA-DCS | WA3201531 | Couple faults cell call on the cell call screen. faults won't clear. Not been resetting | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Apr 2020 | 2020-04-14 07:58:32 | 2020-04-13 10:15:00 | Pass | Attended site.Found on Cell Call monitor two active calls from unit 1.Reseted power on AUSTCO ACS-100-R unit and checked the monitor.Calls were cleared.Tested.All ok at departure
MSA-DCS | WA3201557 | sink and drain blocked | Melaleuca Prison | GMP-RM | Building | Materials (BU) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 13 Apr 2020 | 2020-04-14 11:22:54 | 2020-04-13 15:30:00 | Pass | Food grime and hair blocked basin and shower
MSA-DCS | WA3201580 | Fault- Fire Alarm to be reset-Karnet Prison Farm-Kinsbury Drive | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 13 Apr 2020 | 2020-04-13 18:13:28 | 2020-04-13 15:58:00 | Pass | AH callout for FIP in fault - see FSR
MSA-DCS | WA3201583 | fire alarm, constantly alarming | Hakea Prison-Main Gatehouse | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 13 Apr 2020 | 2020-04-13 20:23:28 | 2020-04-16 13:22:00 | Fail | Attended Hakea prison for fault keep alarming. When arrived fault stopped due to latching on to panel it is a earth fault loop 1 gatehouse detectors causing the problem checked lower heads around the area and no sign of water damage. Will need to return with second tech to trace out more some areas super high will need extension pole with grabber to take of heads. Also need 10’s or 12’s for some areas.Revisit with 2 technicians booked, next available escort 16.04.2020 070016/04/20 JN MSInvestigated earth fault split circuit multiple times until fault could be narrowed down to a few detectors including old unit 11 and 12 I/Omodules. Found loop 1 had been junctioned in the panel to include a circuit that ran underground into a conduit below ground floor riser.Disconnected junction and connected old loop circuit into card so that I/O modules weren’t on the loop and earth fault cleared. Deletedmodules from program as no longer in use (now used melaleuca prison). Panel clear no fau
MSA-DCS | WA3201592 | Unit 5-Console in the Master control room Battery is showing low-MB | Bandyup Prison | GMP-BR- HO | Building | General Building (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Apr 2020 | 2020-04-14 19:28:24 | 2020-04-14 15:00:00 | Pass | Travelled to site, replaced 1x 12vdc 7ah battery in unit 5 house 1. All replaced and tested ok. Job complete
MSA-DFES | WA3201539 | Warning strobe lights not working, door number 3 | CFRS Rockingham- TO BE DECOMMISSIONED Rockingham FS-Main Building | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 13 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-13 13:40:00 | Pass | Arrived onsite and spoke to senior officer, senior officer advised me that another contractor had been called out and that he was organising a specialist contract for the required job. He contacted programmed and was happy with the process.
MSA-DFES | WA3201564 | Warning strobe lights not working, door number 3 | CFRS Rockingham- TO BE DECOMMISSIONED Rockingham FS-Main Building | GMP-BR | Electrical | General Electrical (EL) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 13 Apr 2020 | 2020-04-14 17:00:00 | 2020-04-14 09:59:59 | Pass | Technician attended the site of Rockingham Fire Station Volunteers Door # 2 on 14/04/2020. Following full test and inspection of door components identified that the strobe light working fine. Technician modified setting to ensure operationSETTINGS CHANGED ON CONTROLLER AND RECTIFIED - TESTED OK
MSA-DCA | WA3204265 | Emergency Exit lighting UPS fault | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 16:02:00 | Pass | UPS inverter and rectifier test correctly but Battery fuses have blown due a recent power outage. UPS left in bypass and isolate due to recommendations.Quote to be supplied for Recommendations:Replacing battery fuses.Replace AC and DC capacitorsReplace cooling fans
MSA-DCS | WA3202154 | ELEC Monitoring panels - Zone 16 keeps alarming, voltage is out of range | West Kimberley Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Apr 2020 | 2020-04-14 11:02:11 | 2020-04-17 19:17:00 | Fail | Checked fence and removed debris from the fence.Tested fence and confirmed activation.Fence zone sealed
MSA-DCS | WA3202430 | Cell C16 - 2 windows are broken - needs glazier | Hakea Prison-Relocatable living unit | WSM-BR-SITE | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 14 Apr 2020 | 2020-04-14 09:05:34 | 2020-04-14 12:00:00 | Fail | OBS PANEL RE GLAZED - CELL WINDOW TO BE RE GLAZED ON WA3234822
MSA-DCS | WA3202540 | unit 9 C10 Glass viewing hatch cracked | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 06:05:37 | 2020-04-14 10:30:00 | Pass | reglazed obs window
MSA-DCS | WA3202543 | Unit 7 cell H7 Cell Call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-17 10:30:00 | Fail | Replaced damaged cell call, job completed.
MSA-DCS | WA3202550 | Zoom Cameras are not activating when the alarms set off | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Apr 2020 | 2020-04-14 10:16:33 | 2020-04-14 11:00:00 | Fail | Travelled to site and reset senstar server and indigo NVR.Made site all zones were activated correctly on software. Logged control into correct operator group log in. Retested zones and all zones and cameras activated correctly. Job complete
MSA-DCS | WA3202552 | Unit 10 Cell B6 Ceramic sink broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-14 12:18:00 | Pass | Went inside to investigate found no broken basin
MSA-DCS | WA3202560 | Unit 5 A wing Exhaust Fans Not Working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 06:22:39 | 2020-04-14 15:00:00 | Pass | Ex fans not working
MSA-DCS | WA3202563 | Unit 1 D9 CCTV camera cover damaged | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-05-05 13:34:00 | Fail | Attended site, found camera is a FLIR CC-3103 and requires replacement glass/perspex for lens.Scratch/crack is not interfering with camera image.job will be completed under WA3253947
MSA-DCS | WA3202567 | kitchen front door Door Lock Faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-14 15:15:00 | Pass | Repaired kitchen front door
MSA-DCS | WA3202594 | Unit 2 S/O's office Air Con Faulty-see notes | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-16 08:23:00 | Pass | Arrived on site and signed in tools, checked over aircond found to be running ok, checked pressures and operation,no sign off rats or mice,all cables look ok,system running as normal.
MSA-DCS | WA3202680 | visits area Visits 1 door is not opening with the key. Currently only being opened electronically. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-05-29 12:30:00 | Fail | Job completed - remove lock for repairs, beyond repair, installed temp lock. replace lock and relocate electric trike to allow correct operation
MSA-DCS | WA3202685 | Unit 2 - B & D sliding window in cell D13 Unit 2 was shattered/broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-20 08:45:00 | Fail | Job Already completed
MSA-DCS | WA3202707 | Unit 6 - D Wing cleaning cupboard,down pipe on the right hand side of the sink leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-05-15 11:00:00 | Fail | Replace copper pipe work in cleaning store.
MSA-DCS | WA3202715 | Edvoc 1 class 3 Broken lower sash window Approx 500 x 650 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-16 10:30:00 | Pass | reglazed
MSA-DCS | WA3202722 | unit 3 PIR are continue to activate on night shift | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 07:55:51 | 2020-04-29 16:13:00 | Fail | Checked terminations. Reset masking Tested ok
MSA-DCS | WA3202728 | Unit 3 - A & C tap in A13 is not faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-14 13:00:00 | Pass | Remove and replace faulty quarter turn spindle on basin
MSA-DCS | WA3202755 | Unit 4 - A & C flooring is badly bubbled and lifting in front of oven- trip hazard | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-08-03 14:44:00 | Fail | THIS JOB WAS ATTENDED TO BY OUR GUYS ON THE 20/04/2020 AND VINYL CONTRACTOR ORDERED, COST TO DATE IS THEIR LABOR, - NEW JOB WAS ISSUED (WA3504998) AND VINYL CONTRACTOR RE-ORDER TO COMPLETE ON NEW JOB
MSA-DCS | WA3202762 | ISU C wing front door lock faulty (keys getting stuck YCO lock) | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-14 13:55:00 | Pass | Replaced Front door YCO Cylinder with new to replace old faulty Cylinder key was getting stuck in
MSA-DCS | WA3202766 | gatehouse internal perimeter Lights not working Zone 16 & 17 | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-05-13 15:30:00 | Fail | Replace perimeter light, cherry picker needed
MSA-DCS | WA3202768 | Education External Art room door not locking | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 08:25:48 | 2020-04-16 14:15:00 | Fail | Repaired door lock
MSA-DCS | WA3202788 | Urquhart upstairs office Toilet exhaust fan not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-22 08:00:00 | Fail | Attended Urquhart - had to get parts waiting for parts - in the mean time AAS completed the job unbeknown to us.
MSA-DCS | WA3202793 | External Education corridoor door lock sticking | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 14:45:00 | Pass | Repaired lock
MSA-DCS | WA3202798 | kitchekn cooking bell not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 08:37:44 | 2020-04-14 12:50:00 | Pass | Dry out lots of water from side box also replaced switch and 2 lamps on control box. Reset & test ok.
MSA-DCS | WA3202823 | Amenities Ladies changing rooms. Second sink from right tap leaking continuously | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-05-05 12:30:00 | Fail | Remove and replace 1/4 turn spindle
MSA-DCS | WA3202824 | Jasper, B Wing, Day room - broken window - Approx 1200x500 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 12:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3202830 | Turner office - all cell calls to office can be heard through cell #B03 | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 10:22:00 | Pass | Cell B3 overhearing calls, re established ACM file with node 7 CI3210 controller, cell restored now functioning correctly, possibke bug in original ACM file.
MSA-DCS | WA3202832 | MPU (8) - M7 no power to cell | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 10:30:00 | Pass | Repaired damaged gpo in mpu m7
MSA-DCS | WA3202833 | Unit 13 - B & D-D8 tap need new washer /leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-15 08:00:00 | Pass | Remove and replace one quarter turn cold water spindle in Plumbing duct
MSA-DCS | WA3202836 | MPU (8) - M13 No power in cell | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 09:30:00 | Pass | Repaired damaged cell gpo in m13
MSA-DCS | WA3202837 | Unit 3, Control Room - cell call console, constant flashing warning - networkk error | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-14 09:30:00 | Pass | Attended unit 3, found cell call system indicating network error, network appears correct, network indicating errir due to kitchen temporarilly offline, tested system fully operational.
MSA-DCS | WA3202853 | Unit 6 - B & D wing door no power to wing door from control room panel can only be opened by key | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 13:00:00 | Pass | Picked part for repair, replaced push button afor new, soldered connections mounted and tested fully operational.
MSA-DCS | WA3202856 | Unit 13 - B & D Oven seal from the side has come apart. Does not heat up properly | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-17 09:25:00 | Pass | Replaced Doorseal, test for leaks, all ok
MSA-DCS | WA3202860 | Unit 3, C Wing- Water leaking from cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-16 13:00:00 | Pass | Run both basins and flush both toilets in cells 7 and 8. No leak found in cells or Plumbing duct.
MSA-DCS | WA3202861 | Unit 13, B & D, cell D8 - the cold water tap when turned on very slightly, jets water out of spout | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-14 16:00:00 | Pass | Remove and replace vandalised aerator in basin tap
MSA-DCS | WA3202864 | Unit 3 - B Wing-CELL B12, DOOR WILL NOT CLOSE AND STAY CLOSED UNLESS DOUBLE LOCKED. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 09:00:00 | Pass | adjusted hinges
MSA-DCS | WA3202870 | Unit 14 - B & D oven has had the safety grill covering the fan removed | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 09:03:01 | 2020-04-14 11:20:00 | Pass | Remount safety grill
MSA-DCS | WA3202871 | INF (10), toilet in the main communal toilet in infirmary - not flushing properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-14 15:00:00 | Pass | Officer who recorded fault is not working. We checked all communal toilets and no issue was found.
MSA-DCS | WA3202873 | Unit 3,A Wing, Cells A8 & A9- smell coming from sewerage | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-16 11:00:00 | Pass | Flush toilets and run basins, no leaks found. Moflo floor waste in duct and rinse.
MSA-DCS | WA3202877 | Unit 5 Cell D3 Toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-14 14:00:00 | Pass | Adjust push button assembly in plumbing duct and test.
MSA-DCS | WA3202878 | Unit 5. D wing. Cell D03- Toilet is not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-14 12:00:00 | Pass | Replace worn outlet rubber in plumbing duct between D3 and D4 on cell D4
MSA-DCS | WA3202881 | Unit 1, B & D - kitchen day room faucet has come off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-14 11:00:00 | Pass | Reattach spout and thread paste grub screw.
MSA-DCS | WA3202947 | Kitchen- Cool Room fridge runner needs adjustment | Casuarina Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-14 14:45:00 | Pass | Warranty repair required.
MSA-DCS | WA3202988 | Unit 2 - A Wing Cell A7, Window frame damaged. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-20 09:45:00 | Pass | SPIRAL BALANCES RENEWED
MSA-DCS | WA3203085 | Unit 1, D Wing, Cell D13- Reading light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-14 09:35:00 | Pass | Repaired damaged cell light in unit 1.Job radioed through late afternoon 13/4/20
MSA-DCS | WA3203228 | Unit 5, Cell C10- Cell window is broken | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-28 11:00:00 | Fail | CELL WINDOW RE GLAZED
MSA-DCS | WA3203458 | Unit 1, Cell A2- Light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-14 12:30:00 | Pass | Repaired light
MSA-DCS | WA3203808 | Unit 3 - Control Room-Control room carpet damaged. Trip hazard. | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-09-29 11:30:00 | Fail | Carpet tiles replaced
MSA-DCS | WA3203811 | Unit 7, D Wing-Dryer is faulty | Casuarina Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-20 10:30:00 | Fail | Unit 7 D Wing Dryer faulty. Remove dryer for repairs. Dismantle, remove broken door lock and drive belt. Replace drive belt & door lock. Repair element wiring damaged by belt. Clean out fluff. Assemble & test, return to store.
MSA-DCS | WA3203856 | Cameras IRB 23 is not activate & alarm keeps tripping | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Apr 2020 | 2020-04-14 13:59:48 | 2020-04-16 11:37:00 | Fail | Investigated faults. Repaired server comms fault between Melaleuca and Hakea which was preventing camera switching.Tested OKJob CompleteParts:Consumables
MSA-DCS | WA3203864 | Ass Dir Office,Pilbara Wing and Stationery Store lights flashing and buzzing | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 12:15:00 | Pass | Replaced lamps and starters , test ran ok.
MSA-DCS | WA3203884 | unit 1 cell B18 prisoner lock not woking SITE COSTED | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 14 Apr 2020 | 2020-04-14 14:21:20 | 2020-04-14 11:50:00 | Pass | unit 1 Cell B18 - prisoners privacy lock is not working new privacy lock fitted ,and main cell lock strike adjusted
MSA-DCS | WA3203885 | recreation door lock not working SITE COSTED | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 14 Apr 2020 | 2020-04-14 14:23:42 | 2020-04-14 12:30:00 | Pass | Whilst at Bandyup Womens PrisonEntry into Recreation office - lock is not functioning correctlyNew barrel fitted .
MSA-DCS | WA3203960 | Unit 5, front entrance - disconnect damaged electrical wires and light from support post | Casuarina Prison | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 11:13:15 | 2020-06-12 10:00:00 | Fail | Isolated and removed damaged external light on unit 5 pillar. Returned once pillar was installed and re-installed external light and tested
MSA-DCS | WA3203964 | zone 3 cowling continues to activate-SEME on site | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Apr 2020 | 2020-04-14 15:15:49 | 2020-04-14 13:01:00 | Pass | Reset senstar controller and tested and of line for correct resistance reading. All measured ok. Reset and retested zone. All tested and working correctly. No false activations. If issue re occurs then recommend replacing senstar module located in EC3
MSA-DCS | WA3203965 | Vegetable Preparation, Workshop - potato rumbler stopped working | Casuarina Prison | WSM-BR-SITE | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-17 12:00:00 | Pass | Reconnected potato rumbler in veggie prep
MSA-DCS | WA3204004 | Unit 4, L 47 - Fluro banten broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-17 11:00:00 | Pass | Investigate unit 4 cell L47 Fluro light. Source replacement parts. Replace light in cell.
MSA-DCS | WA3204013 | Unit 3, A10 - Main light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-15 08:30:00 | Pass | Investigate and replace light in unit 3 cell A10
MSA-DCS | WA3204038 | Unit 1, Control Room - smoke detector keeps beeping | Hakea Prison | GMP-BR- HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 12:06:17 | 2020-04-15 08:30:00 | Pass | Unit 1 vesda continuously beeping. No fault and/or beeping on arrival. Checked logs to see vesda had been isolated at 1552 on the 13/4/20 by staff. Isolation then removed the following day. This would have caused continuous beeping due to isolate/ fault reminder. All airflow correct. Smoke thresholds adjusted to lessen alert level alarms.
MSA-DCS | WA3204045 | Metal workshop- RCD needs replacing | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-17 15:00:00 | Pass | Investigate guillotine circuit breaker tripping. Circuit breaker requires replacement. Source parts. Replace circuit breaker.
MSA-DCS | WA3204047 | Unit 2, d wing - grille lock faulty, works with some keys and not others | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 12:13:37 | 2020-04-14 16:30:00 | Pass | repaired grille lock
MSA-DCS | WA3204051 | Unit 5, front courtyard brick pillar severly damaged ,will need removal & rebricking | Casuarina Prison | GMP-BR- HO | Building | External Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 12:10:26 | 2020-06-10 14:30:00 | Fail | BRICK PILLAR REMOVED AND REPAIRED
MSA-DCS | WA3204075 | Unit 4 - #29 Perimeter EC4 power low | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 12:30:47 | 2020-04-15 08:00:00 | Pass | Multiple zones alarming regularly. Reset all perimeter modules and unshunt problem zones. False alarms no longer occurring. If occurs in the future trial of new product may be recommended.
MSA-DCS | WA3204099 | Unit 7 B Wing - Faulty Cooktop | Casuarina Prison | SPA-BR | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-05-12 11:25:00 | Fail | Installation of new stove/oven as required & approved
MSA-DCS | WA3204203 | Unit 9, A/B dayroom - 4x dayroom windows smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 14:25:04 | 2020-04-22 13:00:00 | Fail | TEMP PANELS REMOVED - WINDOWS RE GLAZED
MSA-DCS | WA3204215 | Unit 14, B wing - sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-16 10:00:00 | Pass | Plunge sink to no avail, remove trap in duct and clear blockage. Reinstall and test.
MSA-DCS | WA3204220 | Unit 5, the whole unit -PA system stopped working | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-15 10:00:00 | Pass | Unit 5 PA system found failing to operate, checked phone line via butt phone operational,checked small supply unit and amplifier ok, checked direct line faulty, reset trunks and phone line restored, PA system tested fully operational.
MSA-DCS | WA3204231 | Omnitrax processor 1 offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-20 08:58:00 | Pass | Tested cables and found resistances is in the correct range.Tested board with PFM spare, No change.Reloaded configuration and calibrated.All zones activated.Left senator OT processor on site as spare
MSA-DCS | WA3204235 | Zone 16,17,21 MW no activation | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-17 19:13:00 | Pass | Replaced fuses in EC 7 and re aligned microwavesTested and confirmed activations
MSA-DCS | WA3204239 | Zone 8 MWH no activation | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-19 16:10:00 | Pass | Realigned microwave and testedCorrect operation
MSA-DCS | WA3204246 | Zone 16,17 MWH and MWL no activation | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Apr 2020 | 2020-09-28 17:00:00 | 2020-04-17 10:00:00 | Pass | Tested controller and found GBUS 1 dropping offline intermittently.Swapped controller out with Gallagher 6000 High spec from Site stock, loaded correct software and tested.Back online and operational.Gallagher 6000 High spec controller to be order to replace site stock
MSA-DCS | WA3204250 | Level 1, room 1.C & 1.A - faulty lights | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 11:00:00 | Pass | Repaired lighting in rooms.
MSA-DCS | WA3204258 | Key watcher- Batteries are low and need replacing | Bandyup Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 15:37:16 | 2020-04-15 09:03:00 | Pass | Collected parts and replaced 4x 12vdc 7ah batteries in keywatcher. All replaced and tested ok. Job complete
MSA-DCS | WA3204311 | Unit 2-Cell B 11 -Cell door and prisoners lock is jammed | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 18:16:52 | 2020-04-15 08:30:00 | Pass | Repaired personal lock
MSA-DCS | WA3237109 | Retrospective work order do not attend-Wireless receiver in fault | Maddington (South East Metro) | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 14 Apr 2020 | 2020-04-20 17:00:00 | 2020-06-26 17:30:00 | Fail | Attended site. Found Inovonics duress receiver offline. Tested power supply, tested ok. Issue with receiver itself. Sourced replacement unit and returned to site, Installed in place of old unit. Enrolled existing duress pendants on site into new receiver and tested in full through to monitoring. Tested ok. Works complete
MSA-DFES | WA3203882 | Applied training ground - bottom dam pump is not turning on | FESA RHQ - Forrestfield | GMP-BR | Mechanical Services | Pumps (MS) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-06-26 16:06:00 | Fail | Panel and control upgrades as per quote submitted.
MSA-DFES | WA3203909 | Dorm - Air Con is leaking | CFRS Duncraig | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 11:53:00 | Pass | Unblocked and fixed drain
MSA-DFES | WA3204010 | L2 board room kitchen billi unit is flashing | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 10:10:00 | Pass | Unit requested to be replaced
MSA-DFES | WA3204102 | Applied training ground - ensuite dongas - 1 fluro light not working and 1 exhaust fan not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-21 14:00:00 | Fail | Replaced faulty fan with new
MSA-DFES | WA3204198 | Applied training ground - Fire hydrant has been damaged | FESA RHQ - Forrestfield | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Critical Fire Protection & Training | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 13:00:00 | Pass | as per signature slip
MSA-DFES | WA3204210 | Applied training, Staff Change Room, Room 8 - Air Con has to have fresh air increased | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-06-12 09:30:00 | Fail | Travel to site, commission the fresh air fan and make sure there is 200 L/s coming out of the outlet
MSA-DFES | WA3204223 | Industrial pad, Leaking gas valve M | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | WA BOILER SPARES & SERVICE | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-17 11:00:00 | Fail | Attended site, repaired gas leak on gas isolation valve spindle
MSA-DFES | WA3204229 | Kitchen- Tap is leaking | CFRS Joondalup | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 08:45:28 | Pass | Repair taps in kitchen and s/o bathroom
MSA-DTAG | WA3202742 | Intercom not working again - continuously beeping noise | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-14 11:00:00 | Pass | Checked all Intercoms. Intercoms were offline to Server. When Optic Fibre switch was reset, Intercoms OK
MSA-DTAG | WA3202745 | cameras down no visual in our control room . see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 14 Apr 2020 | 2020-04-14 12:08:37 | 2020-04-14 10:30:00 | Pass | Job completed - Optic Fibre switch down. Reset and resynced all Pacom controllers.
MSA-DTAG | WA3203132 | Level 5, court 57 - flickering lights in courtrooom | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 08:00:00 | Pass | Job complete
MSA-DTAG | WA3203807 | Level 5, Sherriffs office - flashing lights | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 09:30:00 | Pass | Job complete
MSA-DTAG | WA3203839 | Level 3, Court 36 - desk in courtroom is loose and needs to be screwed down | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-28 08:15:00 | Fail | BENCH TOP RE SECURED
MSA-DTAG | WA3203843 | Level 3, Kitchen - two lights are not working and the fire escape green sign is flashing | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 11:15:00 | Pass | Job complete
MSA-DTAG | WA3203991 | Room 102 - Make good skirting | Supreme Court | GMP-BR-HO | Carpentry | Joinery (CA) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-14 14:30:00 | Pass | SKIRTING REMOVED
MSA-DTAG | WA3204226 | Isolate system to allow mechanical repair | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-18 12:37:00 | Pass | Isolated and de isolated panel for contractor works to be completed
MSA-DTAG | WA3204271 | Cells 1 and 3 in custody center - see further notes below | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 15:17:00 | Pass | Work done in two partsCell 3 Start 14/04/20 5:00 pm Finish 14/04/20 7:30 pmCell1 Start 15/04/20 2:45 pm Finish 15/04/20 3:17 pm
MSA-DTWD | WA3203688 | E Block, Room EG07 - Faulty 4 gang light switch. | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-17 09:11:00 | Pass | Replaced faulty light switch with new.job completed
MSA-DTWD | WA3203822 | canteen Speaker torn from ceiling, repair/replace. | Rockingham Campus | GMP-BR-RC | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-16 16:10:00 | Fail | Attended site and signed in. Located damage speaker speaker in canteen. Picked up new speaker and replace. All now working. Informed staff of job completion
MSA-DTWD | WA3203829 | Lvl 2, Room A214- Air Con has no power | Perth Campus B5 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-15 16:02:00 | Pass | Received job and traveled to site collected keys and attended building 5 located split unit and carried out investigation. Checks for power to indoor unit. Gained access to outdoor unit and checks for power. Checked for power at isolator. No power present at unit. Returned to level 2 and located power service boards. Bracker could not be located. Returned to roof plant area and checks mssb for braker. Unit power supply identified and braker reset. Carried out full operation tests on unit monitored for correct cooling and function. Tested fans. No further fault has occurred. Unit may have had a power surge leading to braker to trip. Work area left tidy.
MSA-DTWD | WA3203840 | Lvl 2, Library- Reception desk is damaged | Perth Campus B2 | GMP-BR | Furniture | Office Furniture (FU) | AWB Co. | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-14 14:30:00 | Pass | Attend site Speak to facilities Got access to library building 2 Book scanner units to be mounted under side of desk location 1 Location 2 Cut batten and melamine sides to fit scanner within cupboardLeft site to get channel and materials to make brackets etc Returned and brought tools and equipment in Mark and cut Chanel for location 1 fit to desk and mount scanner Mark and cut batten out for location 2 Cut melamine Mount bracket Drill hole and pull cable through Mount scanner Clean up Remove rubbish
MSA-DTWD | WA3203917 | K block, ground level, K12(male) & K14 (female) toilets - no power on two ceiling lights, | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-17 09:16:00 | Pass | Replaced blown fuses to lights in toilets. Job completed
MSA-DTWD | WA3203920 | A Block, Main Carpark in front of Admin- Faulty PA horn speaker, may possible be loose wiring | Carlisle Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 09:15:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro TAFE - Carlisle Campus, Bank Street, Carlisle WASite contact: Frank Femia- 9267 7162Work Order Number: WA3203920Call out Date: 14/04/2020Target finish: 17/04/20 17:00pmOriginal information: A block, Main carpark in front of admin- Faulty PA Horn speaker, may possible be loose wiringAttended site:Date:15/4/10Start Time:8.00Finish Time:9.30Techs on Site: 2Works Carried Out: Found cable to speaker has been cut in 2 places. Joined and also tidied up conduit work. All OK
MSA-DTWD | WA3203932 | K Block, K20 (games room) - water leaking from ceiling | Midland Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 14 Apr 2020 | 2020-04-17 17:00:00 | 2020-06-08 15:00:00 | Fail | cleaned box gutters out. removed worn silicone from each joint. prepped joints and dried, resealed each joint .
MSA-DTWD | WA3204158 | K Block, ground level K01, Fire hose reel cupboard - termite nest | Midland Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 3 | CLOSE | 14 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-20 09:55:00 | Pass | Treated active termites to fire cupboard, skirting board and kitchen cupboard with Fipronil @ .6%
MSA-DTWD | WA3204266 | Door bell outside reception not working | West One Services | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 14 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-16 12:15:00 | Fail | Job complete
MSA-DTWD | WA3509151 | Retrospective work order-L1&2 Comms cupboards Replace out of date back-up batteries to 2 panels | Perth Campus B4 | GMP-BR | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 14 Apr 2020 | 2020-04-20 17:00:00 | 2020-05-06 06:34:00 | Fail | job completed - Collected batteries from supplier and attended site.Installed batteries to both access cabinets at 133 Newcastel st. Checked and confirmed powersupply voltages and confirmed back up battery function
MSA-DCS | WA3208444 | L4 Desk W4.43 Light flashing, please change globe. | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 12:00:00 | Pass | Repaired lighting.
MSA-DCS | WA3208504 | boiler house-Tv signal problem, antenna located above Boiler House | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 3 | CLOSE | 15 Apr 2020 | 2020-04-21 17:00:00 | 2020-06-17 12:30:00 | Fail | Job completed - 17/04/2020 Attended site. Job changed to Cabinet & Paint Shop requiring TV points. Assessed parts required.Technician to source parts and return.17/06/2020 - Job completed, works to be completed under WA3252139
MSA-DCS | WA3208511 | unit 6 day room elec fault with burning smell | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 15 Apr 2020 | 2020-04-15 11:53:03 | 2020-04-15 10:00:00 | Pass | Replaced damaged power point
MSA-DCS | WA3208529 | Admin tea room dishwasher door not closing failing to seal | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 09:00:00 | Pass | Admin dishwasher door faulty. Check washer & controls. Found lock catch faulty. Repair latch on lock. Assemble & test. All working correctly.
MSA-DCS | WA3208544 | External zone 10-16 ramp up lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 15:00:00 | Pass | Repaired ramp up lights
MSA-DCS | WA3208545 | Jeelia C wing Right hand side of hob, electrical socket not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 10:00:00 | Pass | Repaired damaged hob socket in jeelia c wing.
MSA-DCS | WA3208549 | Jeelia C wing Airconditioner not working Vibrating on roof noisey | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-15 13:30:00 | Pass | Bearings on motor failed. Motor replaced. All ok
MSA-DCS | WA3208551 | Unit 14, C wing, C15 - Shower drain seems blocked. water is going down slowly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-16 12:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3208554 | Cell A1 in Unit 14. The shower is blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-16 14:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3208556 | Visits area, toilet - blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-15 09:00:00 | Pass | Water has been isolated and the toilet has been marked and taped out of service. A contractor off the build site must have come down from the roof space (there is no ceiling) and used the toilet and not been able to flush. We have cleared the toilet using buckets of water.
MSA-DCS | WA3208557 | Unit 2 - B Wing Shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-15 15:00:00 | Pass | Plunge shower drains to clear blockage and test.
MSA-DCS | WA3208568 | Visits Area - Toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-24 12:00:00 | Fail | Plant store to clear blockage
MSA-DCS | WA3208591 | perimeter CCTV Camera 7 & 16 flickering image | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 09:11:43 | 2020-04-15 12:38:00 | Pass | Travelled to site and found cameras 7 and 16 flickering. Reset fiber modems from gatehouse and still had same issue. Located perimeter fiber modems in EC cabinet and reset modems. Retested cameras and all tested and working correctly. Job complete
MSA-DCS | WA3208598 | Unit 2, A wing, middle shower not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-16 09:00:00 | Pass | Make new spindle connector and install. Replace missing split pins.
MSA-DCS | WA3208608 | Unit 2, A wing, A11 - Window mechanism has broken again, making it impossible to open & stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-05-19 12:34:00 | Fail | works to be completed on LVM job number WA3338133
MSA-DCS | WA3208610 | Health Admin light in the X Ray room in the old Health Administration building is not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 08:30:00 | Pass | Investigated lights in health administration. Found construction site has disconnected lights in X-ray room. Advised staff
MSA-DCS | WA3208616 | Unit 7, C wing - Oven light needs replacement | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 10:20:00 | Pass | Remove lamp holder, adjust terminals, refit then replaced lamp. Assemble unit & test functions & lamp ok.
MSA-DCS | WA3208623 | Kitchen- Fridge not working (sitting on 26 degrees) | Banksia Hill Detention Centre | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 11:45:00 | Pass | Connection repaired. Unit operational.
MSA-DCS | WA3208625 | Unit 6, Cell 11 - faulty/broken GPO | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-15 11:00:00 | Pass | Replaced cracked power point
MSA-DCS | WA3208627 | Unit 3, staff toilets - light switch MECH faulty | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-15 13:00:00 | Pass | Waited in lock down for access. Replaced cracked light mechanism
MSA-DCS | WA3208630 | Internal stores, garden storage shed - Back Flow water valve is leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 17:45:00 | Pass | Replace backflow
MSA-DCS | WA3208644 | Unit 3, D15 - light hanging off ceiling | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 09:57:45 | 2020-04-15 15:00:00 | Pass | Replaced light
MSA-DCS | WA3208650 | Unit 3, D15 - smoke detector melted | Hakea Prison | GMP-BR- HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 10:06:15 | 2020-04-15 13:15:00 | Pass | Replaced burnt sampling point with new
MSA-DCS | WA3208661 | Unoit 1, Cell B13 - power point & TV antenna hanging off wall | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 10:16:09 | 2020-04-15 13:00:00 | Pass | Replaced gpo and antenna point
MSA-DCS | WA3208668 | Unit 3 D wing 03 faulty light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 15:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3208689 | Unit 7, E wing, Cell 1 - window is cracked and broken | Hakea Prison | GMP-BR- HO | Glazing | Glass wall (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 10:27:02 | 2020-04-15 15:00:00 | Pass | re glazed window
MSA-DCS | WA3208696 | skills workshop PTZ camera 37 rotating or zooming | Boronia Pre-release-AS20 - Industries Vocational Skills Development-Ground Floor | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 10:34:14 | 2020-04-15 15:00:00 | Pass | Travelled to site and found camera 37 had no movement, reset indigovision joystick and reset indigovision CCTV workstation for monitor video wall. Reloaded camera video wall and tested camera 37. All tested and working correctly. Issue was with connection between joystick and indigovision control centre.
MSA-DCS | WA3208702 | Boiler house, Boiler 2 - water level glass leaking from boiler 2 | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 09:00:00 | Pass | Attended site to repair leaking gauge glass on Boiler #2.
MSA-DCS | WA3208728 | Unit 2, C13 - observation light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 09:00:00 | Pass | Replaced blown fuse and test lights
MSA-DCS | WA3208731 | Mulitple Perimeter microphonics & alarm issues | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 10:50:12 | 2020-04-17 12:00:00 | Fail | Outer 9MX - found break in cable and repaired. Tested ok. 3 and 12 OX - run plot graph. Calibrated and tested okInner 12 and 13MX - tested okParts used:2 x microphonics Splice kits
MSA-DCS | WA3208735 | Unit 5, B3 - light not working but cell still operable | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 13:00:00 | Pass | Repaired light
MSA-DCS | WA3208744 | Unit 9, A13 - Medical hatch can be open from inside the cell | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 11:00:11 | 2020-06-04 10:00:00 | Fail | supplied and installed replacement hatch.
MSA-DCS | WA3208753 | East Gym -re run pipe damaged to gym east, valve damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 11:05:18 | 2020-04-15 16:45:00 | Pass | Rerun new water line to hot water unit in the gym.
MSA-DCS | WA3208759 | Unit 3, B11 - Blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-16 15:00:00 | Pass | Plunge sink to clear blockage and test.
MSA-DCS | WA3208761 | Crypt - Plant-Room-air con has mouldy smell issues | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 15:30:00 | Pass | Drain altered to suit. Tested flow. All ok. Eliminated odour.
MSA-DCS | WA3208762 | Abbaitor- Main power board, tripping power | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 13:00:00 | Pass | Investigate abattoir tripping power. Traces fault to faulty element. Source replacement parts. Replace element.
MSA-DCS | WA3208766 | Unit 6, Day Room- Zip hot water unit, electrical fault | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 11:14:19 | 2020-04-23 15:00:00 | Fail | Technician installed maxiflow scale & wilson system. Removed old unit. Installed New Capex Assets 1 x Maxiflow Scale System A40184127G + Wilson WB90 Hot Tap SN R2766102 Prog Number A40184128H removed old to tip
MSA-DCS | WA3208770 | Kitchen, water leak in ceiling | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 11:16:19 | 2020-04-20 13:15:00 | Fail | COMPLETED
MSA-DCS | WA3208773 | Kitchen- 70mm copper pipe suspended off the floor | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 11:17:18 | 2020-04-15 15:30:00 | Pass | COMPLETED
MSA-DCS | WA3208778 | external door to building pin coming out of hinge-photo to follow | Midland (North East Metro) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 09:00:00 | Pass | Attended site and reinserted hinge pins on external door, carried out inspection on all external doors.
MSA-DCS | WA3208809 | Yeeda, education class 1 - smashed window to bottom door panel (approx 800x600) | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 15:30:00 | Pass | DOOR PANEL RE GLAZED
MSA-DCS | WA3208811 | Unit 13, Cell C13- Window stays are not working | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-07-02 10:00:00 | Fail | STAYS REPAIRED - LUBRICATED
MSA-DCS | WA3208848 | Bakery, workshop - Bun rounder machining is not operating due to the outer ring not dropping | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-15 16:30:00 | Pass | 15/04/2020 - Called as requested to the BDR ceasing up. Cleaned and oiled tested all ok.
MSA-DCS | WA3208868 | Kitchen- Air Con B Side Dining room very noisy | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 12:14:13 | 2020-04-21 13:00:00 | Fail | Further works as described in the BRAF now completed, unit is in bad condition. Rough estimates put in place for future replacement.
MSA-DCS | WA3209020 | ISU, A Wing. Air Con leaking from roof | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-05-13 15:30:00 | Fail | Complete
MSA-DCS | WA3209028 | Industries Admini Office lock going in to haircut room (next to industries control) is not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 12:15:00 | Pass | replaced bolt throw and install door bumper.
MSA-DCS | WA3209029 | INF (10) - Maytag Dryer not heating, drum rotating | Casuarina Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 14:00:00 | Pass | Infirmary dryer has no heat. Check dryer & controls. Remove & dismantle, clean out fluff. Check element wiring. Repair burnt out connection on element. Replace filter. Assemble & rest. Return.
MSA-DCS | WA3209035 | Unit 6 - A & C Cold water tap in day room leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-05-04 08:00:00 | Fail | Remove and replace faulty quarter turn cold spindle in day room
MSA-DCS | WA3209066 | SOG Base - Electrical power switch plug that goes into vehicle does not work | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 14:37:19 | 2020-04-16 11:00:00 | Pass | SOG Base GPO Smashed - Relocated so it cant be run into again
MSA-DCS | WA3209070 | Lenard - Yard lights not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 09:00:00 | Pass | Repaired lights
MSA-DCS | WA3209084 | Murchison - Node 10 power failure | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-12-09 08:11:00 | Fail | 7/12/20 BG/EIAttended site & replaced the faulty Murchison DGP PSU OK.
MSA-DCS | WA3209118 | Unit 4, House K, Kitchen GPO circuit ELCD not tripping and it should | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 15:19:37 | 2020-04-16 14:00:00 | Pass | Repaired fault in switchboard
MSA-DCS | WA3209127 | Unit 2, B Wing- PA system is not working | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 15:36:05 | 2020-04-30 13:42:00 | Fail | Scope, improved design, acquire parts, prefabricate, install and test new PA installation in the NW corner of unit 2.
MSA-DCS | WA3209130 | Unit 1 Cell B11 - Cell door prsioner lock barrell is faulty SITE COSTED | Melaleuca Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 15 Apr 2020 | 2020-04-15 19:42:01 | 2020-04-15 17:00:00 | Pass | Replaced faulty lock.
MSA-DCS | WA3209183 | Perimetre fence camera not operating - Zone 3 camera 1 | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 21:38:27 | 2020-04-16 10:00:00 | Pass | Zone 3 camera 1 found operational, checked recordings to find a simgke block where camera changed to green screen power cycled both camera and encoder, camera ia fully operational, checked history om camera ok.
MSA-DCS | WA3209186 | Video link fire alarm error on system, audible alarm every 20-30 seconds | Hakea Prison-Main Gatehouse | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 15 Apr 2020 | 2020-04-16 03:13:12 | 2020-04-16 01:26:00 | Pass | 16/4/20 JN HakeaEarth fault intermittently on gatehouse FIP from 9pm to 11pm. When arrived no fault on panel and history logs show fault stayed clear for 1.5hours. Monitored FIP and checked all accessible heads nearby for obvious signs of corrosion or damage. 2 I/O modules showing on loop forunits 11 and 12 could possibly be issue but couldn’t locate. Fault stayed clear while on site, let SOG control know we are attending in themorning anyway.
MSA-DFES | WA3208515 | Station office bathroom, tap is leaking | CFRS Rockingham | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-15 14:15:00 | Pass | Replaced basin set
MSA-DFES | WA3209046 | Inside the station have found mouse droppings | VFRS Falcon | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-16 15:30:00 | Pass | Cleaned and rebaited existing stations - 1x Alpha, 1x Peti. Added baited stations to appropriate spots as required - 6x Beta stations.
MSA-DFES | WA3209177 | the cable of the roller door for the front room is snatched | CFRS Canning Vale-Main Building | GMP-BR | Building | Materials (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 10:00:00 | Pass | Technician attended the site of Canning Vale Fire Station Engine bay exit door #2 on 16/05/2020. Arrived on site and found firefighters had gone to call out. Waited 1/2 hour and spoke with Programmed. Left site as unable to gain access. Technicians returned on site on 17/06/2020. Removed damaged hinge, cables and brackets. S&I new cables and brackets. S&I new hinge and 2 wheels, straightened guides and refixed guide lugs to wall. Carried out full test of operation okFull test and inspection of door components completed prior to leaving site.
MSA-DTAG | WA3208618 | Court 3 Water drinking fountain in court 3 waiting room not working | Rockingham Justice Complex | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-23 14:14:00 | Fail | ATTENDED DIAGNOSED REPLACEMENT ASSETS REQUIRED CANNOT REPAIR COLD TANK SPLIT - RETURNED AND INSTALLED NEW MAXIFLOW FILTER SYSTEM A40190506E AND ZIP SITEMASTER FOUNTAIN MF 2020032403021 installed tested and commissions. Isolation still requires replaced. Hadn’t been done prior to Installation as requested
MSA-DTAG | WA3208805 | Levels 3 & 6 no visual for levels 3 & 6 in DMJC building | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-15 13:00:00 | Pass | Reset switches and re-establish connection
MSA-DTAG | WA3208816 | L1 court 1.01 duress is not working | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-15 13:00:00 | Pass | Job completed - Attended site. Found wiring fault, repaired wiring, tested and secured
MSA-DTAG | WA3208822 | Level 3, court 35 - Court 35 has a power issue with the JSO desk – AV have checked and all seems OK | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-16 07:45:00 | Pass | Job complete
MSA-DTAG | WA3208837 | Ground & 1st floor - various rooms - Emergency exit signs are loose and need reaffixed to the wall | Perth Children's Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 09:15:00 | Pass | Job complete
MSA-DTAG | WA3209051 | GAS meter enclosure cannot be secured, door appear damaged | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-06-17 12:00:00 | Fail | INSTALED NEW STEEL FRAMEWORK AND DOORS TO GAS METER ENCLOSURE
MSA-DTAG | WA3236488 | Hallway Db & RCD Failed (Circuit B1) - Retrospective Work Order | Armadale Courthouse | GMP-BR-HO | Electrical | Distribution Board (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 15 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 09:30:00 | Pass | Replaced faulty RCD to hallway db
MSA-DTAG | WA3254333 | L1 - NOT RESPONDING - Do not re-attend, refer # 51207531 | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 15 Apr 2020 | 2020-04-15 17:00:00 | 2020-04-15 13:30:00 | Pass | Adjusted several floor levels as lift was occasionally cycling doors at different floors. Monitored lift toensure lift would stay in service
MSA-DTWD | WA3208499 | Room B5 light switch arching | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 15 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-15 10:30:00 | Pass | Attended site and signed in. Located B5, found light switch with burnt out switch mech. Replaced with new and tested all okay. Job complete
MSA-DTWD | WA3208589 | T Block T201 Open plan Office area - Ceiling lights not working again. | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 15:30:00 | Pass | Attended site and signed in. Located faulty lights on level 2 T block. Found to be a different row not the same ones as last time. Removed covers and diffusers. Replaced tubes and refitted covers. Tested all okay. Job complete
MSA-DTWD | WA3208617 | H Bock, Outside pole light needs repair | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-30 18:59:00 | Fail | Replaced pole top with new.job completed
MSA-DTWD | WA3208658 | Level 2, tool store - Alarm on Tool Store Area 2 | Perth Campus B5 | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 15 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-16 14:59:00 | Pass | 15/04/2020, 1300-1400Zone 431 which is zone 4-11, replaced tool store pir
MSA-DTWD | WA3208712 | L1 east wing E104 AC unit not working in Office | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 16:39:00 | Pass | Accessed office being serviced by ac in fault. Test shows indr fan unit runs no out door unit activation on demand. Removed indr unit covers and found pwr ok. Isolated unit and removed cover. Found burnt comms wire into terminal .Rectified and repowered circuit. Tested on fan only, ok.Introduced cooling for comp and outdr operation.Unit came on and now operating as desired. Checked on heat too and ok. Left unit running for time to check repair. Ok. Unit returned to normal.
MSA-DTWD | WA3208724 | L2 B244 Replace broken seal around the glass window | Perth Campus B6 | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-16 08:52:00 | Pass | ATTENDED SITEREMOVED RUBBER FROM WINDOWRE POSITIONED GLASS AND REFIT RUBBERSEALED WITH SILICONE
MSA-DTWD | WA3208741 | L5 east male toilets Toilet constantly running | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 17:00:00 | Pass | Replaced broken cistern
MSA-DTWD | WA3208743 | E Block, Hallways, Male, Female & Staff Toilets - lights have blown | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-16 16:31:00 | Pass | Replaced all faulty downlight bulbs throughout e block as well as a faulty light switch 1 x light switch, 32 x globes.
MSA-DTWD | WA3208749 | L1 B120 Rectify door handle lock | Perth Campus B6 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 15 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-16 08:51:00 | Pass | Adjustment to handle B120Note: Job was completed 15/04/20 13:45-14:30. Promaps would not accept those times for some reason.
MSA-DTWD | WA3208838 | Vessel centre classroom- Unable to arm panel fault code #3 | Marine Vessel Centre | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-05-05 13:00:00 | Fail | 16/04/2020, 1015-1115Attend vessel centre classroom and test the test the alarm system all working when on site no faults at all note drop offand pick up key from one Fleet Street offices
MSA-DTWD | WA3208885 | O block - Security light cover missing at the rear of O block, needing replacing | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-05-20 10:30:00 | Fail | Attended site and signed in. Located car park drive way pole light at the back of O block to have missing diffuser. Can’t get parts for the old school lights. None on site either. Will need to replace to new led street light. Will organise parts and pricing. Ewp needed. Access easy from driveway. Upon testing the operation of external driveway and pathway lighting found W5 fuse blowing instantly. Various poles and pole tops are not working. Will require investigation to identify fault. Job not complete20/5/20. Replaced damaged pole top with new .tested grounds lights all working now in carpark. Job completed
MSA-DTWD | WA3209073 | N block rooms N3 and N8 alarm code not working-see notes | Rockingham Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 15 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-30 08:35:00 | Fail | Attend site and change codes for N block systems A/B test, all working
MSA-DCA | WA3227046 | ** Retrospective work order** DB MA NP Red 4 circuit not powered | State Library of WA-Main Building-Mezzanine | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-20 11:00:00 | Pass | Fault found lights to find that they were crossed with another circuit in the field. Seperated and made good.
MSA-DCS | WA3210587 | PFM critical spares stores – Rat infestations | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 07:13:43 | 2020-04-16 13:00:00 | Pass | Carried out a service for rodents at Hakea Prison critical spares stores. Installed three rodents stations in the in the shed and one under DDU subfloor. A monthly follow up is highly recommended to monitor and replenish the rodent stations.
MSA-DCS | WA3210596 | Kitchen west end sink restricted flow – TMV issue | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 16 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 12:05:00 | Pass | Replace aerator
MSA-DCS | WA3210640 | MPU (8) - West SPU shower tap not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 08:00:00 | Pass | Replace missing split pin in spindle in plumbing duct
MSA-DCS | WA3210754 | Unit 3, Cell D4- Light is broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-16 12:30:00 | Pass | Investigate and replace cell light in unit 3 cell D4
MSA-DCS | WA3210788 | Cooling pit emitting foul stench requires cleaning | Hakea Prison | SPA-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-08-05 11:30:00 | Fail | nil
MSA-DCS | WA3210810 | Unit 14, B14 - Blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-20 10:00:00 | Pass | Plunge sink to clear blockage. The sink was blocked with food scraps again.
MSA-DCS | WA3210814 | Unit 3 Cell B1 Cell call is static not clear | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 09:33:58 | 2020-04-20 15:00:00 | Fail | Job complete
MSA-DCS | WA3210839 | Kitchen, brat pan not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 09:58:22 | 2020-04-16 14:30:00 | Pass | Kitchen Brat Pan faulty. Check pan & controls. Repair wiring. Assemble & test.
MSA-DCS | WA3211088 | Unit 3, B1 - the door hinges need replacing/repair due to wear & tear. Cell door is hard to secure | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 14:30:00 | Pass | Replaced hinges, door plate and lock.On site weld on strike plate.
MSA-DCS | WA3211094 | Unit 5 - B Wing-cell B1 Botton bunk light needs replacing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-22 08:30:00 | Pass | Repaired faulty lights in unit 5 b1
MSA-DCS | WA3211131 | Unit 2, A & C day room- Window winding handle has snapped off | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-20 12:00:00 | Pass | RE SET, RE ALIGN WINDOW MECHANISM
MSA-DCS | WA3211136 | Unit 2 - wing ceiling lights faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-24 13:00:00 | Fail | Repaired multiple faulty lights in unit 2 wing corridors
MSA-DCS | WA3211216 | Health centre, office - lights broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-17 09:30:00 | Pass | Investigate and Replace lights in medical office
MSA-DCS | WA3211250 | Internal service road - camera pole has infestion of bees, bee hive | Melaleuca Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-05-21 08:30:00 | Fail | Working at heights with pest technician spotter to dust bee activity in CCTV Camera pole.
MSA-DCS | WA3211271 | Unit 3, B Wing- Fluro light end of corridor faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-20 09:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3211294 | Drain near large freezer, Drain cover needs to be plumbed into floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-17 11:35:00 | Pass | Cut down and Installed floor waste grate
MSA-DCS | WA3211297 | BR-Zone 13 internal micro phoenix is in constant alarm. | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 12:54:16 | 2020-04-17 13:00:00 | Fail | RECTIFY & FIX DAMAGED CABLE, TEST ZONE 13 MICROWAVE. BACK TO NORMAL OPERATION. PARTS USED CABLE TIES (SEME STOCK)
MSA-DCS | WA3211302 | Jasper, C Wing Lounge- Broken lower sash window Approx 500 x 500 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-05-07 10:15:00 | Fail | SASH WINDOW REGLAZED
MSA-DCS | WA3211308 | Unit 4, B Wing Showers- Fluro light faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-17 12:00:00 | Pass | Repaired light
MSA-DCS | WA3211309 | L1 W1.122 light has been removed needs to be replaced | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-20 10:00:00 | Pass | Repaired lighting.
MSA-DCS | WA3211314 | A-WING scenario control room - Repair training control equipment - no signal on computer screen | Nyandi Training Academy-Main Building | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-17 11:15:00 | Pass | Travelled to site, located equipment rack. Found battery backup turned off, possibly due to power outage. Reset and repowered UPS. Retested and all tested ok. Powered up duress computer and tested duress system. All tested and reset ok. Job complete
MSA-DCS | WA3211317 | unit 4 D13 Split copper pipe under basin | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 13:03:46 | 2020-04-17 10:19:00 | Pass | Installed new water line and Pilar tap
MSA-DCS | WA3211321 | Unit 3 C8 light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 13:09:39 | 2020-04-16 14:30:00 | Pass | Replaced broken light switch.
MSA-DCS | WA3211366 | L4 Glass sliding door onto floor next to large kitchen door not closing swip issue | Westralia Square | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 13:40:07 | 2020-04-16 15:30:00 | Pass | Job complete, email sent to Annette Parker re sig slip to sign
MSA-DCS | WA3211378 | Unit 2, B wing - damged metal strip on bottom of door on bathroom outer door needing repair/replace | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-05-06 14:45:00 | Fail | fit new stainless steel pressing to bottom of door
MSA-DCS | WA3211382 | entry control, perimeter security alarm not connecting with the computer | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Apr 2020 | 2020-04-16 17:52:08 | 2020-04-16 15:15:00 | Pass | Attended site and reset network switch and workstation. Found issue between network switch and workstation. Relocated switch port to a spare port. Retested and all configured and tested ok. Job complete
MSA-DCS | WA3211404 | Unit 3 - B & D-The sink tap is loose in cell B11. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-20 16:00:00 | Pass | Replaced tap in basin with tap salvage from previous works
MSA-DCS | WA3211410 | External Visits Building- Duress alarm is not working | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Apr 2020 | 2020-04-16 18:12:53 | 2020-04-17 14:00:00 | Fail | Replaced flat battery and test, ok and back to normal operation. Job completed.
MSA-DCS | WA3211450 | unit 2 B13 light switch faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 14:39:20 | 2020-04-16 15:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA3211477 | Assessments centre- MKH key lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 12:15:00 | Pass | replaced faulty cylinder
MSA-DCS | WA3211507 | Zone 5 perimeter fence is constantly activating | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 15:26:54 | 2020-04-17 08:30:00 | Pass | Attended site and reset intelliflex controller. Tested resistor value and tested slightly low. Replaced with new resistor and retested . All replaced and tested ok. Job complete
MSA-DCS | WA3211555 | Unit 1, Cells B28 & B29- toilets are blocked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 16:06:06 | 2020-04-17 10:05:00 | Pass | COMPLETED
MSA-DCS | WA3211637 | Wooroloo Prison Farm - Fence line cameras are not turning to focus when alarm activated. | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Apr 2020 | 2020-04-16 21:27:27 | 2020-04-16 21:30:00 | Fail | Attended site and investigated the fault.Checked IndigoVision system.Restarted servers and conducted test.All ok at departure
MSA-DCS | WA3211642 | Wooroloo Prison Farm - Zone 1 not responding to any activity on the perimeter fence. | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Apr 2020 | 2020-04-16 21:37:19 | 2020-04-16 20:45:00 | Pass | Attended site.Checked microphonics cable for any damage and replaced missing cable ties.Checked EOL resistor.Reseted power on Senstar module and conducted test.All ok at departure
MSA-DFES | WA3210709 | Room 14 ants are coming in around the light fitting | CFRS Joondalup | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 14:50:00 | Pass | Carried out a service for ants at Joondalup fire station. Inspected the roof void for ant activity, none could be located at time of service. Thoroughly dusted the roof void and wall cavitys on the north and east sides of the building. It's highly recommended that all cracks in wet areas are sealed to deny ants access.
MSA-DFES | WA3211043 | southern dormitory, Room 17 - aircon tripping out | CFRS Fremantle | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-06-02 15:30:00 | Fail | SEE WORK NOTES
MSA-DTAG | WA3210865 | ground public male toilet hand dryer not working | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 08:00:00 | Pass | Job complete
MSA-DTAG | WA3210908 | Basement ladies toilet light not working | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 10:00:00 | Pass | Job complete
MSA-DTAG | WA3211171 | Custody, cells - Cellguard System intermittently restarting and activation cell call buttons | Mandurah Courthouse | GMP-BR-HO | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-17 15:30:00 | Pass | 17/04/20 - Dylan ParslowFound call info held in controllerPower cycled cell guard equipmentTestedCell guard equipment operating correctly.
MSA-DTAG | WA3211196 | up stairs custody Ceiling Light not working | Mandurah Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-17 13:00:00 | Pass | Replaced 2x T5 Fluro, tested ,all in working order
MSA-DTAG | WA3211417 | Lvl 4,Nth end just inside Community Corrections office near the kitchen- Falshing Exit Sign | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 12:00:00 | Pass | Job complete
MSA-DTAG | WA3211458 | Lvl 3, Back of court 38- Blocked toilet | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-17 11:45:00 | Pass | Complete
MSA-DTAG | WA3211533 | Level 8, Water Fountain needs repair | Central Law Courts | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-05-04 12:59:00 | Fail | Replaced Bubbler on fountain A402021525 and installed new GAC Filter to System A401904980 . All working ok.
MSA-DTWD | WA3210591 | L1 arming panel Battery System Low fault on North Block Arming Panel | Mount Lawley Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 16 Apr 2020 | 2020-04-16 17:00:00 | 2020-04-16 14:40:00 | Pass | (16/04/2020) - Work NoteReplaced main panel battery in system C
MSA-DTWD | WA3210612 | B block L3 male toilet Urinal drain blocked , also floor drain | East Perth Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-16 10:25:00 | Pass | COMPLETED
MSA-DTWD | WA3210715 | E block ground LSK tap in the pot was has come loose | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-16 14:30:00 | Pass | COMPLETED
MSA-DTWD | WA3210855 | Graffiti various locations | Rockingham Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 11:00:00 | Pass | REMOVAL OF GRAFFITI FROM VARIOUS LOCATIONS AT ABOVE BUILDING
MSA-DTWD | WA3211189 | level 1, A 120c Cafe store room - Two door SKOPE freezer is not working, | Leederville Campus | GMP-BR | Refrigeration | Freezers (RE) | Precise Air Group | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-05-01 16:00:00 | Fail | Picked up required parts,attended site,isolated system,isolated fire alarm and reclaimed old refridgerant.removed faulty compressor and associated electrical. Installed new compressor solded in new pipe work.pressure tested system and leak tested.evacuated system and gased accordingly.tested system and monitored. Left system all operationalNote::: due to problems with accessing promap could not restart times for job untill 3:19pm. Correct start and finish time is 8:00am to 4:00pm
MSA-DTWD | WA3211278 | D Block, Room DG03- Can’t open padlocks in motorbike shop. | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 11:30:00 | Pass | D Block - Room DG03 - cannot open padlocks
MSA-DTWD | WA3211337 | A block, AG10 - Evap AC water dumping issues and not turning on some times | Carlisle Campus | GMP-BR | Air Conditioning | Evaporative Coolers (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-28 16:30:00 | Fail | Carried out repairs on the Evaps not dumping water located on C block Automotive area.
MSA-DTWD | WA3211338 | A block, AG10B - Noisy Evap AC and issues with water leaking from AC | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 15:00:00 | Pass | Carried out repairs to evaps 13,6,9 and Cafeteria units x 2
MSA-DTWD | WA3211343 | C block, CG03 - AC not blowing air properly | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-28 15:30:00 | Fail | Travelled to supplier to pick up parts. Travelled to site signed in. Removed and disposedo dirty disposable filters and installed new filters on room Cg01, Cg02, Cg03, Cg05, Cg06 and Dg01.
MSA-DTWD | WA3211352 | E block, EG22 - Noisy fan on Split System AC and not blowing air properly | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 09:30:00 | Pass | Travelled to site signed in. Disassembled two high wall spilts and chemically cleaned the indoor coil. TBC. Travelledto site signed in. Replaced indoor fan motor on Daikin split system located in E block Reception.
MSA-DTWD | WA3211381 | west side of G block Square paving near service road lifting, causing trip hazard | Mandurah Campus (formerly Peel) | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 16 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 14:30:00 | Pass | Works completed - Removed and replaced pavers and all level now
MSA-DTWD | WA3211446 | East block L2 Auto Door East Block Level 2 is faulty | Mount Lawley Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 16 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-17 12:29:00 | Pass | On inspection, found cables damaged/broken due to unknown reasons.Replaced and repaired all cables.Tested and adjusted with security guard.All ok.
MSA-DTWD | WA3509176 | Retrospective work order-Level 1, room 120 - Repair proxi reader in Fire door | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 17:00:00 | 2020-05-14 13:11:00 | Fail | job completed - Replaced readers and door lock also replaced door transfer loop as the new lock cable would notfor in the old transfer loop.Checked and tested door function and confirmed door transactions
MSA-MRWA | WA3210722 | ground front gate The manual override has been damaged -see notes | Office and Warehouse-Malaga | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 13:10:00 | Pass | Inspected gate and found clutch release broken and gearbox broken with no drive. Requires new unit. Pics attached. Braf raised
MSA-MRWA | WA3210742 | ground near pedestrian gate-Hazard Clean near Pedestrian Gate. | Traffic Operations Centre | GMP-BR | Cleaning | Hazardous Materials (CL) | Codee Cleaning Services | 1 | CLOSE | 16 Apr 2020 | 2020-04-17 17:00:00 | 2020-04-16 17:00:00 | Pass | Complete
MSA-DCS | WA3226422 | Network Fault PA system control | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-19 15:14:00 | Pass | Intermittent power dropping off during the wet season,All nodes onlines, broadcast all nodes to reset and cleared alarms
MSA-DCS | WA3226425 | Perimeter Beams near zone 16,17 not activating | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-19 16:13:00 | Pass | Tested all internal PE beams,No fault found
MSA-DCS | WA3226430 | EC-7 constantly activating | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-19 15:43:00 | Pass | Realigned microwaves ans inspected PE beams and EFAll working and sealed
MSA-DCS | WA3226434 | Houses aren’t automatically disarming. Have to manually unlock. | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-19 16:15:00 | Pass | Checked Gallagher calender and cross referenced prison unlock schedule and and confirmed all ok
MSA-DCS | WA3226462 | Control room - EBI is not recording | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Apr 2020 | 2020-04-18 07:25:13 | 2020-04-17 13:51:00 | Pass | Sourced parts, attended site, traced fault to data network switch, installed replacement, cabled, configured and tested ok.Parts (Seme stock):Network SwitchConsumables
MSA-DCS | WA3226468 | Unit 5 House 7 front entry door not unlocking electronically | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Apr 2020 | 2020-04-17 11:29:09 | 2020-04-17 11:00:00 | Pass | Checked and found Unit 5 House 7 front entry door not unlocking. Further check located the problem to be the Cardax controller itself. Rectified the fault and tested all ok.
MSA-DCS | WA3226505 | Control - internal H2 no CCTV alarm activation | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Apr 2020 | 2020-04-18 08:01:36 | 2020-04-23 12:23:00 | Fail | Checked HLI and noted IndigoVision alarm detector not being triggered by alarm from Gallagher. It was discovered a virtual output that triggers the HLI was stuck in the ON state. Alarms refreshed on all controllers onsite and a hidden alarm was discovered relating to H2. This alarm was cleared and zone retested and confirmed as functional.
MSA-DCS | WA3226541 | Gatehouse - Camera's PTZ 33, 34, 35 & 47 not operating correctly | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Apr 2020 | 2020-04-18 08:23:50 | 2020-07-09 08:30:00 | Fail | Asked to check cameras 33, 34 and 35 in visits after power outage. Reset RCD to restore picture but there is no PTZ function. Unable to manually shift camera direction without damaging the cameras. Parts ordered for upgraded Indigo CCTV system capability.
MSA-DCS | WA3226546 | Unit 14 - Control Room Cell Call Error | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-20 15:30:00 | Pass | Cell call system errors as a direct result of work being done for new units by another contractor on-site.
MSA-DCS | WA3226549 | Unit 13, A wing, cell 9 - Basin spout leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-17 12:00:00 | Pass | Remove and replace 1/4 turn spindle in plumbing duct
MSA-DCS | WA3226571 | Admin East door lock not securing | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 17 Apr 2020 | 2020-04-17 12:44:05 | 2020-04-17 11:30:00 | Pass | repairs to rear door
MSA-DCS | WA3226591 | Unit 5, House 7 - all down lights in the day room not working, (closed units) | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-30 10:00:00 | Fail | Replaced high downlights and oyster light
MSA-DCS | WA3226612 | Unit 7, Room 1 - wall mounted heater is not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-30 11:00:00 | Fail | Replaced wall heater
MSA-DCS | WA3226615 | Unit 2, cell 17 - hot tap leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-05-21 10:50:00 | Fail | COMPLETED
MSA-DCS | WA3226617 | Unit 2, C11 - hot tap leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-23 08:30:00 | Pass | COMPLETED
MSA-DCS | WA3226636 | Unit 4, entrie B wing - all toilets blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 17 Apr 2020 | 2020-04-18 09:23:25 | 2020-04-17 15:08:00 | Pass | Cleared numerous blockages in cells throw A & B wing using drain machine and plunger
MSA-DCS | WA3226639 | unit 5, house 8 - down lights in day room not workinf | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-30 13:00:00 | Fail | Replaced 7x downlights
MSA-DCS | WA3226642 | Unit 4, A2 - cell light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 13:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3226647 | Unit 3, B6 - cell light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 12:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3226668 | Main building - rear of A wing (external)- Repair Rheem hot water system not auto starting. | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 12:30:00 | Pass | COMPLETED
MSA-DCS | WA3226742 | DDU Kennel Complex - issue with a build-up of leaf and tree debris in section of gutter | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | AFD Contracting | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 12:20:00 | Pass | 17/04/20clean gutter of leaf and tree debris
MSA-DCS | WA3226759 | Master control room, front gate - camera is constantly spinning | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Apr 2020 | 2020-04-17 15:07:49 | 2020-04-17 14:30:00 | Pass | Attended site and reset camera from EC cabinet and tested voltage levels. All tested and reset ok. Camera functions all working ok. Job complete
MSA-DCS | WA3226764 | Master control room, front gate - duress alarm sound is quite and can hardly be heard | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Apr 2020 | 2020-04-17 15:11:53 | 2020-04-17 12:30:00 | Pass | Duress issue related to Honeywell installation works. Unable to rectify fault
MSA-DCS | WA3226769 | Unit 1, Cell B13 - GPO Faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 14:00:00 | Pass | Replaced faulty gpo
MSA-DCS | WA3226772 | Unit 1, Cell B10 - GPO Faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 15:00:00 | Pass | Replaced faulty gpo
MSA-DCS | WA3226773 | External perimeter fence, 2 zones 83 & D4 not activating | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Apr 2020 | 2020-04-17 15:19:11 | 2020-04-17 15:30:00 | Fail | Attended site and reset EC cabinets 2 and 9. Tested electric fence controllers and all online and working ok. Not reporting back to control room. Reset software in gatehouse and retested zones. All tested ok. All alarms activating on both Gallagher and senstar system . Job complete
MSA-DCS | WA3226776 | Unit 4, A Wing- Urn Leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-29 10:15:00 | Fail | Went and inspected urn issue is maintance and they have sent unit for repairs need us to install it once it returns to prison works on hold until it’s back
MSA-DCS | WA3226780 | Unit 8, Cell A6- Toilet constantly runs | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 12:48:00 | Pass | Replaced outlet washer
MSA-DCS | WA3226782 | The Aluminium channells top and bottom of the first piece of glass need replacing/repairs | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 17 Apr 2020 | 2020-04-18 11:26:02 | 2020-04-17 16:45:00 | Pass | REPAIR, RE GLAZE, RE SET FRAMEWORK
MSA-DCS | WA3226787 | SHu (9), court yard - Concrete path down SHU alley the concrete is broken and lifted | Casuarina Prison | GMP-BR- HO | Paving & Roadworks | Paving (PR) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-05-12 14:00:00 | Fail | PATH GROUND DOWN
MSA-DCS | WA3226790 | Unit 8, Cell D8- Hand basin is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 13:55:00 | Pass | Drain machine used to unblock basin
MSA-DCS | WA3226793 | Unit 14, A2 - sink needs attention the spout can be rotated 360 degrees, the water has been turned o | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Apr 2020 | 2020-04-18 11:34:40 | 2020-04-17 14:09:00 | Pass | Tighten up Basin spout from within plumbing duct
MSA-DCS | WA3226795 | SOP, A Wing- Fluro light flickering near prisoners tea room | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-21 11:30:00 | Pass | Repaired faulty lights in SOP corridors
MSA-DCS | WA3226799 | Unit 14, A2 - The toilet seat is loose needs tightening | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 15:00:00 | Pass | Remove toilet seat and install new fixing kit supplied by the prison.
MSA-DCS | WA3226806 | Unit 4, C wing, shower block - Shower tap in cubicle nearest the window does not turn on | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-20 11:00:00 | Pass | Replace missing split pin in plumbing duct
MSA-DCS | WA3226814 | external stores - Air Bridge needs a service as its not opening all the way up | Casuarina Prison | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-21 13:30:00 | Pass | External stores Air bridge faulty. Check bridge & controls. Open hydro pump. Refill oil tank. Bleed air from lines. Clean & lubricate small ramp. Assemble & test.
MSA-DCS | WA3226817 | Keywatcher door will not open. Lock makes a noise but remains engaged | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-05-22 15:36:00 | Fail | installed lock & tongue on keywatcher, tested ok. job complete
MSA-DCS | WA3226876 | Kitchen - A side pot washer not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 17 Apr 2020 | 2020-04-18 12:37:08 | 2020-04-18 12:15:00 | Pass | Kitchen A side pot washer faulty. Check washer & controls. Dismantle, check wiring & inlet solenoid. Pick up new solenoid, remove faulty solenoid, install new part. Replace inlet hose. Clean out strainer. Assemble.
MSA-DCS | WA3226879 | Bakery- Freezer leaking water onto floor, possible damaged drop tray | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-20 15:47:00 | Pass | Blockage clear, drain ok.
MSA-DCS | WA3226884 | SITE COST Unit 3, B & D Oven vent is dripping water/blocked, exhaust system/filter | Casuarina Prison | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-05-05 13:50:00 | Fail | Cleaned oven vent
MSA-DCS | WA3226897 | S O P, A Wing- Water leaking in service duct between cells HA13 & HA14. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-30 13:00:00 | Fail | Replace pan collar and IO in plumbing duct behind toilet.
MSA-DCS | WA3226900 | S O P, A Wing- water leaking in service ducts between cells HA9 & HA 10 and HA3 & HA4 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-05-01 09:00:00 | Fail | Replace leaking pan collar and IO 90.
MSA-DCS | WA3226925 | towers 04 / 13 / 32 - lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-23 12:30:00 | Pass | Investigate and repair perimeter lights
MSA-DCS | WA3226926 | ABBS / Addmin facing the gate - lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-23 15:00:00 | Pass | Investigate and repair pole lights near abattoir and admin using cherry picker
MSA-DCS | WA3226945 | Gardens, Lettuce shed - electrical fault in shed | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-23 09:00:00 | Pass | Investigate electrical fault in lettuce shed. Found blown fuses on transformer. Replaced fuses.
MSA-DCS | WA3226983 | Unit 5, Cell D6- Cistern is constantly leaking into pan | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-30 15:00:00 | Fail | Remove and replace 1x outlet rubber in cistern in plumbing duct
MSA-DCS | WA3227066 | Visits- relocate security data points | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-21 15:11:00 | Pass | Security data points relocated, old points blankplated and new points tested fully operational. Cabling surface mounted.
MSA-DFES | WA3226445 | Administration building SODP Change Room/BA Training Services increase fresh air | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 17 Apr 2020 | 2020-04-17 17:00:00 | 2020-08-06 12:50:00 | Fail | BRAF declined 06/08.
MSA-DFES | WA3226762 | Drainage issue - Possible void under ashpalt, see further notes below | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 17 Apr 2020 | 2020-04-20 17:00:00 | 2020-07-15 09:42:00 | Fail | advised by steve cassie to close off work order as project works been undertaken on storm water issue and works not required.
MSA-DFES | WA3226902 | Administration building staff dining room - external door swipe card reader is not working - pacom | FESA RHQ - Forrestfield | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 17 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 12:00:00 | Pass | 20/4/2020 - Dean SimpsonDoor reader not responding correctlyIdentified fault with door controller, power cycled door controllerFound reader icon removed from GMS map, re-added to map.
MSA-DFES | WA3226965 | Sewer pit pump has failed & has an alarm which is activating | CFRS Duncraig | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 17 Apr 2020 | 2020-04-20 17:00:00 | 2020-07-22 10:51:00 | Fail | up grade of sewer pump pit at Duncraig DFES complete
MSA-DTAG | WA3226830 | 2x disabled toilets (blocked) 1x ground level & 1x 4 level | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 13:00:00 | Pass | Complete
MSA-DTAG | WA3226858 | multiple lights not working out - x6 level 5, court 56 & level 9 lift lobby | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 17 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 11:00:00 | Pass | Job complete
MSA-DTAG | WA3227072 | ground level - Step leading to courtroom 3 door has come loose and is caving downwards | Armadale Courthouse | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-05-04 15:15:00 | Fail | REPAIRS TO STEP/THRESHOLD COMPLETED
MSA-DTAG | WA3227088 | Ground level, public toilets - taps are leaking/dripping | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-21 09:00:00 | Pass | Complete
MSA-DTWD | WA3226510 | A block, level 1, West end path - repair damaged pavers | East Perth Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-05-08 14:30:00 | Fail | Relaying pavers after cutting out tree roots and topping up sand.
MSA-DTWD | WA3226650 | B Block New staff carpark retic piep in the garden bed is broken | Murdoch Campus | GMP-BR | Landscaping & Gardening | Materials (LG) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-22 08:30:00 | Pass | Locate and repair broken pipe
MSA-DTWD | WA3226680 | A Block, G Floor, West room A006- Aircon drain blocked | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-17 15:55:00 | Pass | Attended site, found smell to be coming from a006 still, we have quoted filters but problem persists even with filters removed, removed covers from unit, found unit to be in good condition inside with nothing to create a smell, removed supply grilles to look into ducting , found that there is debris in duct that must have been caused by rodents or other vermin Poured 6l of water down drain and is operating fine and can see draining outside so nothing to do with a blocked drain , also no water on ceiling or any other evidence pointing towards a drain being blocked originally
MSA-DTWD | WA3226701 | E block, Skills kitchen - blown range hood lights | Joondalup Kendrew Campus | GMP-BR | Electrical | Materials (EL) | Techworks Electrical | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 14:05:00 | Pass | Fix various hood lights and components. While changing the ballast of one of the lights, other components started to crumble due the heat, as requested, sourced a LED batten to replace the whole fitting. Dave also asked us to fix a light switch and various other lights within E-block.
MSA-DTWD | WA3226746 | level 2, W204 - Skirting board loose: Entrance to call centre/student services | Perth Campus B1 | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 17 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-28 14:00:00 | Fail | Works are now completed and the skirting is now re-affixed
MSA-DTWD | WA3226842 | E block, corridor outside kitchen E30 - Loud buzzing noise from contactor in Electrical Distribution | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 17 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-17 16:37:00 | Pass | Attended site and signed in. Located e30 and found box next to switchboard to control the emergency stop system. Tested to find 2 x contactors out of 5 to be excessively buzzing. Replaced with new. Tested all okay. Job complete
MSA-DTWD | WA3226854 | Pressure pump that does the rain water tanks for the toilets stopped working | Munster Campus (ACEPT) | GMP-BR | Mechanical Services | Pumps (MS) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Apr 2020 | 2020-04-22 17:00:00 | 2020-05-15 11:00:00 | Fail | Replace pump
MSA-DCS | WA3232421 | Albany Regional Prison- camera not working exrternal as well as internal | Albany Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Apr 2020 | 2020-04-18 15:33:37 | 2020-04-20 12:00:00 | Fail | Job complete
MSA-DCS | WA3232447 | Unit 2- D landing- PDA triangular is in alarm. Security. | Albany Regional Prison-Prisoner Accommodation Unit 2 | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Apr 2020 | 2020-04-18 18:45:45 | 2020-04-20 13:30:00 | Fail | replaced unit 2 receiver & enclosure, tested ok. job complete
MSA-DCS | WA3232550 | Equipment room system alarm- Power Fail F21 | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Security Equipment (EQ) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Apr 2020 | 2020-04-19 18:01:41 | 2020-04-18 20:45:00 | Pass | Attended site and investigated the fault.Checked power supply on Senstar system.Checked system for any active alarms.Conducted test on all sensors.All ok at departure
MSA-DFES | WA3268043 | Restrospective work order - BYPASS ON ARMING ZN 18 APP BAY 1 FRONT ROLLER DOOR | VFRS Mandurah | GMP-BR | Security | Guards (SE) | Securex Security Systems & Services | 0 | CLOSE | 18 Apr 2020 | 2020-04-19 03:45:00 | 2020-04-19 00:24:00 | Pass | EXTERNAL CHECK CARRIED OUT. NO OFFENCE DETECTED. ALL APPEARS SECURE. CANSEE STAFF ONSITE IN THE BACK GROUND ASLEEP, WEARING UNIFORMS. OFFICERDEPARTED SITE
MSA-DCA | WA3234288 | Fault on fire phone connected fire hydrant booster. | State Library of WA-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 19 Apr 2020 | 2020-04-19 07:51:10 | 2020-04-19 06:30:00 | Pass | Call out for WIP Fault/alarmMain sprinkler pump feed has sprung a leakwetting WIPDisconnected WIP and investigated leakleak requires further works WIP Disconnected requires replacing and resistor on repair of leaking pipeworkQuote/BRAF to be submitted
MSA-DCS | WA3234287 | Personal Duress Alarm Panel is not working. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Apr 2020 | 2020-04-19 07:35:32 | 2020-04-19 05:30:00 | Pass | Attended site.On arrival found that problem with MDAS monitor has been rectified.Adjusted volume on speakers.Conducted test.All ok at departure
MSA-DCS | WA3234298 | Bunbury Regional Prison- Sally port gate not opearting | Bunbury Regional Prison | GMP-BR- HO | Building | Materials (BU) | AFD Contracting | 0 | CLOSE | 19 Apr 2020 | 2020-04-19 16:52:34 | 2020-04-19 09:30:00 | Pass | Sunday 19/04/20Re-calibrate limits effecting inter-locks
MSA-DCS | WA3234321 | Door from secure room into lobby is not closing properly | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 Apr 2020 | 2020-04-20 11:03:45 | 2020-04-20 09:30:00 | Pass | No completion notes
MSA-DCS | WA3234330 | Karakin unit cell call system going into tamper | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Apr 2020 | 2020-04-19 16:25:51 | 2020-04-19 16:00:00 | Pass | Karakin cells 3 & 6 showing tamper. checked master station & all is ok upon arrival. checked cell call units & all fixed on wall fine. power cycled node unit 8. tested ok. all is working. job complete.job recalled, attended site & replaced cell call point with spare site stock. job complete
MSA-DCS | WA3234337 | Unit 4-B WING-Cells 6,7 and 8 blocked toilets. | Hakea Prison-Unit 4 | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 19 Apr 2020 | 2020-04-19 19:48:34 | 2020-04-19 19:07:00 | Pass | Unblocked and Cleared out shirts jocks plastic bottles rags etc sent down 32meters off drain rod then flushed all cells on bwing to confirm blockage was cleared
MSA-DCA | WA3235170 | Male public toilets - right sink, sensor tap running contintouisly | Sunset Hospital Heritage Precinct | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 20 Apr 2020 | 2020-04-20 13:46:49 | 2020-04-20 13:40:00 | Pass | On my arrivale the sensor tap was running and sink was full of water. Replaced sensor tap with push button pillar tap.
MSA-DCA | WA3235546 | Boiler room - water leaking in plant room | Shipwreck Galleries-Main Building-Ground Floor-Plant Room - In Front of Lift | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 17:00:00 | 2020-06-05 16:30:00 | Fail | Please refer to Enviro plumb and Boilertronics service reports for in-depth long description of defects with in Boiler. Job to be closed out with a quotation to be submitted to replace Boiler.
MSA-DCS | WA3234822 | Unit 10, Cell C16- Broken cell main window | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 06:54:41 | 2020-05-11 14:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3234824 | Front Entrance - Sally port internal doors are faulty | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 20 Apr 2020 | 2020-04-20 10:46:40 | 2020-04-20 10:40:00 | Pass | Monday 20/04/20inspect inner east sally port doors for fault.Adjust door open limit.Lubricate hinges.(hired scissor lift)
MSA-DCS | WA3234826 | Unit 9, Cell D9- Sink not draining properly | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 10:40:00 | Pass | Cleaned out blockage in trap
MSA-DCS | WA3234828 | Unit 9, C & D Wing cleaning cupboard- Sink not draining properly | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 09:35:00 | Pass | Removed blockage from trap
MSA-DCS | WA3234829 | Unit 10, C & D Wing Day Room - Sink tap spins around and hard to grab | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-23 16:05:00 | Pass | Replaced quarter turn tap cold only
MSA-DCS | WA3234831 | Unit 10, Cell C16 - Basin tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 07:01:49 | 2020-04-20 18:35:00 | Pass | Renew basin set to c16
MSA-DCS | WA3234834 | Unit 5 House 6 all call speaker is not working | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 07:03:48 | 2020-04-20 15:22:00 | Pass | Unit 5 house 6 PA system repaired, found interface failing repaired and tested operational.
MSA-DCS | WA3234837 | Kitchen - Tap next to Dayroom broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-22 16:15:00 | Pass | Went to repair. tap needs replacing order new one
MSA-DCS | WA3234839 | Unit 2, Cell A3 - Water leaking from under sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 14:59:00 | Pass | Replaced outlet washer
MSA-DCS | WA3234845 | Gym- Bracket hanging from ceiling. Hanging dangerously | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-22 14:00:00 | Pass | We found the cage around a light is hanging - electrician required
MSA-DCS | WA3234848 | Unit 3, Cell B12- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 15:00:00 | Pass | Repaired light
MSA-DCS | WA3234851 | Level 4 glass sliding entry door near large kitchen - Swipe reader ha dislodged and needs repair | Westralia Square | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 07:13:03 | 2020-04-20 10:30:00 | Pass | Remount reader and wall plate, test, all ok
MSA-DCS | WA3234854 | Unit 1 Cell B27 toilet isn’t working, possibly a broken (float) | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-23 09:14:00 | Fail | No faults found
MSA-DCS | WA3234884 | Gascoyne, Cell B5- Blocked toilet & damaged flush | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-22 12:00:00 | Pass | Replaced broken cistern with invisi cistern and ran new water feed
MSA-DCS | WA3234888 | Unit 6- Door to B & D dayroom not working/faulty | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-05-29 08:45:00 | Fail | job to be invoiced at costs to date
MSA-DCS | WA3234892 | Unit 4, Cell D11 - Cell Call not working at all | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-20 11:30:00 | Pass | Cleared out cell call due to being blocked up and causing loss of sound from speaker. All cleared out and tested ok. Job complete
MSA-DCS | WA3234893 | Unit 4, Cell A- Cell call very faint | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-20 12:30:00 | Pass | Cleared out cell call due to being blocked up and causing loss of sound from speaker. All cleared out and tested ok. Job complete
MSA-DCS | WA3234895 | INF(10)- C Wing, Cell C2- TV keeps flickering | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 09:00:00 | Pass | Tested TV, no issues, all channels are clear with strong signal strength.
MSA-DCS | WA3234898 | Unit 1, A & C- Rear window is shattered | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-20 13:30:00 | Pass | UNIT 1, C12 CELL WINDOW REGLAZED
MSA-DCS | WA3234904 | Unit 1, A & C- Padlocked tap in A Wing cleaning store has become unattached & requires repair | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-21 11:00:00 | Pass | Investigate plumbing duct. Valve is padlocked and no issue could be found.
MSA-DCS | WA3234907 | Unit 6, A Wing, Cel A6- Toilet cistern does not shut off (always filling) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-20 13:00:00 | Pass | Replace faulty Inlet valve in plumbing duct
MSA-DCS | WA3234913 | Unit 4, B Wing- Tap in cleaning store has broken off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-20 09:00:00 | Pass | Reattach cleaners trough tap in cleaners closet
MSA-DCS | WA3234924 | Cell A12, blocked sink, draining but very slowly. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-30 16:00:00 | Fail | Plunge basin to clear blockage
MSA-DCS | WA3234926 | Unit 1, B & D- Sink is blocked, reported as overflows | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-20 15:00:00 | Pass | Plunge sink to clear blockage and test.
MSA-DCS | WA3234936 | Unit 7, B Wing, Cell B7- Main light in cell not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 10:30:00 | Pass | Repaired faulty lights in unit 7 B7
MSA-DCS | WA3234939 | Unit 14, A Wing, Cell A14- Intermal cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 13:00:00 | Pass | Repaired faulty lights in unit 14 a14
MSA-DCS | WA3234942 | Unit 5 - C7 CELL EMERGENCY ALARM VERY FAINT WHEN DOING CHECKS./ | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-20 15:00:00 | Pass | Cleared out cell call as was blocked up, all cleared and tested ok. Job complete
MSA-DCS | WA3234945 | Unit 3, C Wing, Cell C9- Cell alarm buttons not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-22 08:30:00 | Pass | Unit 3 C wing cell C9, cell alarm button stuck, released button and secured tested fully operational.
MSA-DCS | WA3234965 | unit 2 upstairs plant room, water leak on the pipe work | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 08:10:38 | 2020-04-20 16:22:00 | Pass | Located water leak in plant room is coming from flange off boiler contacted maintance to call boilertronics
MSA-DCS | WA3234968 | unit 1 control room CCTV TV monitors frozen | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Apr 2020 | 2020-04-20 12:13:41 | 2020-04-20 10:00:00 | Pass | Attended site and reset unit 1 camera system and PC. Reset and reloaded camera layouts. All presets reloaded and tested ok. Job complete
MSA-DCS | WA3234979 | Unit 3, D Wing, Cell D4- Cell alarm button not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 11:00:00 | Pass | Unit 3 D wing cell D4 button stuck, released and secured, tested now fully operational.
MSA-DCS | WA3234996 | Unit 14, A Wing, Cell A10- Internal cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 12:00:00 | Pass | Repaired faulty lights in unit 14 a10
MSA-DCS | WA3235011 | Unit 14, C Wing, Cell C03- Blocked shower drain, draining but very slow | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-20 12:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3235017 | Unit 14, A Wing, Cell A09 sink and shower blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-20 14:00:00 | Pass | Remove grate, remove hair, moflo, rinse, plunge, reinstall grate, plunge sink and test both shower and sink.
MSA-DCS | WA3235028 | Unit 14, D Wing, Cell D01- Reading light (bottom bunk) not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-28 08:30:00 | Pass | Repaired faulty lights in unit 14 d1
MSA-DCS | WA3235044 | Medical centre main treatment room- tap is not turning off at all | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 08:37:54 | 2020-04-20 14:22:00 | Pass | COMPLETED
MSA-DCS | WA3235046 | Unit 12 SOP cell A11 Cell call connecting successfully. Receiving audio correctly. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-20 14:00:00 | Pass | Attended site and reset cell call system due to slight distortion of audio. All reset and tested working ok. Job complete
MSA-DCS | WA3235058 | Unit 3, Cell A8- Cell alarm has activated but alarm system did not activate within the unit | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-22 09:30:00 | Pass | Unit 3 cell A8 cell alarm tested operational, cgecked multiple times activating correctly to both unit control and casuarina main control.
MSA-DCS | WA3235059 | Unit 14 - B Wing Cell B14 Hatch Lock is faulty and very hard to open. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 08:43:36 | 2020-05-21 12:00:00 | Fail | Replaced hatch lock
MSA-DCS | WA3235062 | Unit 5, Cell D6- Taps in handbasin leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-30 13:00:00 | Fail | Tighten up Basin spout connection Under The Basin
MSA-DCS | WA3235063 | Unit 2, D Wing, Cell D8- Toilet will not stop flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-21 12:00:00 | Pass | Remove and replace faulty outlet rubber in cistern in plumbing duct
MSA-DCS | WA3235071 | Unit 14, A Wing, Cell A15- Blocked shower drain, draining but slowly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-20 09:33:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3235074 | Unit 4 - A & C A/C Dayroom storeroom has a hole in the wall behind fridge.-see notes | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-07-21 14:30:00 | Fail | wall sheeting replaced
MSA-DCS | WA3235087 | INF (10) - ceiling light in the control room is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-21 13:00:00 | Pass | Repaired faulty lights in infirmary control room
MSA-DCS | WA3235125 | Gardens, pump shed - retic cooler keeps tripping out - see Paul Reeves | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 09:00:00 | Pass | Investigate and reset gardens pump VSD
MSA-DCS | WA3235133 | Unit 7, D Wing, Cell D7- Cell light and light switch not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 09:30:00 | Pass | Repaired faulty lights in unit 7 D7
MSA-DCS | WA3235218 | Disconnect and remove faulty mag lock to front security screen door | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 15:00:00 | Pass | Disconnected Front Entry Screen Door maglock power. Removed magnet as requested
MSA-DCS | WA3235230 | Unit 3, Cell C7 & C8 - service duct doorlock needs a service as faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 12:45:00 | Pass | Service and replace bolt throw
MSA-DCS | WA3235244 | Unit 3 cell C9 & C10 service duct doorlock needs a service . | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 13:30:00 | Pass | serviced and replace bolt throw
MSA-DCS | WA3235262 | Kitchen, front door - door closer damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-05-20 13:00:00 | Fail | new door closer fitted
MSA-DCS | WA3235287 | Unit 3, D Wing Day Room- Water leaking through ceiling | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-05-15 10:04:00 | Fail | located leak and rectified
MSA-DCS | WA3235309 | Gatehouse, Door to key Control - Door not opening & closing correctly | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 10:34:05 | 2020-04-20 13:03:00 | Pass | Investigated intermittent fault, checked wiring, checked lock, monitored for correct operation but found fault reoccured, traced cable and repaired.Tested OKJob CompleteParts Used:Consumables
MSA-DCS | WA3235316 | SHU (9) Dirty camera also covered in cob webbs/spiders, camera, 287 & 291 west wing | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-21 10:00:00 | Pass | Arranged escort officer to accompany long ladder to south West side of SHU. Note: Ladder is the only access to this camera due to very soft sand around this side of building.
MSA-DCS | WA3235358 | Unit 14 Alliminuim channell needs repairing on window in A2/Cell cannot be used | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 11:02:04 | 2020-04-20 18:00:00 | Pass | dismantled window and frame, refitted, reset and secured glass panel.
MSA-DCS | WA3235471 | Unit 6 A22 Toilet continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 15:25:00 | Pass | Replaced cistern
MSA-DCS | WA3235483 | Unit 6, A6 - toilet not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 14:22:00 | Pass | Replaced inlet valve
MSA-DCS | WA3235486 | Unit 6, A5 - Toilet continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 13:48:00 | Pass | Replaced cistern
MSA-DCS | WA3235494 | Unit 6, A13 - Toilet continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 00:47:00 | Pass | Replaced outlet washer
MSA-DCS | WA3235497 | unit 6 A14 toilet continues to run | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 12:12:00 | Pass | Replaced outlet washer
MSA-DCS | WA3235501 | Unit 6, N11 - Toilet not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 11:08:00 | Pass | Replaced cistern
MSA-DCS | WA3235506 | Unit 6, D2 & D5 - Leaking taps | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 10:05:00 | Pass | Replaced tap valve and washer
MSA-DCS | WA3235509 | Unit 6 D9 toilet leaking from base | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 15:50:00 | Pass | Replaced outlet washer
MSA-DCS | WA3235511 | Unit 6, C wing shower - Middle shower in c wing continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 09:30:00 | Pass | Replaced tap valve and washer
MSA-DCS | WA3235516 | Kitchen - Workshop Emergency Power switch located on the wall | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-22 15:00:00 | Pass | Isolated damaged estop button. Picked up replacement parts and installed/tested
MSA-DCS | WA3235528 | unit 1 cell B18 lock not working | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 20 Apr 2020 | 2020-04-20 16:29:10 | 2020-04-20 14:00:00 | Pass | main Cell Lock on B18 Unit 1 - out of alighnment adjusted alighnment and checked cell lock
MSA-DCS | WA3235533 | Unit 6, A2 - Toilet continuously running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 16:45:00 | Pass | Replaced outlet washer
MSA-DCS | WA3235583 | Community Rooms 1; 2 & 3 - Exterior building lights not turning on with timer | Boronia Pre-release-AH19 - Administration, Education Senior Officers and Programs | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-24 11:00:00 | Fail | Replaced failed p/e cell and resecured relay in distribution board of community rooms building. Replaced failing security lighting time clock after sourcing replacement.
MSA-DCS | WA3235606 | Unit 2, Back Unit- Hot Water system faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 09:00:00 | Pass | Investigate and repair unit 2 external shower block hot water system
MSA-DCS | WA3235608 | Unit 2 outside huts foucet leaking badly | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-05-04 11:30:00 | Fail | COMPLETED
MSA-DCS | WA3235623 | Unit 3, B Wing- Tap broken on hot water urn | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 10:02:00 | Pass | DIAGNOSED AND REPLACE TAP ASSEMBLY ON RHEEM BWU A40166241C
MSA-DCS | WA3235626 | unit 4 day room south urn faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 15:00:00 | Pass | COMPLETED
MSA-DCS | WA3235631 | Unit 3, C Wing- Faucet in sink is faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 15:00:00 | Pass | COMPLETED
MSA-DCS | WA3235707 | Cleaning - Workshop OFFICE AREA LEAKING THROUGH AIR-CON VENT. | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 13:24:00 | Pass | Arrived on site and signed in tools, checked for water leak,no water present in outdoor drip tray on mezzanine level, resealed drip tray and checked to see if any damage to roof from inside,could not see any damage.
MSA-DCS | WA3235718 | Administration/Security, Monitor Room - Proximity card #7 not working | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Toilet - Security Room | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 09:55:00 | Pass | Card tested and working all ok
MSA-DCS | WA3235723 | Unit 10, A4 - Leaking sink tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-29 11:15:00 | Fail | Repair leak to basin set Take out bridging piece and renew o rings
MSA-DCS | WA3235725 | Admin, Female toilet is leaking onto the floor | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-24 09:30:00 | Fail | Replaced worn out washer between cistern and toilet bowl
MSA-DCS | WA3235727 | Unit 8, A6 - Toilet cistern constantly running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-29 09:05:00 | Fail | Installed new top push button for cistern
MSA-DCS | WA3235729 | Murchison, B Wing- Kitchen Tap leaking | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-29 13:16:00 | Fail | Unable to fix leaking tap as i was not allowed to dig up the pavers to find the isolation valve which is located underground outside the unit.
MSA-DCS | WA3235730 | Unit 7, H3 - Toilet does not flush at all | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-05-05 11:30:00 | Fail | Removed old cistern replaced with new
MSA-DCS | WA3235756 | unit 7 E9 Toilet does not flush at all | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 15:48:00 | Pass | Replaced cistern
MSA-DCS | WA3235757 | Unit 1, Cell C2 - sink leaking and flooding cell | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 15:04:57 | 2020-04-20 17:30:00 | Pass | Sink leaking from silcone removed stainless cover located leak cleaned off old silcone reinstalled stainless cover and re siliconed
MSA-DCS | WA3235759 | kitchen Rational oven not following cycle | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 16:20:00 | Pass | 21/04/20 - Called as requested to the oven not working correctly, intermittently jumping programs. Found no fault when tested, left on test for 1 hour and still no fault. Checked over the oven to find the bottom fan motor vibrating and I/O board in poor condition. Will leave this job open for a few day to see if the fault occurs again.
MSA-DCS | WA3235763 | Unit 1, B wing - Most toilets blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 15:08:45 | 2020-04-21 12:15:00 | Pass | Unblcoked sewer line-t-shirt had been flushed down the toilet
MSA-DCS | WA3235765 | Unit 1, C7 - Toilet service panel needs replacing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 15:12:11 | 2020-04-21 13:22:00 | Pass | Repaired side panel on toilet pan
MSA-DCS | WA3235769 | Unit 7 G1 toilet button is stuck | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 14:46:00 | Pass | Installed new flush button
MSA-DCS | WA3235770 | Unit 2, Cells C3, B14 and A2 - Cell calls faulty | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 15:14:36 | 2020-04-24 15:30:00 | Fail | Removed, stripped and cleaned intercoms. Assembled and secured. Tested ok. Parts used:Consumables
MSA-DCS | WA3235774 | Unit 2, A10 - light awitch faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 14:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3235775 | entry control duress alarm screen going dark | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 15:17:56 | 2020-04-23 13:00:00 | Fail | Replaced duress monitor with new 19inch monitor. All tested and working ok. Job complete
MSA-DCS | WA3235781 | unit 7 G7 Toilet continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 14:17:00 | Pass | Replaced cistern
MSA-DCS | WA3235784 | Unit 7 H24 toilet does not flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 13:16:00 | Pass | Installed new flush button
MSA-DCS | WA3235787 | Unit 7, E17 - Toilet does not flush at all | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 12:43:00 | Pass | Replaced cistern
MSA-DCS | WA3235804 | Unit 10, cell C13 & C14 - damaged vinyl | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-10-28 14:00:00 | Fail | NEW VINYL LAID TO CELL 14 - CELL 13 IS ON JOB #WA3719756
MSA-DCS | WA3235807 | Unit 10 A4 Floor tile missing consequently hole in floor now | Hakea Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-06-26 11:00:00 | Fail | JOB HAS BEEN COMPLETED- TILE REPLACED
MSA-DCS | WA3235820 | Unit 9, D wing - Sliding window needs resecuring end of D wing ( Slider located in staff toilet ) | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-05-01 10:30:00 | Fail | window secured
MSA-DCS | WA3235853 | Gate house - Rear Door Staff Access - Lock not engaging | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 16:37:22 | 2020-04-21 11:00:00 | Pass | No completion notes
MSA-DCS | WA3235856 | Unit 2, B wing - Fluorescent light hanging from ceiling (2nd in Hallway ) | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 13:00:00 | Pass | Remounted light
MSA-DCS | WA3235861 | Unit 4, B13 - Viewing Hatch Window Brocken | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-05-01 15:00:00 | Fail | OBS PANEL REGLAZED
MSA-DCS | WA3235863 | Unit 3, C14 - Toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 18:00:00 | Pass | Replaced pillar tap and outlet washer
MSA-DCS | WA3235864 | SOG base disposal of waste and unwanted equipment | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-10-26 15:30:00 | Fail | Returned old electronic equipment to PFM stores at Hakea and Casuarina prisons.
MSA-DCS | WA3235895 | DCP system in the control room wouldn't restart | West Kimberley Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 19:42:49 | 2020-04-25 11:00:00 | Fail | Collected parts and travel to site, investigated fault and ran diagnostic software to determine if any major faults on PC exist. Checked all hardrives and found that C drive had reached full capacity (200GB of 200GB used) investigated further and found hidden files located in users under Gallagher file. Files labelled mini dump file. Cleared all files and restarted PC. Checked hardrive and all cleared and working ok. Tested Gallagher functions and all tested ok. Job complete, will send off mini dump file to Gallagher support to get further feedback on reason for hardrive to be full.
MSA-DFES | WA3235777 | Manager Fleet Maintenance Office - has bad odour - possible dead rodent | Fleet Management Services - O'Connor Workshop | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-21 12:00:00 | Pass | Carried out a service for rodents at DFES Fleet & Equip Services. There were reports of an odour coming from one of the offices. Upon further inspection no dead rodent could be located. Installed a odour bag in the area where odour was.
MSA-DTAG | WA3234980 | cameras down no visual in our control room | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 20 Apr 2020 | 2020-04-20 12:07:38 | 2020-05-28 15:30:00 | Fail | cameras down no visual in our control room
MSA-DTAG | WA3235000 | intercoms not working . | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-20 11:30:00 | Pass | Rebooted switch, intercoms came online
MSA-DTAG | WA3235157 | 1987 L1 air con to cold | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-20 15:00:00 | Pass | Attend site. Investigate AC 3 serving first floor 1987 building not working. Access plantroom and found unit in fault. Further investigation found there to be a control issue. Trace through wiring and eventually found there was a broken neutral causing the evaporator fan not to start. Found bad conection ontop of evap fan motor contactor. Isolate power supply. Remove wire from contactor and strip back for new connection. Replace wiring in contactor. Test operation and found unit to start and operate as normal.
MSA-DTAG | WA3235268 | Server has lost connection for levels 25, 26 & 27 – Milestone Device Communication Error | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 13:30:00 | Pass | Rebooted switch and swapped fibre port connections, brought cameras online
MSA-DTAG | WA3235321 | L3 kitchen Hay street end – No hot water coming out of the Bilie heater | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-22 14:01:00 | Pass | Unit was only isolated at gpo and was reason for no water. No faults in log toIndicate that it may have been turned off due to faulty. Ran system up, flushed out tanks and was all working ok.
MSA-DTAG | WA3235330 | Ground level, Toilet to Mitchell & Murphy JJ chambers - Water is continually running | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-21 11:49:00 | Pass | Replace 50mm flush pipe cone to judges WC
MSA-DTAG | WA3235453 | Level 13,foyer oppsite last lift - flickering light | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-22 10:15:00 | Pass | Job complete
MSA-DTAG | WA3235462 | L13 female toilet light not working | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-22 13:30:00 | Pass | Job complete
MSA-DTAG | WA3235465 | Level 3, Court 31 - Light closest to custody box and above bar table is not working. | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 12:15:00 | Pass | Job complete
MSA-DTWD | WA3234922 | T Block- Lifts not operating | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 20 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-20 12:30:00 | Pass | Not chargeable
MSA-DTWD | WA3235007 | Block 6, Ground, Metal Fab 2 Compound- Faulty KA 19 lock | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-21 13:45:00 | Pass | Padlocks replaced.
MSA-DTWD | WA3235122 | L6 east block plantroom Boilers not starting | Perth Campus B1 | GMP-BR | Mechanical Services | Boilers (MS) | Equans Mechanical Services Australia | 3 | CLOSE | 20 Apr 2020 | 2020-04-28 17:00:00 | 2020-05-12 11:00:00 | Fail | Met with Schneider Electrical on site. assisted with fault finding on AHU7.AHU 7 NEEDS A NEW SA STATIC PRESSURE SENSOR. SOUTH BLOCK XENTA CONTROLLER NEEDS REPLACING. BMS IS BEING TENDERED FOR UPGRADE. JOB COMPLETE
MSA-DTWD | WA3235140 | Tower Block, Level 3 - Noisy air vent | West One Services | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 20 Apr 2020 | 2020-04-21 17:00:00 | 2020-04-20 13:57:00 | Pass | Attended site, signed in and completed safety questions and jsa , located noisy grille, found noise to be a light metal rattling, founf this was due to age of grille , re strengthened lover in grille with insulation wrap, this will give the lovers support and stop the small movements that are creating the noise
MSA-DTWD | WA3236428 | Retrospective work order donot attend-Canteen smashed window from break in | Rockingham Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 20 Apr 2020 | 2020-04-20 17:00:00 | 2020-04-22 09:26:00 | Fail | ATTENDED SITE AFTER HOURS 20/04 12:30AM REGLAZED BROKEN GLASS PANEL TO CANTEEN 6.38 CLEAR LAMINATED SAFETY GLASS 1 - 1540 X 1170 3.8 LM OF RUBBER REPLACED SILICONE USED
MSA-DTWD | WA3509178 | Retrospecitve work order-A block L1 Access control of Leederville doors not accessible | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 2 | CLOSE | 20 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-21 12:45:00 | Pass | Job completed - Investigated fault and found that the Inet Xenta was off line.Restarted Xenta and LIU controllers. Noticed that Inet AMT window was full of opened transaction pages. Cleared these pages as thiscan overload the Workstation.Updated all save files from all TAFE controllers to keep an updated folder
MSA-DCA | WA3236610 | Leaking sink mixer spout in Admin building kitchen | Collection and Research Centre Welshpool-Administration and Library Building-Ground Floor-Kitchenette | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 16:00:00 | Pass | On arrival found leaking tap to be working fine, the leaking was normal as the mixer tap is connected to a billi boiler unit which vents through the tap itself.
MSA-DCA | WA3236614 | Leaking sink mixer spout in CRC warehouse kitchen-see notes | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 16:35:00 | Pass | Replace KS outlet to kitchen
MSA-DCS | WA3236084 | Offical Visits, Holding Cell- Crack in window | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 21 Apr 2020 | 2020-04-23 17:00:00 | 2020-05-01 13:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3236091 | Unit 2, D Wing, Cell D2 MK Barrel, keys unable to turn in lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 21 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 11:30:00 | Pass | replace hinges, door plate, lock and adjusted strike.
MSA-DCS | WA3236095 | Unit 6, C Wing, Cell C6- Broken sink tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-21 14:00:00 | Pass | Replace worn thermal spacer on tap and reattached Tap
MSA-DCS | WA3236097 | Unit 7, Cell A10- Door hinges faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 21 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-21 11:00:00 | Pass | Replaced hinges
MSA-DCS | WA3236115 | control room monitors in unit 13 are not displaying video feed | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 07:56:56 | 2020-04-21 11:00:00 | Pass | Travel to site, found indigovision software password had expired. Reset with new password and reloaded indigovision software and camera presets. All reset and tested ok. Job complete
MSA-DCS | WA3236153 | Unit 7, C Wing, Cell C10- Toilet is constantly leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-21 13:00:00 | Pass | Remove and replace faulty Inlet valve in plumbing duct
MSA-DCS | WA3236165 | Unit 5, Intercom is not working | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 15:37:00 | Pass | Contacted site spoke with SO Fixter, system has functioned correctly since without fault, no further action is required.
MSA-DCS | WA3236239 | Level 4, Behind desk W4.21- flickering light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 15:30:00 | Pass | Replaced lamps and starters, test ran ok.
MSA-DCS | WA3236246 | Unit 4, PRU camera 45 no picture | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 09:19:00 | 2020-04-21 17:22:00 | Pass | Rebooted cam 45 psu and modem in switchboard house kTested ok
MSA-DCS | WA3236302 | Unit 2 electrical room Fault zone 024 L2D4 | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 09:55:09 | 2020-04-21 13:00:00 | Pass | 21/4/20 MBReplace faulty high level smoke detector in unit 2 wing D, L2 D4 in Zone 24.De-isolate and leave system in normal working order.
MSA-DCS | WA3236322 | Unit 2 Up Stairs Plant Room Boiler Feed Water Pipe Work Leaking-see notes | Melaleuca Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 10:00:10 | 2020-04-21 15:00:00 | Pass | Carried out repairs to leaks on Hot Water Boiler #2 feedwater pipe.
MSA-DCS | WA3236404 | Jasper, Cell A06- Broken light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-21 12:00:00 | Pass | Replaced light switch
MSA-DCS | WA3236411 | Lenard, Cell B06- Broken Mirror | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Mirrors (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-05-07 14:30:00 | Fail | mirror replaced
MSA-DCS | WA3236422 | Social club Ladies/men’s toilet exhaust fan not working (located on the roof) -see notes | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-05-15 13:00:00 | Fail | Repaired fan motor
MSA-DCS | WA3236443 | Front Gate - Metal Detector blue light not working when you walk through | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 15:33:00 | Pass | Investigated fault, repaired intermittent faults with metal detector. Modified software, replaced faulty switch and cabling. Flashing blue light monitored for correct operation.Materials Used: ConsumablesTested OK.Job Complete
MSA-DCS | WA3236444 | control room NVR 2 H OD failure-SEME on site | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 11:03:35 | 2020-06-10 11:00:00 | Fail | Removed faulty hard drive and replaced with new one. Tested ok once configuration completed. Parts used:4TB hard drive
MSA-DCS | WA3236452 | Rear of old Video Link Scheme water leaking under footpath by safety cone | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 08:30:00 | Pass | Dig up pipe exsposed broken retic pipe reported to maintance
MSA-DCS | WA3236591 | Unit 14 - B5 basin tap loose/leaking/ | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-28 10:00:00 | Pass | Tighten Basin spout from behind in plumbing duct
MSA-DCS | WA3236629 | MPU (8) - Court Yard-M19 rear yard grille lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-23 13:00:00 | Pass | Serviced lock & adjusted strike
MSA-DCS | WA3236664 | Unit 2B Pod 2- faulty GPO for oven | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 12:48:23 | 2020-04-22 10:00:00 | Pass | Replaced PowerPoint and oven isolator
MSA-DCS | WA3236665 | Unit 2A Kitchen- oven not working correctly | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-28 13:30:00 | Fail | 2A Oven faulty. Check oven & controls. Found thermostat faulty. Pick up new parts. Return, remove faulty parts, install new thermostat & fittings. Repair pilot burners & fan noise. Assemble & test. Report to staff.
MSA-DCS | WA3236667 | Bakery- Door catch broken on Turbo 3000 Rack Oven | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-05-04 16:00:00 | Fail | Attended 4/5/20 12.30pmWorks complete as per service report.
MSA-DCS | WA3236672 | Unit 13, Cell D10- Personal lock striker plate missing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 10:30:00 | Pass | Replaced lock, strike & handle screws
MSA-DCS | WA3236678 | Main Prison- Zones B1,C1,D2,D3 & F1 - constant alarm outer perimeter, fence panel alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Apr 2020 | 2020-04-21 20:56:32 | 2020-05-13 14:52:00 | Fail | Calibrated intelliflex zones and confirmed activation.Zones cleared and stable
MSA-DCS | WA3236691 | Unit 14, Cell A10- Cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-29 10:30:00 | Pass | Repaired faulty lights in unit 14 a10
MSA-DCS | WA3236849 | L4 emergency door release has been knocked of wall and is hanging - see notes | Westralia Square | GMP-BR- HO | Building | Automatic Doors (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 13:49:48 | 2020-04-22 08:45:00 | Pass | Found glass break on west lobby door to be broken. Install new service spare and test. ALL OK. 1 x Standard glass break (white)
MSA-DCS | WA3236902 | ground outside Gwynlea building break in retic mains | Nyandi Training Academy | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 11:59:00 | Pass | CRACK IN MAIN LINE CUT OUT ADDED SLIPFIX TESTED AND ALL IN WORKING ORDER
MSA-DCS | WA3236906 | Gardens compound- Prisoners toilet not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-29 09:55:00 | Pass | Flushing mechanism was jammed pulled apart cistern and refitted it worked fine
MSA-DCS | WA3236908 | Reception, Light in passage above restraints cupboard near property office not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 08:30:00 | Pass | Repaired lights
MSA-DCS | WA3236912 | Unit 9 Cell C10 - secondry lock will not open, cant open the cell to lock inmates into | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 21 Apr 2020 | 2020-04-21 19:03:11 | 2020-04-22 14:15:00 | Fail | Installed replacement lock
MSA-DCS | WA3236927 | U8 C/D wing Regi oven not heating up properly | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 15:00:00 | Pass | Tested U8 C/D Wing Oven, tested fine. 14A per phase
MSA-DCS | WA3236931 | kitchen dishwasher Conveyor not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-21 17:45:00 | Pass | 21/04/20 - Called as requested to the dishwasher not working correctly the conveyor not running. Found the wiring fault so rectified, all working correctly now.
MSA-DCS | WA3236933 | kitchen Centre Diets Work Station Water spraying from copper pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 15:39:08 | 2020-04-22 15:12:00 | Pass | Jack hammerd floor to repair burst pipe under ground
MSA-DCS | WA3236938 | medical centre exterior light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-05-29 15:00:00 | Fail | Repaired lights
MSA-DCS | WA3236942 | medical centre corridor light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 10:30:00 | Pass | Repaired light
MSA-DCS | WA3236949 | U10 C2 Tap constantly running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-05-05 12:18:00 | Fail | Pulled apart taps replaced o rings and washers
MSA-DCS | WA3236973 | Monitor room PDA system TR7 fence in comms room - system trouble reported | Boronia Pre-release | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Apr 2020 | 2020-04-21 20:18:34 | 2020-04-23 10:15:00 | Fail | Attended site and replaced faulty duress enclosure kit with new enclosure kit. All replaced and tested ok. Job complete
MSA-DCS | WA3236984 | Unit 9 A Wing Grille far end of wing is damaged | Hakea Prison | GMP-BR- HO | Building | Internal Screens (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-07-20 10:00:00 | Fail | WELD GRILLE SECURE AGAIN
MSA-DTAG | WA3236197 | Please attend to the SAT issues following the below- | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 21 Apr 2020 | 2020-04-21 12:57:00 | 2020-04-21 15:30:00 | Fail | Level 6 Security PC was working slowly. Found critical error with memory. Recommend PC replacement as it currently can not handle too many apps opened at once. Also running Windows 7 which is no longer supported
MSA-DTAG | WA3236639 | Rockingham Court - Cell 4 Prisoner has urinated on the cell floor | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 0 | CLOSE | 21 Apr 2020 | 2020-04-21 16:28:23 | 2020-04-21 18:30:00 | Fail | Job done as per Work Order
MSA-DTWD | WA3236120 | EXIT door near to office - Testing for asbestos | Perth Campus B6 | GMP-BR | Waste Management | Asbestos removal (WM) | AWB Co. | 2 | CLOSE | 21 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 15:00:00 | Pass | Take sample of door for asbestos testing - Results sent to Manlio & Eric.
MSA-DTWD | WA3236287 | T Block, library wall GPO faulty at reception photocopy, picked up by Test and tag team | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 06:30:00 | Pass | Attended site and signed in. Located T block library. Found power to gpo for printer to be incorrect. Rewired gpo to correct terminations. Tested all okay. Job complete
MSA-DTWD | WA3236292 | M block L2 TM155/156/165 SENSOR LIGHTS NOT WORKING | Munster Campus (ACEPT) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-28 14:45:00 | Fail | Attended site and signed in. Located at T block. Found room with sensor turning lights on and aircon. Disconnected aircon from coming on with lights. Found another 2 rooms with sensors turning on really easily when you walk past in the hallway. Removed sensors and installed switches to rooms. Sensor in server room was faulty and not turning on. Replaced with 1 we removed from other room. Tested all okay. Job complete
MSA-DTWD | WA3236567 | D block D6 rear store lights need fixing | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 07:15:00 | Pass | Attended site and signed in. Located D block lab store room. Found 2 x lights in store not turning on. Tested sensor to be working fine. Replaced tubes to light fittings. Tested all okay. Job complete
MSA-DTWD | WA3236571 | S block exit door bell faulty | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 08:15:00 | Pass | Attended site and signed in. Located S block rear entry. Found door bell button perished and corroded. Removed and replaced with new style push button weatherproof switch. Tested all okay. Job complete
MSA-DTWD | WA3236670 | A Block Level 2 A267 - auto door is not operating electronicaly | Leederville Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 14:47:00 | Pass | Inspected door and found that the break glass unit had been pressed, reset break glass, checked over door, checked off sensors and tested operation.
MSA-DTWD | WA3236856 | Lvl 3, Deck - Exhaust fan has fault | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 21 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-29 16:25:00 | Pass | Chris Spadak completed investigation an repair to EAF systems.
MSA-DTWD | WA3236924 | Block 6 ground kitchen no cold water | Armadale Campus - 145 Jull Street | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 21 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-28 09:42:00 | Fail | Replaced taps
MSA-MRWA | WA3236548 | Ground male toilet Blockage in Male toilet end cubical -see notes | Heavy Vehicle Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-21 13:15:00 | Pass | Cleared blockage to male WC
MSA-MRWA | WA3236979 | Change rooms old shower head has broken off, please replace with new | Don Aitken Centre MRWA Head Office-Main Building-Basement | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-22 10:52:00 | Pass | Replaced shower rose to male toilets last shower cubicle basement
MSA-MRWA | WA3236981 | Level 2 -Lift not moving, please remediate- Please attend Wednesday 22/04/2020 | Don Aitken Centre MRWA Head Office | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 21 Apr 2020 | 2020-04-22 17:00:00 | 2020-04-22 10:29:00 | Pass | Found pressure switch not working. Isolate switch and advise Grant Smith of situation. Return lift to service
MSA-DCS | WA3237106 | Investigate bearings on washing machine #3 | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 3 | CLOSE | 22 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-22 08:15:00 | Pass | Bearings noisy. Contact supplier of machine for further repairs - machine not supplied by Veeco Laundry Systems
MSA-DCS | WA3237131 | monitor room camera 33 showing blue screen on wall | Boronia Pre-release | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 07:22:33 | 2020-04-22 10:00:00 | Pass | Attended site and found camera had lost its login authentification on software. Reconfigured camera login properties and re tested. All tested working correctly. Job completejob recalled, reattended installed firefox to configure PTZ, ADJUSTED BIT RATE,COMPRESSION VALUES & CREATE NEW ONVIF USER
MSA-DCS | WA3237133 | monitor room, zone 7 camera vision dark cannot tell which camera | Boronia Pre-release | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 07:24:49 | 2020-06-16 07:30:00 | Fail | Zone 7 realigned and focused via cherry picker.
MSA-DCS | WA3237161 | gym door 2 door lock fail | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 07:49:26 | 2020-04-22 15:15:00 | Pass | serviced gym door lock.
MSA-DCS | WA3237166 | Unit 5 - A Wing There is excess water, water leak in the service duck between A7 and A8 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-30 16:00:00 | Fail | Remove all copper pipe from Basin and toilet back to isolation valve and reinstate with new copper
MSA-DCS | WA3237170 | Unit 2 - D Wing Cistern to cell D8, Unit 2 will not fill completely / difficuilt to flush, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-28 11:00:00 | Pass | Realign push button assembly in plumbing duct
MSA-DCS | WA3237187 | SOP the lead on the hoover is getting hot when plugged in | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-29 11:30:00 | Fail | Picked up replacement appliance lead. Installed and tested for SOP hoover
MSA-DCS | WA3237194 | U10 B wing Major leak coming from roof | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 08:11:41 | 2020-04-22 21:00:00 | Pass | Temp fix with repair coupling until I got gear to replace pipe
MSA-DCS | WA3237204 | front gate control room kitchen Hot/Cold Hydro Tap not working | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-28 13:06:00 | Pass | Billi eco system in fault on arrival. Had to put computer on eco to find out what fault. Not registering filter and also in a filter lock out fault. Back to car to retrieve part. Flushed filter, ran system up to temp and further tests. Normal operation
MSA-DCS | WA3237262 | conrol room alarm with permatrax system constant alarm | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 08:55:54 | 2020-04-22 13:00:00 | Pass | Perimatrax zone F4 fulse activating, tuned and tested fumctioning correctly no longer fulse activating.
MSA-DCS | WA3237264 | control room MW system constant alarm C3 | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 08:59:26 | 2020-04-28 14:52:00 | Fail | Replaced anaconda and returned to nornal status, tested fully operational.
MSA-DCS | WA3237296 | kitchen Small kettle adjacent to rotel ovens tripping out power | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 09:19:53 | 2020-05-05 17:30:00 | Fail | 22/04/20 - Called as requested to the kettle not working, shorting out and tripping the breaker. Found the water level relay faulty and both indicator lights are not working and thermostat is in very poor condition. 05/05/20 - Returned to site with the parts required, fitted & tested, all working correctly now.
MSA-DCS | WA3237309 | Unit 4A Cell 34 Ceiling fan faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 12:00:00 | Pass | Replaced faulty ceiling fan
MSA-DCS | WA3237311 | Internal stores Office GPO Pulled out of the wall | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 09:30:07 | 2020-04-22 14:30:00 | Pass | Re secured gpo
MSA-DCS | WA3237317 | Reception - Door lock 9 south entry won’t turn & Handle 20 sally port & 39 strip room loose | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-28 15:45:00 | Pass | supplied replacement handle and cylinder
MSA-DCS | WA3237321 | Unit 10, D13 - Viewing hatch glass is broken | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 09:35:38 | 2020-04-22 16:00:00 | Pass | OBS PANEL REGLAZED
MSA-DCS | WA3237388 | key watch PTZ 22 not panning | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 09:35:24 | 2020-04-22 15:00:00 | Pass | Phone support, contacted site and advised to reset indigo vision PC. All reset and tested ok, PTZ 22 all working ok. Job complete
MSA-DCS | WA3237636 | SOP - H12 toilet seat damaged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-28 12:00:00 | Pass | Replace missing toilet seat in Cell. (Seat supplied by prison)
MSA-DCS | WA3238347 | Unit 2, - oven on B & D side of unit drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 14:00:00 | Pass | Remove oven, moflo tundish to clear fat blockage, rinse and test. Replace oven.
MSA-DCS | WA3238428 | Chlorine Plant - no chlorine injecting into the mains water | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | TRILITY Solutions Pty Ltd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 09:53:15 | 2020-04-24 10:07:00 | Fail | Flow switch replaced
MSA-DCS | WA3238596 | Unit 2 - B & D Door seal on oven, B&D wing requires attention and replacement | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-28 11:00:00 | Pass | Replaced Doorseal
MSA-DCS | WA3238808 | Master control room - golf 1 on the external microwave, in constant alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 09:59:26 | 2020-04-22 14:59:00 | Pass | Microwave set zone Golf 1 external alligned and tested fully operational (alarm relay 1 faulty utilising alarm relay 2)
MSA-DCS | WA3239188 | ISU Harding D wing Main Air-con unit is leaking really bad | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-28 14:00:00 | Pass | Fitted and secured dektites to frame. All ok
MSA-DCS | WA3239404 | garden Remand Controller switching off halfway through cycle | Hakea Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-05-22 11:30:00 | Fail | fitted temporary transformer and today replaced with new correct transformer. all working correctly
MSA-DCS | WA3240472 | Harding ISU C wing Really bad mold following air-con unit unit ripped off the roof twice -see notes | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-07-15 12:39:00 | Fail | REPAIR DAMAGED CEILING AND PAINT REPAIRS AREAS
MSA-DCS | WA3240991 | unit 4A near cell 60 verandah light missing | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 10:38:06 | 2020-04-22 14:30:00 | Pass | Replaced damaged verandah light
MSA-DCS | WA3241117 | unit 4A pod 1 verandah light faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 10:40:16 | 2020-04-22 16:30:00 | Pass | Replaced faulty PE cell and tested
MSA-DCS | WA3241119 | education programms, air con faulty | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 10:41:11 | 2020-04-24 11:30:00 | Fail | Attend site. Sign in. Found wall controller faulty on full time education room. Took unit details. Order parts. Pick up parts. Isolate unit. Remove and replace controller. Run unit. Check operation. All ok. Inform client.
MSA-DCS | WA3241312 | Assessments, room 27 - cannot lock with key 107 | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 10:42:37 | 2020-04-22 13:30:00 | Pass | gained entry to assessments office
MSA-DCS | WA3242338 | Unit 6, B & B Wing - hot water boiler states that the filter needs to be changed. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-28 11:25:00 | Pass | Call out for filter change. Filter had already been bypassed due to being blocked. Returned to car to get new filtration system. Removed old head and replaced with new capex asset - scale Maxi flow scale system. Fed to wallmounted unit - hung onto wall to be secure. Reset the counter on the rheem unit
MSA-DCS | WA3242722 | Harding ISU B wing-shower not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 11:51:00 | Pass | Repaired not working shower
MSA-DCS | WA3243634 | Kitchen, workshop - Kettle # 3 is making a noise when the paddle is engaged | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 15:30:00 | Pass | 24/04/20 - Called as requested to the kettle not mixing. Found the lid switch out of position so made good and tested all ok. Also checked the dishwasher as continuously using chemical (rinse aid). Found the sensor connected to the wash pump not the solenoid so made good tested all ok now.
MSA-DCS | WA3243992 | CCU, Cell 6- Lock is not working, door is unable to be open | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 22 Apr 2020 | 2020-04-22 15:31:15 | 2020-04-22 13:00:00 | Pass | Cell lock on CC Unit Cell 6 - Reported as not functioning correctlyLock removed from door and checked Issue is with worn officers cell keys reported to Security that these keys need replacing
MSA-DCS | WA3244861 | Gascoyne - Fire panel alarm fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 11:45:02 | 2020-04-22 13:47:00 | Pass | Attended site for fault on fire panel. When arrived contractor was drilling hole and set off fire panel. When arrived found zone isolated de-isolated and all back to normal working condition when left.
MSA-DCS | WA3248974 | unit 2 rear yard Plumbing isolation taps need lockable cover | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 13:30:00 | Pass | Secure valve pit lid
MSA-DCS | WA3249436 | Unit 9 A07, A10 Judas hatches Unable to open | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-06-03 10:00:00 | Fail | Job completed - inspect hatches require replacements. Attend site supply and install replacement.
MSA-DCS | WA3249490 | training building blocked sewer pipes | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 13:54:13 | 2020-04-24 08:30:00 | Fail | Complete
MSA-DCS | WA3249756 | unit 3 C wing urinal systems faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-28 11:00:00 | Pass | COMPLETED
MSA-DCS | WA3250368 | unit 2 C1 blocked sink | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 14:38:17 | 2020-04-23 12:45:00 | Pass | Clear blockage to basin waste
MSA-DCS | WA3250372 | Unit 2 C15 blocked shower and sink | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 14:42:55 | 2020-04-23 12:45:00 | Pass | Clear blockage to shower waste
MSA-DCS | WA3250377 | Unit 3, Cell C14- Cistern cracked at base, leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-29 08:00:00 | Fail | Pulled apart outlet valve replaced washer reinstalled
MSA-DCS | WA3250383 | Unit 1, Cell B13- Cell sink is cracked at base | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 11:40:00 | Pass | Pulled apart and cleaned
MSA-DCS | WA3250389 | Unit 2 A2 light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 11:30:00 | Pass | Replace faulty lamp in Unit A2
MSA-DCS | WA3250445 | SOG Base S/O Office damaged carpet | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-06-05 14:00:00 | Fail | Carpet tiles replaced
MSA-DCS | WA3250446 | SOG Base TSU Office damaged carpet | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-15 15:15:00 | Fail | Installed new carpet tiles and skirting
MSA-DFES | WA3249916 | 2x External GPO's waterproof covers are broken | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 17:00:00 | 2020-05-01 08:30:00 | Fail | Complete
MSA-DTAG | WA3237136 | L11 Swipe card reader / key pad – located at staff entrance near lifts-see notes for faults | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 22 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-22 12:00:00 | Pass | Tested with Officer's card & Area user's card, working OK. Reviewed transactions, noticed some had invalid Pins. Advice to get the user name, as suspected card or Pin issue.
MSA-DTAG | WA3238026 | L2A kitchen dishwasher has a pool of water on the bottom where filter blades are- see notes | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-22 13:00:00 | Pass | Complete
MSA-DTAG | WA3250465 | Central Law Courts-Main Building-Level 9 - rear of court 93, water leak from a pipe | Central Law Courts-Main Building-Level 9 | GMP-GR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 22 Apr 2020 | 2020-04-22 21:51:43 | 2020-04-22 20:00:00 | Pass | Complete
MSA-DTAG | WA3581209 | Retrospective WO Ref:48878497 - Up lift access system install | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-23 11:45:00 | Pass | Assist security contractors fit card reader
MSA-DTWD | WA3237142 | L2 canteen backyard broken tiles | Perth Campus B1 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 22 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-23 10:26:00 | Pass | Attend site Locate pavers that need replacing Source spare pavers onsite Use trolley and bring materials to level 2 Remove damage paver Lift other pavers to make room Re lay paving Clean up Remove rubbish
MSA-DTWD | WA3237306 | D Block - 2nd Floor - Staff Kitchen smoke alarm activation | Joondalup Kendrew Campus | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Critical Fire Protection & Training | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 17:00:00 | 2020-04-22 14:00:00 | Pass | BRAF - Investigated callout - D Block - L2 Staff Kitchen.Smoke detector Zone 15 isolated. Removed detector - out of date (no longer manufactured).replaced smoke detector and base - system back to normal.
MSA-DTWD | WA3238540 | A block, roundabout, foot path - street lighting damaged | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-05-07 14:55:00 | Fail | Attended site and signed in. Located faulty pole top light. Removed old fitting. Replaced with new led. Terminated in pole. Tested all okay. Job complete
MSA-DTWD | WA3238886 | C Block Admin Foyer - lighting faulty, Lighting in Foyer C Block admin. Height 4 metres | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-23 13:00:00 | Pass | Attended site and signed in. Located foyer lights. Found 1 to be out. Removed lamp from fitting. Replaced with new. Tested operation of lights. All okay. Job complete
MSA-DTWD | WA3239704 | Vehicle body building, ground level - High bay lights out and flashing west end of workshop | Thornlie Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-26 15:30:00 | Fail | Attended site and signed in. Removed old light fittings from roof. Installed suspended led battens to vehicle building. Tested all okay. Job complete
MSA-DTWD | WA3240153 | East end of T Block - The dripper line irrigation is not working | Murdoch Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | WESTERN IRRIGATION PTY LTD | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 09:15:00 | Pass | Irrigation technician checked the drip line and pressure reduce valve supplying drip line, increased irrigation run time to provide plant with sufficient water.
MSA-DTWD | WA3240347 | B block, student lounge room B40 - Automatic door is not working | Murdoch Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 22 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-22 14:42:00 | Pass | Inspected door and found to be working on arrival removed cover and inspected all ok checked for fault codes all ok at time of test.
MSA-DTWD | WA3240730 | L2 sth blk server room, Continuation of hire of temporary a/c units (April 2020-see notes | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-22 11:49:00 | Pass | Collected portable coolers from site on 21st April 2020
MSA-DTWD | WA3242968 | B block, B29 classroom - Water leaking from ceiling light and mini strip ceiling in classroom | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 22 Apr 2020 | 2020-04-23 17:00:00 | 2020-06-09 12:45:00 | Fail | Sourced leak and measured up for materials. Will need BRAFPicked up materials , installed box gutter as per BRAF.
MSA-DTWD | WA3243323 | Room D111 - Repair damaged carpet tiles along East Wall | Leederville Campus | GMP-BR | Flooring | Carpet (FL) | K Craft Building | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 16:48:00 | Pass | Cutting back to existing carpet , lay floor tiles supplied by client
MSA-DTWD | WA3250438 | level 1, E100 Cut Mine - replace batteries out of date | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 22 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-13 08:15:00 | Fail | Replaced faulty batteries with new . Job completed
MSA-DCA | WA3250703 | fault on fire panel (Loop 1 sensor 27 - workshop device in fault) | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Carpentry Workshop | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-23 12:45:00 | Pass | Attended site for fault on fire panel. When arrived found smoke detector loop1 sensor 27 in maintenance fault replaced all back to normalworking condition when left
MSA-DCA | WA3250735 | riverside left of the little house structure a burst pipe or tap | Sunset Hospital Heritage Precinct | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-23 16:31:00 | Pass | Redirect hose tap to below ground level supply and install valve box
MSA-DCS | WA3250513 | Zone lights in the perimeter 16 18 and 24 are not working | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 06:45:27 | 2020-04-23 11:30:00 | Pass | Attended site and checked Gallagher programming and all programming tested ok, issue with perimeter lights to do with electrical contractors . Job complete
MSA-DCS | WA3250521 | Zone 17, BE beam not working | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 07:02:03 | 2020-06-24 09:00:00 | Fail | Job complete
MSA-DCS | WA3250531 | Health, Cage Door- Lock is loose | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 23 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-13 08:15:00 | Fail | Job completed - Job completed - Replaced worn lock cylinder.
MSA-DCS | WA3250538 | Unit 2, B Wing, Cell B6- toilet cistern does not fill with water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-28 13:00:00 | Pass | Replace worn outlet rubber in cistern in plumbing duct
MSA-DCS | WA3250540 | Unit 1, B & D Wing - Hot water in showers not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-28 08:00:00 | Pass | Pull apart thermostatic mixing valves and clean out non return valve
MSA-DCS | WA3250542 | Stores, repair damaged concrete floor - safety hazard | Casuarina Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 23 Apr 2020 | 2020-04-28 17:00:00 | 2020-05-15 15:00:00 | Fail | OLD WALL REMOVED & NEW CONCRETE LAID
MSA-DCS | WA3250549 | Stores, Mens toilet and shower blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-28 09:00:00 | Pass | Plunge toilet to clear blockage, test several times.
MSA-DCS | WA3250569 | Unit 4, B & D Wing- Red handle/tap on urn broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 14:00:00 | Pass | Drain down boiling water unit, remove tap, clean out calcium buildup, reinstall and test
MSA-DCS | WA3250615 | control sprinkler valve room fire alarm panel is in fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 23 Apr 2020 | 2020-04-23 12:41:54 | 2020-05-04 08:01:00 | Fail | Attended site and found sprinkler valve room DBA in alarm and unable to reset.Checked valve and found alarm valve bypassing water and will require a fitter to repair replace valve set.Left in alarm/isolated.04-5-20MH&CVIsolated incoming towns mains supplyDrained sprinkler installation and mainsRemoved passing sprinkler mSv and alarm valve installed new mSv and alarm valve to include all new fittingsReconfigured drain and trim pipe work to suitRefilled mainsCleared fip
MSA-DCS | WA3250655 | visits room Multiple Camera faults | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-26 10:08:00 | Pass | Multiple faults in Visits centre and Video Link after generator testing. Sourced parts, attended site, repaired faults with workstations in video link and cameras in visits centre.Tested All OKJob CompleteParts:Consumables (SEME)
MSA-DCS | WA3250698 | kitchen water leaking from the roof | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 09:25:54 | 2020-04-23 13:03:00 | Pass | To be repaired by others
MSA-DCS | WA3250764 | SOG Pod, Front entrance - Unknown alarm, GLU1 Security DGP1 in POD | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-29 15:45:00 | Pass | Following additional alarms we traced all cabling from fibre modem to DGP. Finally located damaged cable in cable tray (rodent damage) repaired cable and taped joint.
MSA-DCS | WA3250765 | MPU (8) - Control Room-Personel access handle from spu to mpu door is broken | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 13:00:00 | Pass | Replace handle, hinges, adjusted strike and repaired door control
MSA-DCS | WA3250774 | Unit 13, A & C dayroom - Vinyl floor covering is lifting by the Kitchen/water cooler area | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-06-22 10:29:00 | Fail | SUPPLY AND INSTALL NEW STUDDED RUBBER FLOORING TO AREAS
MSA-DCS | WA3250781 | Unit 14, D Wing, Cell D03- Shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 15:00:00 | Pass | Remove grate, remove hair, moflo, rinse, plunge, reinstall grate and test. Plunge Basin.
MSA-DCS | WA3250840 | Fire panel- Sub Fip remand fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 23 Apr 2020 | 2020-04-23 14:59:42 | 2020-04-24 11:00:00 | Fail | Attended site and found fault to be unit 7 Vesda low flow fault. Now access to cells or roof at this time.Will require return visit booked for two techs with hand held programmer to find out what pipe is low then to access roof area to clear pipes and sample points.24/4/20 JN MSUnit 7 Wings G F and S in low airflow fault. Cleared sampling points and tubing out from roof space above and levels returned to normal. Normalised wing E F S vesda as flows were all 800-1300 after cleaning. All ok when left site.
MSA-DCS | WA3250859 | Paint Shop - Workshop-please investigate flooding to rear of paint shop | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-07-25 15:30:00 | Fail | 10/6/20- Prep work. Marked out and cut concrete.25/7/20 - Removed concrete. Dug holes. Installed blue metal base. Installed soak wells and rio pins. Installed new concrete slab and cleaned up.
MSA-DCS | WA3250889 | Gatehouse, kitchen - Urn in the kitchen leaking and overflowing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-29 08:15:00 | Pass | Recalibrate boiler unit
MSA-DCS | WA3250950 | Visits-Non Contact area H12 toilet seat faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-05 14:00:00 | Fail | Attend visits and searched for the job. No such area exist within the prison
MSA-DCS | WA3251008 | Unit 3, B Wing Cleaning Cupboard - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 10:30:00 | Pass | Replaced light
MSA-DCS | WA3251012 | C wing yard light cover is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 11:30:00 | Pass | Repaired light
MSA-DCS | WA3251016 | Kitchen, Back Fridge - Electrical Box come off from back fridge | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 14:00:00 | Pass | Electrical box exposed, had metal workshop make up top hat and installed.
MSA-DCS | WA3251026 | Unit 3, Cell C1- Judas hatch not unlocking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-28 16:15:00 | Pass | Installed replacement padlock.
MSA-DCS | WA3251030 | Unit 3, A & B Wing- External dayroom doors unable to unlock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 12:42:46 | 2020-05-25 14:15:00 | Fail | Supplied and Installed new strikes to Unit 3 - A and B Wing External Day Room doors.
MSA-DCS | WA3251056 | Kitchen, aircon B side dinning room - leaking | Wooroloo Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 12:54:40 | 2020-05-05 10:00:00 | Fail | Attend site. Sign in. Found evap cooler leaking water. Isolated water supply. Found basin cracked and beyond repair. Braf to be submitted.
MSA-DCS | WA3251057 | Perimeter lights are out , number 16 &18 &24 | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 12:55:13 | 2020-05-13 15:30:00 | Fail | Replaced 3x faulty flood lights with LEDs using cherry picker
MSA-DCS | WA3251063 | Mechanics work shop - hot water urn leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 12:56:38 | 2020-04-24 09:45:00 | Pass | Technician replaced solenoid, replaced hot tap, replaced sedi/carb in original filtration
MSA-DCS | WA3251068 | Unit 4 PRU - MDAS - not showing some PDA locations | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Apr 2020 | 2020-04-23 20:59:59 | 2021-01-11 08:00:00 | Fail | Tune and test 4 times, all ok.
MSA-DCS | WA3251079 | Eyre block kitchen Sink in kitchen is leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 11:00:00 | Pass | Seal around pipe work to run to stop water leaking through
MSA-DCS | WA3251112 | Visits, Outside main spine walkway- Roof flashing falling off | Melaleuca Prison | GMP-BR- HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-08-05 11:27:00 | Fail | REPAIRED WALKWAY FLASHINGS - SCREW OFF
MSA-DCS | WA3251177 | unit 2, B1 - broken toilet seat, blocked sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 14:00:00 | Pass | Clear blocked shower and sink to u2 b1
MSA-DCS | WA3251192 | Unit 2 , B2 - Blocked sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 15:00:00 | Pass | Clear blockage to sink and shower u2 b2
MSA-DCS | WA3251205 | unit 1 B2 blocked sink and shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 16:00:00 | Pass | Clear blockage to sink and shower u1 b2, was also informed by escort officer that hot tap to basin was leaking, replaced hot tap spindle to basin. Was informed that u1 D14 was had just blocked up. Cleared blockage to sink and shower.
MSA-DCS | WA3251223 | laundry No1 dryer Milnor-gas is not coming on not getting hot | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 13:46:26 | 2020-05-12 08:00:00 | Fail | Found lint filter torn letting lint through to sensor. Replaced filter and test OK
MSA-DCS | WA3251241 | Lvl4, 2x lights are flickering- Office 4.D & Outside office | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 16:30:00 | Pass | Replaced lamps and starters , test ran ok.
MSA-DCS | WA3251256 | Reception Roller- not opening or closing correctly | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Automatic Doors (BU) | UNIVERSAL DOORS | 0 | CLOSE | 23 Apr 2020 | 2020-04-23 18:26:08 | 2020-06-22 12:45:00 | Fail | ATTENDED SITE, SUPPLY & INSTALLED ONE (1) GRIECO 1 HP, 3PH HIGH CYCLE DRIVE UNIT AS QUOTED.
MSA-DCS | WA3251300 | Kitchen - Combi oven, smell/leak gas, when using steam function | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 15:31:20 | 2020-05-05 15:45:00 | Fail | Found leak at gas valve also noted steam blower & mixing chamber has warped plastic & some air/gas mix leaks. Left site to arrange quote & parts. Return 5/05/20 with parts to replace.
MSA-DCS | WA3251309 | unit 10 B wing worn out copper pipe above manhole | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 15:30:00 | Pass | Turned off water cut old leaking pipe replaced with new 3m pipe
MSA-DCS | WA3251321 | reception shower block Light fitting needs replacing, lamp holder broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-24 09:30:00 | Pass | Repaired light
MSA-DTAG | WA3250601 | 2x external windows have been smashed | Mandurah Courthouse | GMP-BR-HO | Glazing | Window Glass (GL) | O'Brien Glass With Care | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 17:00:00 | 2020-05-08 14:00:00 | Fail | Reglazed Window 6mm Coloured Toughened Safety Glass
MSA-DTAG | WA3250733 | L13 Flickering light in the Level 13 Foyer opposite the stairway door | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 10:15:00 | Pass | Job complete
MSA-DTAG | WA3251116 | Cell 2 and non contact room in custody center-offender has scabies-see notes | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 19:30:00 | Fail | Job Completed 24/4/20
MSA-DTAG | WA3251174 | L10 Registry of Births, Deaths and Marriages-various lights need changing-see notes | Westralia Square | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 14:15:00 | Pass | Light fitting in male corridor needs replacing. Asked client to call in another job
MSA-DTAG | WA3251233 | registry counter through clean of glass | Mandurah Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-23 14:45:00 | Pass | Job Completed 23/4/20 at 11:45AM
MSA-DTWD | WA3250544 | G Block, Disabled toilets- tiles in doorway are lifting and need repair | Mandurah Campus (formerly Peel) | GMP-BR | Flooring | Tiling (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 23 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-04 16:45:00 | Fail | Have assessed damaged tiles. Old tiles no longer available will need to source suitable replacement tiles and return to complete
MSA-DTWD | WA3251017 | block 6 6F – Painting & Decorating Ducting cover has come away from the wall | Thornlie Campus | GMP-BR | Building | Internal Screens (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-05-13 13:45:00 | Fail | Re-secured ductwork around conduits - All completed
MSA-DTWD | WA3251028 | Level 1, room 260 - replace faulty detector | Perth Campus B5 | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Critical Fire Protection & Training | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-24 12:49:00 | Pass | Rectified as per signature slip
MSA-DTWD | WA3251069 | D Block, D37 Meat Trade – Leaking mixer tap | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-24 16:21:00 | Pass | Multiple leaks all small and only at times until fill trough up - fixed
MSA-DTWD | WA3251176 | Plant Room- Chiller circuit B oil faults | Perth Campus B4 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-06-11 15:42:00 | Fail | ATTEND SITE. SIGN IN. GOT KEYS AND SET UP WORK AREA. ISOLATED CHILLER AND REMOVED B COMPRESSOR FUSES. TAGGED OUT CHILLER. ISOLATED OIL LINE CIRCUIT AND RECLAIMED OIL AND REFRIGERANT INTO CONDENSER. REMOVED END OF OIL LINEENTERING COMPRESSOR AND CHECKED FOR BLOCKAGE. FOUND NONE. BLEW THROUGH OIL LINE WITH NITROGEN AND FOUND NO CONTAMINATES. RESEALED OIL LINE AND PRESSURE TESTED. FOUND NO LEAKS. VAC B STAGE UNTIL CORRECT READING ACHIEVED. OPEN UP ALL ISOLATION VALVES. INSTALL COMPRESSOR FUSES. RAN CHILLER. CHECKED PRESSURE DROP ACROSS INTERNAL COMPRESSOR OIL FILTER. FOUND TO BE 20KPA INDICATING NO BLOCKAGE. FOUND PRESSURE DROP ACROSS OIL LINE TO BE 30KPA. CHILLER IS NOW RUNNING OK. CLEANED UP WORK AREA. INFORMED CLIENT.
MSA-DTWD | WA3251225 | Level 2, Room 213-211- VAV Faults | Perth Campus B4 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-29 13:27:00 | Fail | works completed
MSA-DTWD | WA3251239 | E block ground EG19 Repair/replace lights in upright freezer | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | Equans Mechanical Services Australia | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-07-10 13:00:00 | Fail | Arrived on site, signed in. Checked in gained access keys, had alarms turned off to room. Gathered tools and equipment, isolated and locked out power and tested for dead. Dismantled light area to freezer and replaced required components, reassembled unit. Tested all ok. Disposed of rubbish. Completed paperwork.
MSA-DTWD | WA3251245 | Burst water main at the back of Block 10 | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-23 16:02:00 | Pass | Plugged rpz job complete
MSA-DTWD | WA3251266 | Room JL-14, in Hanger - 5 meters of ceiling thats Collapsed | Jandakot Campus - Hangar | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 17:00:00 | 2020-07-01 14:00:00 | Fail | Have attended site and removed damaged section of the ceiling and made safe. Will need to return to complete repairs once leak has been resolved. New section of ceiling installed
MSA-DTWD | WA3251269 | D block D009 Some of the fluorescent lights are not working | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-06-16 13:04:00 | Fail | Replaced faulty lights with new in D009. All lights working properly now.job completed
MSA-DTWD | WA3251282 | Block 10 Ground floor external chilled water unit Tap and drain leaking | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 23 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 12:48:00 | Pass | Fix leaks and replace jug filler
MSA-DTWD | WA3509554 | Retrospective work order-Corridor, Level 6 - Replace batteries, access door proxy. | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 17:00:00 | 2020-08-04 15:30:00 | Fail | Checked and tested battery voltages and confirmed battery charge voltage.Checked and confirmed back up battery functionality.Removed old batteries from site for disposal.
MSA-MRWA | WA3250716 | L3 nth west corner Bank of LED fittings not working, please attend and remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | LYNX INTEGRATED SYSTEMS | 1 | CLOSE | 23 Apr 2020 | 2020-04-24 17:00:00 | 2020-04-23 13:00:00 | Pass | Re-programmed local sensor to turn lights on when disabled.
MSA-MRWA | WA3251161 | Lift number 4 is not operational and is stuck on level 8 | Don Aitken Centre MRWA Head Office | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 23 Apr 2020 | 2020-04-23 17:36:05 | 2020-04-23 17:45:00 | Fail | Lift4 DAC-Geared :Rope brake circuit open with all switches active. Check all wiring and relays. Reset RCB Circuit board and test. Return lift to service and monitor.To be closed out at $0
MSA-MRWA | WA3251249 | ground carpark Remove damaged ladder from carpark | Heavy Vehicle Services | GMP-BR | Cleaning | Rubbish Removal (CL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 11:00:00 | Pass | Found ladder - hard to get into location, office closed - No onw on site to sign. Brought back to yard for disposal.Works are now completed - Old ladder removed.
MSA-DCS | WA3251792 | External camera B -1 is giving no signal | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 10:49:01 | 2020-04-24 14:27:00 | Fail | External camera B found with faulty cable connector, replaced BNC connector and tested operational.
MSA-DCS | WA3251821 | Kitchen - dishwasher tap broken sink tap damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-24 12:20:00 | Pass | Re washer taps and replace outlet to KS
MSA-DCS | WA3251829 | Case Planning HWU has electrical smell when turned on. | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Apr 2020 | 2020-04-29 17:00:00 | 2020-05-01 09:00:00 | Fail | Disconnected hws , site will generate a job to reconnect when new hws is fitted. Reconnected HWU on this same job. 010520 when asked to by prison.
MSA-DCS | WA3251833 | Unit 1 - B & D Dayroom Flooring lifting in multiple places | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 24 Apr 2020 | 2020-05-01 17:00:00 | 2020-09-08 14:30:00 | Fail | damaged section of flooring replaced
MSA-DCS | WA3251874 | Unit 7 E14 light fitting faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-28 11:00:00 | Pass | Repaired light
MSA-DCS | WA3251875 | PTZ camera 3 visual but no pan or tilt & zoom in & out | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Apr 2020 | 2020-04-25 08:11:46 | 2020-04-24 15:30:00 | Pass | Fixed the faulty ptz function camera 3, job completed.
MSA-DCS | WA3251906 | control camera 177 night vision not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 12:43:56 | 2020-04-25 12:28:00 | Fail | Investigated fault, found this camera is an infrared FLIR combination camera with a day vision and night vision together. Day vision camera is 177 and night vision is 178. Between both day and night vision, a clear image can be seen at all times.Tested OKJob Complete
MSA-DCS | WA3251922 | Unit 4 control room Air Con Smelling-Please see Tony Wicks before starting Job | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-13 09:30:00 | Fail | Replaced cover and deoderiser unit. All ok at time of departure
MSA-DCS | WA3251929 | Unit 5, D wing - toilet and sink leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-01 10:00:00 | Pass | Tighten basin spout connection under the basin
MSA-DCS | WA3251989 | Gound floor, training room 5 - No power to lights and electrical equipment in the room. | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 24 Apr 2020 | 2020-04-25 09:49:55 | 2020-04-24 14:05:00 | Pass | Replaced failed lamps, ballasts and starters as required to prevent rcd to trip in room 5.
MSA-DCS | WA3252013 | Reception Entrance Door - swipe card access not working | Rockingham Justice Complex | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 14:00:20 | 2020-04-28 14:58:00 | Fail | Traced cabling and found yellow and green wires disconnected from egress button. Terminate egress button and configured door. Tested operation - all OK.
MSA-DCS | WA3252054 | Faulty anti-ram barrier over at PFM Stores. | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-24 13:30:00 | Pass | 24/04/20Rectified
MSA-DCS | WA3252074 | Laundry, dryer no 6 - Air leaking badly from small air hose behind dryer 6 | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 24 Apr 2020 | 2020-04-25 11:36:13 | 2020-05-08 12:30:00 | Fail | Attend site & determine air hose split. Supply& fit new hose.
MSA-DCS | WA3252088 | Unit 5 cell A24 Cell light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 14:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3252100 | unit 2, A wing - Sink will not unblock even after plunger | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 08:00:00 | Pass | Plunge sink to clear blockage and test
MSA-DCS | WA3252139 | SITE COST Cabinet shop and Paint shop - Reconnect Aerials | Hakea Prison | WSM-BR-SITE | ICT/Audiovisual | Hardware / Equipment (AV) | Sapio Pty Ltd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 11:00:00 | Pass | re connected aerial
MSA-DCS | WA3252187 | Unit 7, H8 - needs new rubber washer | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 12:15:00 | Pass | Renew outlet washer to cistern
MSA-DCS | WA3252198 | unit 2 cell B4 prisoner lock not working | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 24 Apr 2020 | 2020-04-25 13:23:52 | 2020-04-24 15:45:00 | Pass | Attend to Bandyup womens Prison Prisoners Privacy Lock - Unit 2 Bwing cell B4 - unable to be unlocked from inside New Privacy Lock fitted
MSA-DCS | WA3252201 | unit 5 house 6 room 1 ceiling fan broken | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 15:30:00 | Pass | Replaced high downlights, oyster light and ceiling fan
MSA-DCS | WA3252206 | Unit 6 cells A9 and A21 Flush buttons stuck in | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 13:25:00 | Pass | Removed old cistern installed new one
MSA-DCS | WA3252209 | Unit 5 staff toilet Cistern Leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-24 16:50:00 | Pass | Replaced outlet washer
MSA-DCS | WA3252222 | Unit 6, A wing showers - shower not turning on | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 15:05:00 | Pass | Removed old installed new shower quote turn taps
MSA-DCS | WA3252223 | INF (10) - B Wing -Personal hatch difficult to close (loose screw allows tongue recess to drop) | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 11:00:00 | Pass | job completed - repairs to hatch lock.
MSA-DCS | WA3252235 | Unit 10, A6 - water leaking behind sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-29 14:15:00 | Pass | Repair leak to bridging piece to basin
MSA-DCS | WA3252255 | BR-unit 3 office Transponder 10 failed testing during maintenance | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Apr 2020 | 2020-04-25 14:29:54 | 2020-04-24 16:30:00 | Pass | Battery failed during routine maintenance testing. Removed and replaced. Tested ok. Part used:12V 7AH battery from a Hakea site stock
MSA-DCS | WA3252257 | Crisis care, control room - Power duct is damaged, missing lid | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-12 12:30:00 | Fail | Installed 4 x new GPOs on damaged power duct
MSA-DCS | WA3252274 | kitchen dishwasher Dishwasher Pipe broken,Snapped needs solder or crimp | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 15:50:00 | Pass | Asked to come back on a different day when the kitchen is not so busy b
MSA-DCS | WA3252275 | Unit 6, D10 - toilet button is stuck in | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 12:15:00 | Pass | Removed old cistern installed new one
MSA-DCS | WA3252286 | Unit 9, D9 - S bend in sink is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-29 15:15:00 | Pass | Renew p trap to basin
MSA-DCS | WA3252287 | Zone 11 Vehicle Gate - no alarm | Boronia Pre-release | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 18:59:41 | 2020-05-01 07:57:00 | Fail | sourced partsRemoved non sensitive cable and installed new cable Tested and confirmed correct operation
MSA-DCS | WA3252300 | front gate control fire alarm siren not working | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-28 12:02:00 | Pass | Attended site and found work requested not in our scope of works. On site contact said when job logged with PFM they requested SEME to do the works as part of there system.
MSA-DCS | WA3252318 | Unit 3 cell C14 Water flooding corridor from service duct | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 10:35:00 | Pass | Removed outlet valve replaced and installed new washer
MSA-DCS | WA3252363 | cctv gate house - zone 13 ptz doesnt pan to pe beam activation | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Apr 2020 | 2020-04-25 18:04:09 | 2020-04-29 09:20:00 | Fail | Tested all PTZ function All working normally Visits cameras offline due to refurbishment of building
MSA-DCS | WA3253855 | front gate control fire alarm siren not working | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-10-07 15:50:00 | Fail | Investigated and this requires a small project to install additional equipment if site requires siren to be audible in all areas.Refer to quote.Job Complete
MSA-DCS | WA3509085 | Retrospective work order - Gate House - Crypt Converter on the BMS System is faulty/Not receiving | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Schneider Electric Australia Pty Ltd | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 15:28:00 | 2020-05-12 11:00:00 | Fail | Replaced faulty media converter
MSA-DFES | WA3251970 | workshop and entry ground Lights are not working in the shower area outside lunchroom & carpark | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-14 10:15:00 | Fail | COMPLETED
MSA-DFES | WA3251978 | Office entry Swipe Card Panel working spasmodically, sometime takes 3 to 4 swipe before opening | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-28 16:30:00 | Pass | 28/4/20 - Dean SimpsonReplaced faulty lock, and tested all ok.
MSA-DTAG | WA3251883 | building as the intercoms are not working -see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 24 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 15:30:00 | Pass | Found that the Intercoms are connected through the same optic fibre switch, once it was rebooted the Intercoms came back online
MSA-DTAG | WA3251885 | Control room - Camera's down no visual | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 12:25:17 | 2020-04-29 14:00:00 | Fail | Rebooted switch
MSA-DTAG | WA3251974 | Basement, lunch room - oded lock for the staff lunch room has been playing up | Supreme Court-Supreme Court Building-Basement | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-28 15:34:00 | Pass | Attended site, lockwood 530dx failed due to broken spring.Repaired lock, and all working.
MSA-DTAG | WA3252311 | Special clean Cell 5 - prisoner has been spitting over the cell floors | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 19:33:23 | 2020-04-24 18:15:00 | Pass | Job completed as per work order
MSA-DTAG | WA3252351 | sliding door in f.a.t building is not closing, security screening area | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Keys & Access (SE) | Sapio Pty Ltd | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 21:15:56 | 2020-05-15 10:00:00 | Fail | SAT R1 restored. Checked all cameras for viewing and recording. Checked system out. All OK.Job completed.
MSA-DTWD | WA3251984 | T block, level 2, staff toilet - will not flush out order sign put up. | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-24 16:13:00 | Pass | Lekaing cistern adjusted and fixed
MSA-DTWD | WA3252010 | E block E38 Coolroom – Water leaking through light fitting | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 12:30:00 | Pass | Inspected light in E38 coolroom, went and picked up. New fittings, swapped. Tested all working, job completed
MSA-DTWD | WA3252040 | E block, level 2, E205 - faulty lights require replacing | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 09:30:00 | Pass | Repalced faulty fluro and tombstone.job completedm
MSA-DTWD | WA3252041 | D block L1 main foyer Fire Panel has alarm Charger Voltage 17.58 ST | East Perth Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-07 13:00:00 | Fail | Battery fault. New batteries ordered. Technician to return.7th May - Technician re-attended site to replace fire panel batteries. All clear upon departure.
MSA-DTWD | WA3252046 | E block L1 E104 replace light | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 08:30:00 | Pass | Replace faulty fluro and tombstone.job completed
MSA-DTWD | WA3252048 | E block, ground floor, restaurant female toilets, 2nd cubicle - not flushing | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-07 10:06:00 | Fail | COMPLETED
MSA-DTWD | WA3252051 | A block L3 Replace vent cover missing A344 | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-14 14:00:00 | Fail | Picked up required parts and large ladder,attend site,set up and removed all four supply air grills inside room a344,installed and secured four new grills,tested system and cleaned up work area,left all operational
MSA-DTWD | WA3252211 | E block E23 Female Staff Toilets – Drains overflowing, floor is flooded | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 24 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 15:57:00 | Pass | Unblocked drain
MSA-DTWD | WA3252229 | F block - taps are leaking the the F Block cleaners store. | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 12:00:00 | Pass | Replace leaking taps
MSA-DTWD | WA3252232 | B block 2 cisterns in the female staff toilet & 1 in the male staff toilket are leaking | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 13:15:00 | Pass | Repaired 3x cisterns
MSA-DTWD | WA3252239 | staff room of the annex carpet has come apart from the seam | Jandakot Campus - Annex | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-25 10:45:00 | Fail | Repair carpet join
MSA-DTWD | WA3252250 | Reception fluro lights need to be replaced as they are falling apart | Jandakot Campus - Annex | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 24 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-07 09:45:00 | Fail | Attended site and signed in. Replaced 2x damaged lights in foyer with new led fittings. Work complete.
MSA-DTWD | WA3252272 | Level 2, female toilet 237 - toilet running | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 24 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-29 17:50:00 | Pass | Fixed toilet
MSA-MRWA | WA3251851 | ground Compound entry gate Gate locked open unable to close, intermittent fault. | Materials Engineering Branch | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 24 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-24 10:26:00 | Pass | Inspected manual override on gate motor. It is possible to disengage the drive but the handle no longer locks in place as it has been forced previously. The lock no longer engages. The motor would need replacing to repair this.
MSA-MRWA | WA3252290 | Lift #4 is stuck at level 8 | Don Aitken Centre MRWA Head Office | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 24 Apr 2020 | 2020-04-24 19:04:24 | 2020-04-24 18:15:00 | Pass | Lift4 DAC-Geared :Fault recorded are SAF SAF operated, SAF ETSC inp err, SAF DFC inp err. Trace for fault, found voltage at sc1 and not at sc 2. Changed RBC board with lift 2. Also changed DBP relay. Run lift and monitor. Lift running ok. Put lift back on service.
MSA-DCS | WA3252378 | Main prison gate is not closing | Wooroloo Prison Farm-Administration Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Apr 2020 | 2020-04-25 11:59:56 | 2020-04-25 09:00:00 | Pass | Phoned site - site confimed access equipment is working correctly and gate is attempting to operate correctly, motor is failing to engage, access door mechanic required to repair gate.
MSA-DCS | WA3252391 | Bandyup Kitchen bratt pan is broken SITE COSTED | Bandyup Prison | WSM-BR-SITE | Building | Materials (BU) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 25 Apr 2020 | 2020-04-25 13:47:56 | 2020-05-27 15:20:00 | Fail | 25/04/20Attended Bratt Pan. Right hand burner blocked with rust, gas was bypassing burner inlet and igniting. Cleaned out burner inlet and jet. Burners need replacing.I got unit workingUnit is old and worn.Checked gas pressure: low, adjusted to required pressure.Issues1. Burners are corroded and need replacing.2. Pilot needs replacing.3. Thermocouple has low voltage.4. Piezo worn, needs replacing.5. HT lead needs replacing.6. Gas hose is corroded, needs replacing.7. Unit needs restraint chain installed to protect gas hose.8. New seal between burner box and pan.9. Some steel flashings in burner box need re attaching. And need a strip of 1m x 40mm x .5mm or .3mm SS and some angle. Pop rivetsParts required1 x burner- TPG (right)2 x burner- TPG (both sides)3 x burner- TPG 1 x burner- TPG ( flame bridge on left)1 x pilot RBA/GPGDSA/BLA complete with bracket 1 x thermocouple-L=6001 x electrode- ceramic 1 x Pilot pilot 1 x sparked-piezo for TPG1 xlead-HT 650mm for
MSA-DCS | WA3252405 | Zone 11 alarm is not resetting | Wooroloo Prison Farm-Administration Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Apr 2020 | 2020-04-26 10:44:28 | 2020-04-30 15:45:00 | Fail | Attended site, checked zone 11, all cleared. checked logs & confirmed normal all day 27/4/20 tested all ok
MSA-DCS | WA3252411 | Main prison gate is not closing | Wooroloo Prison Farm-Administration Centre | GMP-BR- HO | Security | Security Management System (SE) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 25 Apr 2020 | 2020-04-25 15:01:03 | 2020-04-25 12:45:00 | Pass | Opened up control board and found "0L2" error on the inverter, motorover load. Found the weather is the cause of the over load. Changed VF setting to High torque. Test operation several times, tested OK
MSA-DCS | WA3252431 | Unit 5 Multiple Cameras,Control room Key damaged,Duress receiver 3.1 no response,4.4 keeps alarming | West Kimberley Regional Prison | GMP-BR- HO | Equipment | Security Equipment (EQ) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Apr 2020 | 2020-04-26 13:35:45 | 2020-04-26 08:30:00 | Pass | Multiple cameras out in unit 5. Investigated fault and found power supply had lost power to fiber modems. Tested supply voltage from UPS and all tested ok. Reset power supply to fiber rack and repowered cameras. All had reset and tested ok. Job complete
MSA-DCS | WA3252446 | Banksia Hill Detention Centre - ISU Unit Cameras 61-65 have lost vision. | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Apr 2020 | 2020-04-25 22:41:33 | 2020-04-28 16:14:00 | Fail | Sourced parts, attended site, traced cables and repaired cable faults, replaced faulty power supply module and fibre patch.Tested cameras 61,62,63,64 and 65 OK.Job CompleteParts Used:24VDC Power Supply Module (PFM stock)Consumables / Fibre Patch (SEME Stock)
MSA-DFES | WA3252379 | In Joondalup FS, 47 Drovers Pl, Wanaroo- sewer pipe is blocked | CFRS Joondalup | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 25 Apr 2020 | 2020-04-28 17:00:00 | 2020-04-26 08:26:00 | Pass | Attended site to blocked septic tanks, used drain machine to clear.
MSA-DCS | WA3252464 | Control room Key is damaged | West Kimberley Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Apr 2020 | 2020-04-27 07:41:31 | 2020-04-26 09:00:00 | Pass | Gallagher master key from keybunch 164 was not working correctly, repaired and cleaned out key components and sprayed with lubricant for spring component of key. All retested and working correctly. Job complete
MSA-DCS | WA3252465 | Duress receiver 3.1 no response | West Kimberley Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Apr 2020 | 2020-04-27 07:42:59 | 2020-04-27 17:30:00 | Fail | Attended site and replaced 3.1 Duress receiver with new duress receiver. Site spare used. All tested and working ok. Job completeTravel to Perth
MSA-DCS | WA3252466 | Duress 4.4 Tampa keeps alarming | West Kimberley Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Apr 2020 | 2020-04-27 07:43:25 | 2020-05-25 18:00:00 | Fail | Located fault on MDAS PC map. Numbering on enclosure does not match. Removed and replaced receiver PCB and enclosure. Alarm messages cleared from PC. Tested PDA 128 for accuracy. Tested ok. Parts used:SEME stock
MSA-DCS | WA3252468 | In the control room - Monitor 9 is faulty. Just a black screen. | West Kimberley Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-19 19:36:00 | Fail | Replaced monitor and modified bracket to suit.Wisenet 19" monitor from seme StockSundries used
MSA-DCS | WA3252469 | Unit 4 Corridor 1- camera is faulty. | West Kimberley Regional Prison | GMP-BR- HO | Equipment | Security Equipment (EQ) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-27 08:00:00 | Pass | Attended site and reset camera and reterminated camera power into separate power supply terminal. Re adjust and focused camera. Tested camera functions and all working ok. Reattended following day and checked camera recordings for correct operation and all tested ok. Job complete
MSA-DCS | WA3252477 | Gatehouse- The external perimeter fence, section D1 is not activating. | Casuarina Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Apr 2020 | 2020-04-26 12:44:01 | 2020-04-26 11:30:00 | Pass | All systems tested ok d1 was activated 3 times all ok
MSA-DCS | WA3252568 | Karnet Prison Farm-SITE COSTED In C wing Unit 3 fridge not cooling | Karnet Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 26 Apr 2020 | 2020-04-26 17:03:14 | 2020-04-29 16:00:00 | Fail | found fridge on 16 degrees, compressor not starting , replace faulty start capacitor.
MSA-DCS | WA3252594 | Gate house PA system display showing network error | Broome Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-18 17:00:00 | Fail | Reloaded correct ACM file and Angela file.Tested all nodes and confirm fault has cleared
MSA-DCS | WA3252611 | fire alarm is going off in unit 2 cell 13 | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 26 Apr 2020 | 2020-04-26 20:14:08 | 2020-04-26 18:28:00 | Pass | Attended site after hours to Bandyup Prisonfor faults on the panel found the following.1: Windjana C Wing Cell 13 device 5095 Az 23 Av 24 located detector and fitted new reset and left normal.2: Unit 6 Cell A9 in intermittent misssing fault device 13014 Az 30.Located detector and tightened terminals and re fitted detector and left normal.
MSA-DCS | WA3252638 | Fire system showing fault for block 6 A9 | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 27 Apr 2020 | 2020-04-27 09:18:10 | 2020-04-27 09:18:00 | Pass | After hours call to Bandyup Prison for fault in unit 6 found device 13014 cell A9.Removed detector and fitted new left system normal.
MSA-DCS | WA3253332 | Banksia Hill Detention Centre-Gatehouse- Inner lobby door not locking | Banksia Hill Detention Centre-Gatehouse | GMP-RM | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 27 Apr 2020 | 2020-04-27 14:15:45 | 2020-04-27 12:45:00 | Pass | job completed - Repaired faulty lock
MSA-DCS | WA3253461 | West Kimberley Regional Prison- unit 2 house 2 is currently offline | West Kimberley Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Apr 2020 | 2020-04-27 23:54:05 | 2020-04-28 09:00:00 | Fail | Phone support for WKRP. Had facility manager replace Gallagher power supply with new power supply from site stock, as power supply was not working. All replaced and tested ok. Job complete
MSA-DCS | WA3253487 | Hot water boiler Unit 9 SITE COST leaking badly and currently flooding. | Hakea Prison-Unit 9 64 Cell Prison Living | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 27 Apr 2020 | 2020-04-27 21:34:02 | 2020-04-28 21:45:00 | Fail | Jack hammerd and located leak cut and jack hammerd out side dig down to main ran new main up and into boiler room replacing old Main in ground tested and back filled
MSA-DCS | WA3253495 | Pelco or Honeywell monitors for CCTV is not working - | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Apr 2020 | 2020-04-28 17:51:37 | 2020-04-28 09:00:00 | Pass | Swap the monitor 16 with 10 which is used with static camera only, job completed.
MSA-DCA | WA3254413 | Level 4, Central Pant room - steam plan 2, pipe leaking water | Art Gallery of WA - James St-Main Building (Block B)-Level 5 - Roof | GMP-BR | Plumbing & Drainage | Materials (PD) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-29 10:30:00 | Pass | Received job, attended site.Investigated reports by contractor of water pooling on dosing containers and floor. Floor and containers dry during inspection. Steam Boiler 2 in lead. Found leak only happening when Steam Boiler 2 nearing end of ON cycle and pressure is at its highest. Was unable to seal the coupler. Arranged for replacement fitting.Isolated Steam Boiler 2 and closed isolation valves either side of leaking coupling. Pressure in line would not drop. Found isolation valve on Steam Boiler 2 supply line also passing. This will be raised with Boilertronics during PM. Isolated all steam units and released pressure in lines. Removed leaking coupling. Cleaned surface, applied sealant tape and installed the new coupling. Removed all isolations and returned units to normal operation. Checked for leaks, found none during inspection.
MSA-DCA | WA3254458 | Kitchen- Tap over the duble sink does not swivel anymore | Collection and Research Centre Welshpool-Bulk Wet Store-Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 16:45:00 | Pass | Tightened billi mixer tap
MSA-DCS | WA3253651 | Unit 5, A23 - Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 15:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3253655 | Unit 2, A Wing - External door lock not turning | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 28 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-29 14:00:00 | Pass | inspect unit 2 A wing external door, no fault found.
MSA-DCS | WA3253662 | chlorine plant - not dosing on automatic | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 07:08:40 | 2020-04-28 15:14:00 | Pass | Changed contactor
MSA-DCS | WA3253670 | POD - M-DAS system is reporting Unit 6 Tamper & Unit 5-1 low battery fault | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Apr 2020 | 2020-04-28 11:18:53 | 2020-04-28 15:19:00 | Fail | Unit 6 tamper, secured tamper switch and closed door.MW3 operational Low battery alarm cleared 09:30-11:00
MSA-DCS | WA3253681 | Staff Tea room - Bain Marie not working. No power from unit | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 28 Apr 2020 | 2020-04-28 11:29:49 | 2020-04-28 13:04:00 | Fail | 28/04/20 - Called as requested to the Bain Marie not working. All working ok. Cold unit fault, not the above.Refrigeration tech required. Unit faulty Roban ERX24. 7670.
MSA-DCS | WA3253704 | Monitor room - camera 32 showing blue screen | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 07:38:58 | 2020-05-01 08:51:00 | Fail | Checked with site after reprogramming,Site advised camera is fully operational and recording is good
MSA-DCS | WA3253777 | Unit 4 - staff toilet cistern not filling with water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 09:00:00 | Pass | Remove cistern Inlet valve, clean out strainer, reinstall and test
MSA-DCS | WA3253779 | Unit 6, A7 - toilet leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 10:00:00 | Pass | Remove and replace badly worn outlet rubber in cistern in plumbing duct
MSA-DCS | WA3253785 | Reception, office - Fluorescent light is blinking and may need replacing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-29 13:00:00 | Pass | Repaired faulty lights in reception corridors and offices
MSA-DCS | WA3253799 | Unit 6, Cell D7 - bed and ceiling light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 13:00:00 | Pass | Repaired faulty cell light in d7 unit 6
MSA-DCS | WA3253813 | SHU (9), west wing - the Obs light of Cell A1 not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 09:00:00 | Pass | Repaired faulty lights in SHU A1. Waited access for cell
MSA-DCS | WA3253829 | staff carpark lights faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-19 14:00:00 | Fail | Repaired / replaced faulty carpark lights
MSA-DCS | WA3253844 | Unit 1, C wing, Cell C07 - lockup needs attention. Is sticking on multiple Officers keys | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-08-12 12:00:00 | Fail | Remove edge capping, service main lock, reinstall lock and edge capping. Requires parts.Replace hinges, remove edge capping, install new lock and re install edge capping.
MSA-DCS | WA3253849 | Unit 4, D3 * Prisoner key stuck in personal lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 11:15:00 | Pass | job completed - remove jammed key, repair barrel and replace lock.
MSA-DCS | WA3253850 | Monitor 6 in CCU control room intermittently fades in and out of focus. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 15:09:00 | Pass | Replaced monitor for new in CCU,tested operational (changed bracket to suit)
MSA-DCS | WA3253853 | Unit 3, A6 - window needs fixing as metal broken | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 10:30:00 | Pass | SPIRAL BALANCES RENEWED
MSA-DCS | WA3253854 | Unit 4, Lunch Room- Power socket behind microwave is falling apart | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-28 15:00:00 | Pass | Replaced damaged mounting block
MSA-DCS | WA3253857 | Unit 1 - Cell B1, electricity in cell continuously shorts out | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 14:00:00 | Pass | Replaced damaged gpos
MSA-DCS | WA3253872 | Unit 7, Cells E19, E20, E21 - no power to sockets | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 08:21:48 | 2020-04-28 12:00:00 | Pass | Reset power
MSA-DCS | WA3253879 | Unit 7, G Wing Shower- Shower block drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 08:28:24 | 2020-04-28 10:30:00 | Pass | Blocked showers hair soap removed
MSA-DCS | WA3253894 | Unit 1, Cell C11- Broken toilet seat | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 08:35:06 | 2020-04-28 13:00:00 | Pass | Renew toilet seat wait fir escort to access wing
MSA-DCS | WA3253897 | Unit 6, B&D day room - hot water tap leaking. Have been turning it off at night from the main valve | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-04 10:00:00 | Pass | Replace faulty jumper valve on hot water spindle in day room
MSA-DCS | WA3253903 | Unit 3, C12 - toilet unable to flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 11:00:00 | Pass | Replace outlet rubber in cistern
MSA-DCS | WA3253904 | Unit 2, Cell C11- Broken toilet seat | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 08:39:51 | 2020-04-28 14:10:00 | Pass | Renew toilet seat
MSA-DCS | WA3253906 | Unit 2, Day room - flooring in both day rooms has places were surface has lift | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-06-30 11:30:00 | Fail | DAMAGED VINYL REMOVED & REPLACED
MSA-DCS | WA3253918 | Main Kitchen - hot water urn not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-04 10:30:00 | Pass | Replaced element and solenoid
MSA-DCS | WA3253922 | Unit 1, A5 - powerpoint needs replacing, smoking and sparking | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 08:55:11 | 2020-04-28 15:00:00 | Pass | Replaced GPO in Unit 1, A5
MSA-DCS | WA3253929 | Unit 3 A Wing Cell Ventilation Stopped working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 08:58:34 | 2020-04-28 12:30:00 | Pass | Arrived on site and signed in tools, checked over exhaust fan found belt broken,isolated unit,found spare belts on site,replaced belts and adjusted tension,turned on and tested all running ok at present.
MSA-DCS | WA3253936 | kitchen Blast Chiller 3 Stopped working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 09:07:41 | 2020-05-15 10:42:00 | Fail | Arrived on site and signed in tools, replaced digital display and timer on blast chiller,turn on and tested all running ok at present.
MSA-DCS | WA3253941 | Unit 1, Cell A3-Blocked sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 15:10:00 | Pass | Clear blockage to basin and shower
MSA-DCS | WA3253947 | Unit 1 D9 CCTV Camera Cracked | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 09:11:19 | 2020-08-13 10:30:00 | Fail | Wait for prisoner to be moved to another cell. Removed and replaced damaged face plate of the camera housing. Parts from PFM stores
MSA-DCS | WA3253949 | Unit 2, Cell A10- Blocked sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 16:11:00 | Pass | Clear blockage to basin and shower
MSA-DCS | WA3253950 | Amenities - Male Changeroom - taps in showers are dripping badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-05 13:30:00 | Pass | Remove and replace 1/4 turn spindle in the showers
MSA-DCS | WA3253964 | Unit 2 B15 Light switch Faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 09:16:34 | 2020-04-28 14:00:00 | Pass | Replaced light switch
MSA-DCS | WA3253968 | Front gate - Sally Port doors are not operating correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | AFD Contracting | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-14 13:30:00 | Fail | 30/04/20checked pins for resistancesdiscuss with Tony Vavier that current motor was all that was available at the time of failure of old motor.Adjusted limits for now for interlock.New supplier has a new type of motor.BRAF to be submitted.14/05/20Replace with new type of actuator
MSA-DCS | WA3253971 | Kitchen- Floor under centre bench- Floor surface is uneven | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-08-11 13:36:00 | Fail | EPOXY HOLES IN KITCHEN
MSA-DCS | WA3253982 | Unit 4, B wing B12 - unable to be locked | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 09:26:32 | 2020-04-29 10:15:00 | Fail | welded on strike plate
MSA-DCS | WA3253984 | Gate House - Front Entrance-nside handle of the Airlock staff side (Door 3) is slightly loose | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-30 09:00:00 | Pass | HANDLE RE FIXED
MSA-DCS | WA3253989 | Gatehouse- Intercom from door one to pod ext 5383 not audible, needs to be louder | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-13 12:30:00 | Fail | Sourcing parts.( Sentry intercom mod.LP8 - supplied by SEME).Attended site.Dismantled old intercom located near door one ( entrance door - high pedestrian traffic).Done modification on door frame and wiring.Done modification on new intercom plate ( new intercom is different from old one).Programmed and tested new unit.All ok at departure
MSA-DCS | WA3253993 | Unit 1, Cell B11- Reading light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 11:30:00 | Pass | Repaired faulty lights in unit 1 cell b11
MSA-DCS | WA3254019 | Unit 2, A-B & C-D day Rooms- Water fountain taps wont turn off | Melaleuca Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 15:35:00 | Pass | Faucets on both fountains in unit 2, both sides are leaking. Returned to car for replacement faucets and isolation. Isolations extremely difficult to get to on both units, had to remove fountains, drain and stainless steel panels to get to isolation. Replaced faucets and checked under pressure A402011704 Unit A & B and A40402890G Unit C & D
MSA-DCS | WA3254129 | Unit 4, Cell K42 - blocked toilet | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-28 14:15:00 | Pass | COMPLETED
MSA-DCS | WA3254221 | Section 95 office - GPO is broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 10:30:00 | Pass | Investigate and replace broken gpo in section 95
MSA-DCS | WA3254241 | Unit 4 Dayroom south, GPO tripping RCD | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 13:00:00 | Pass | Investigate tripping rcd in unit 4 day room south. Found cause was bad connection on element of boiling water unit
MSA-DCS | WA3254242 | unit 9, Boiler house - door not opening | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 11:18:07 | 2020-04-28 14:45:00 | Pass | replaced lock as required.
MSA-DCS | WA3254266 | Unit 6, Cell C9- Main cell light is flickering when turned on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 13:00:00 | Pass | Repaired faulty lights in unit 6 c9
MSA-DCS | WA3254269 | Cabinet Shop- No power to rollerdoor | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-28 15:00:00 | Pass | Investigated no power to roller door. Found and reset overload contact in cabinet shop switch board.
MSA-DCS | WA3254280 | U7, E18 - Broken power point wires exposed, light switch damaged | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 11:38:31 | 2020-04-28 13:00:00 | Pass | Replaced broken light switch and gpo
MSA-DCS | WA3254290 | front gate, sally port - Replace Blown Lights | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 18:00:00 | Pass | Replaced all blown lamps in Sally port
MSA-DCS | WA3254291 | Door entering passageway to dining room east- MKH barrel is faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-29 13:00:00 | Pass | replaced lock
MSA-DCS | WA3254423 | kitchen dough machine faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 16:00:00 | Pass | Kitchen Dough machine faulty. Check machine & controls. Dismantle, check drive belts, wiring & contactors. No fault found. Assemble & test run. Report to staff.
MSA-DCS | WA3254424 | kitchen potato peeler no power | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-06 09:30:00 | Fail | Potato Peeler no power. Remove for repairs, dismantle, found loose connection on circuit board. Resolder joint. Assemble & test. Return to kitchen.
MSA-DCS | WA3254426 | kitchen 2A robo coupe mixer faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 16:30:00 | Pass | Robo Stick Mixer faulty. Check mixer, remove for repair. Dismantle, replace bearing bush, blade assembly, tag. Assemble & test. Return to site.
MSA-DCS | WA3254446 | Reception - large crack in vinyl floor | Wooroloo Prison Farm | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-06-22 14:18:00 | Fail | repaired joint - supplied and installed vinyl expansion cover strip
MSA-DCS | WA3254484 | Unit 5, B & D Dayroom- Frame & winder broken on window | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 12:30:00 | Pass | RENEWED CHAIN WINDER
MSA-DCS | WA3254498 | SHU (9), front entrance - check lock on door 22 as faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-20 10:00:00 | Fail | On site check original key in lock. Security to order new keys
MSA-DCS | WA3254507 | Unit 3, Cell C12- toilet will not flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-07 09:00:00 | Fail | Push button is too short. Extend push button and test.
MSA-DCS | WA3254514 | Investigate leaking water system - further notes below | Riverbank | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 09:01:00 | Pass | nil
MSA-DCS | WA3254540 | Unit 4, I wing - no hot water | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-28 15:00:00 | Pass | COMPLETED
MSA-DCS | WA3254558 | Lenard A1 Smashed light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 11:00:00 | Pass | Replaced light switch with a new one, test ran ok.
MSA-DCS | WA3254561 | ISU, B wing console - intercom phone faulty (button) | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 12:16:00 | Pass | Replaced faulty Cell guard CI-OH hanset with new, job completed.
MSA-DCS | WA3254565 | Karakin, B02 - smashed light switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 10:00:00 | Pass | Replaced light switch with new one, test ran ok.
MSA-DCS | WA3254566 | CCU, Holding cells common area - repair holes in vinyl flooring | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-20 16:15:00 | Fail | vinyl flooring installed
MSA-DCS | WA3254590 | Conference room, flashing/faulty Fluro light | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 14:12:18 | 2020-04-28 16:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3254609 | Lock to the entry door of Skills House is stiff making it difficult to open. | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 12:30:00 | Pass | Lock on Entry door to Skills difficult to open Lock adjusted and serviced
MSA-DCS | WA3254633 | Unit 2 house 2 –UPS failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-05 12:00:00 | Pass | replaced ups with site spare, re routed cabling & tested operation. all is in working order. update firmware for nic card
MSA-DCS | WA3254636 | Unit 2 house 2- no cell call | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-05 10:00:00 | Pass | replaced faulty cell guard psu in unit 2 house 2. re terminated all cabling & re routed. tested intercom in cells & control confirmed all in working order.
MSA-DCS | WA3254711 | Oval various areas Repair Retic Solenoid’s | Melaleuca Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-29 13:00:00 | Pass | reset and retest system and adjusted accordingly
MSA-DCS | WA3254717 | Unit 3, D Wing Dayroom- hole in ceiling where water has come through | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 15:08:44 | 2020-05-21 09:45:00 | Fail | CEILING REPAIRED & PAINTED
MSA-DCS | WA3254720 | unit 2 D3 GPO in cell smashed | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 15:13:56 | 2020-04-29 09:00:00 | Pass | Replaced smashed gpo
MSA-DCS | WA3254727 | Unit 4, Office- Vesda alarm keeps going off even though no fire | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 15:19:29 | 2020-04-29 11:00:00 | Pass | Complete
MSA-DCS | WA3254729 | Unit 1, Office- Vesda alarm keeps going off even though no fire | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 15:20:50 | 2020-04-29 12:00:00 | Pass | Complete
MSA-DCS | WA3254735 | Unit 5, Cells A12, A13, A14- GPO's have been wet and tripping power to cells | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 15:23:38 | 2020-04-29 10:00:00 | Pass | Reset power and tested
MSA-DCS | WA3254871 | ISU A wing camera is not working | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 18:06:47 | 2020-04-29 10:00:00 | Pass | Fixed faulty recorder A wing cameras ISU, job completed.
MSA-DCS | WA3254883 | Unit -4 D 8 Doors locked-SOme one locked | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 28 Apr 2020 | 2020-04-28 22:00:48 | 2020-04-28 19:45:00 | Pass | Job completed - Attend site after hours, open jammed lock and replace latch.
MSA-DFES | WA3253912 | PPC room - door has come off the runner | CFRS Rockingham | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 17:00:00 | 2020-08-07 11:30:00 | Fail | New door roller tracks installed
MSA-DTAG | WA3253910 | Ground floor Internal custody security cameras are not working | Midland Courthouse | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-28 13:00:00 | Pass | Checked PC in Custody and found PSU faulty. Took system offsite and repaced 1x 550W PSU. Returned to site, reinstalled PC. Tested operation and all OK.
MSA-DTAG | WA3253983 | Ground Rear Courtyard please remove grafitti on building | Perth Children's Court | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-05 17:30:00 | Fail | Remove Graffiti
MSA-DTAG | WA3254121 | Level 4 Community Corrections (Hay Street End) blown light globe | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-29 12:30:00 | Pass | Job complete
MSA-DTAG | WA3254149 | Level 2, law library - The law library are unable to open the doors with their proxy cards or | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 17:00:00 | 2020-05-08 16:00:00 | Fail | Multiple issues with CCTV, Intercom and Access Control due to Pacom Server Master Crash, Eski Host and VirtualServers failing. Issues apparent on 2 x San Units also.
MSA-DTAG | WA3254331 | ground security front desk camera monitor provides fuzzy image-see notes | Perth Children's Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 12:30:00 | Pass | Found monitor on ground floor ok at time of testing, security advised what fault normally is, advised would be monitor fault. Have taken notes of model number, would suggest to install better monitor instead of 12v dc. Suggest upgrade of monitor. Client advised they where upgrading entire system in coming weeks.
MSA-DTAG | WA3254391 | Ground level, security office - light has fallen from ceiling in the security office | Armadale Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-01 08:15:00 | Pass | Job complete
MSA-DTWD | WA3253975 | Evap aircons not working on auto but will work when turned to manual | Kwinana Automotive Centre | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-08 11:51:00 | Fail | Arrived on site signed in, checked Auto on workshop floor all ok started no issues. Checked operation on all classrooms all fault is user not sure on operation, they turn unit on. Then put unit into auto without turning up fan speed all control's had fan off. Once fan speed turned up auto system works correctly. Cleaned up and completed paperwork and signed out.Icon Logic completed reboot on control system and completed works.
MSA-DTWD | WA3254003 | Main entry doors- jammed opened | Armadale Campus - 40 Commerce Ave | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-28 11:30:00 | Pass | Found rubek r7000 motor lock jammed on with the door only 100mm apart. Carried out temporary repair to get door working. Locking began working after repeated testing. Door is locked over night via the manual lock in the door. The motor lock is used for emergency locking. Requires new r7000 locking motor. Braf raisedJob completed and claim submitted, as Braf has not been approved
MSA-DTWD | WA3254211 | A Block, Room AF18- backflow valve leaking | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | Water (PD) | Techworks Plumbing | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-01 12:37:00 | Pass | Faulty backflow valve, replaced and all tested OK.
MSA-DTWD | WA3254219 | Level 1, Main room - Faulty Detectors in building | Perth Campus B7 | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-18 13:24:00 | Fail | 30/04/2020, 1030-1115Staff and job notes unclear about what issue is. Guards report issues with arming system.Managed to connect with software and upload, can see a few alarms on zone 22. Replaced device battery and tested arming with guard code all ok
MSA-DTWD | WA3254275 | E Block, E58 Large Scale Kitchen – Leaking Mixer | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-01 10:00:00 | Pass | Replaced leaking basin mixer
MSA-DTWD | WA3254306 | T block L1 T105-key broken off in the lock | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 28 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-28 14:45:00 | Pass | replaced lock
MSA-DTWD | WA3254471 | East block toilets - replace/fix broken belts on exhaust fan | Perth Campus B6 | GMP-BR | Building | Materials (BU) | Equans Mechanical Services Australia | 3 | CLOSE | 28 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 16:10:00 | Pass | New beltd collected from supplier and brought to site. Signed in and collected keys. Gained access to roof plant to area and used dedicated internal walkways to access East toilet EAF system. Isolated and locked out. Replaced belts tensioned and carried out alignment check. Tested operation and confirmed airflow. Isolated and refit covers. Fan returned to auto operation. Old belts removed from roof top. Works area left tidy.
MSA-DTWD | WA3254739 | block 3 ground 3F1 Test cell and 3F5 Test cell doors.-locks not working | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 28 Apr 2020 | 2020-04-29 17:00:00 | 2020-04-29 11:30:00 | Pass | Test cell doors 3F1 & 3F5 need services.
MSA-MRWA | WA3254538 | Level 5, Lift floor - lift not operational | Don Aitken Centre MRWA Head Office | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 28 Apr 2020 | 2020-04-28 17:50:06 | 2020-04-28 16:15:00 | Pass | Lift1 DAC-Geared :Reset rope brake after self testing.
MSA-DCA | WA3255460 | Main FIP, detector intermittently going into fault and setting off alarm | State Theatre Centre (Heath Ledger Theatre)-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-04-29 12:00:00 | Pass | Attend site and rectify main fip detector intermittently going into fault
MSA-DCA | WA3256293 | potable water pump 2 is leaking | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 1-Mechanical Plant Room | GMP-BR | Electrical | General Electrical (EL) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 16:30:00 | Pass | Replaced pressure relief valve on expansion tank
MSA-DCS | WA3255151 | Unit 3, A&C - issues with hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-29 11:00:00 | Pass | Investigate all hot water systems throughout the unit. Problem is due to a boiler house fail not within the unit.
MSA-DCS | WA3255157 | Unit 2, D wing shower - tap on the wall requires a split pin to turn water on & off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 12:00:00 | Pass | Replace missing split pin in shower spindle
MSA-DCS | WA3255161 | Kitchen, fridge not cooling, 3 door fridge. | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 07:19:12 | 2020-04-29 14:00:00 | Pass | checked fridge found faulty GPO and dirty condenser.Chemical clean and move supply to another GPO
MSA-DCS | WA3255203 | Control - Perimeter zone – zone TTXc02 nwc01 mbco2 mwc03 continuously alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 07:42:48 | 2020-04-29 14:00:00 | Pass | 29/04/2020 checked control room Equipment and proceeded to Outer Perimeter MW C01. C01 Tested ok at receiver. Checked MW C02 & C03, both Microwave Units has no 12v Supply. Located blown fuse in EC cabinet. Obtained replacement fuse and installed. Tested all microwaves to tech at Gate Control and confirmed operating correctly. Tested PTX zone C02 by walk test so tech in Gatehouse could plot a trace. Made multiple walk tests to allow plot adjustments to be made. Left operating correctly. Attended microwave on zone G01, found that one of two alarms contacts in microwave not changing state, in Perm Alarm. Swapped alarm cables to second contact. Zone functioning correctly.
MSA-DCS | WA3255211 | unit 1, plant room - top loading lights faulty in roof space | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 15:30:00 | Pass | Repaired faulty lights in unit 1 plant room
MSA-DCS | WA3255255 | Unit 2, Cell A7- Blocked toilet sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 08:16:45 | 2020-04-29 10:05:00 | Pass | Cleared blocked shower,toilet and basin to Unit 2 cell A7.Used drain cleaner to clean the shower and basin waste pipes.
MSA-DCS | WA3255256 | Construction shed - broken glass window | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-27 15:00:00 | Fail | REPLACED BROKEN WINDOW - AWNINGREPAIR/RESET DAMAGED FRAME
MSA-DCS | WA3255304 | Unit 1, fire alarm panel - faults | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 08:36:40 | 2020-04-29 15:30:00 | Pass | Attended site found the following faults on the system.Unit 11 - low airflow on vesda wing a&b 11/12Fault caused by blocked sampling point cleaned sampling point and grill and fault cleared, left normal.Unit 12 - fault on vesda wing c&d cells 11/12, logged in with vesda programmer and found fault due to blocked valve on pipe 1, cleared outvalve and fault cleared, left normal.Reception RH holding cell vesda fault caused by corrupt log, removed logs and fault cleared. Left normal.
MSA-DCS | WA3255338 | Gatehouse - MPC Cell 1 & 2 Cell call is not alarming to the main panel | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Apr 2020 | 2020-04-29 12:53:21 | 2020-06-11 20:11:00 | Fail | Completed under WA3083134
MSA-DCS | WA3255340 | Multiple alarms on main duress system | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Apr 2020 | 2020-04-29 12:54:06 | 2020-05-07 12:30:00 | Fail | Replaced receiver in wet riser unit 3 for new along with internal enclosure sealed and tested ok.
MSA-DCS | WA3255369 | Unit 6, Cell A18- Toilet does not flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-05 13:25:00 | Pass | Removed old cistern replaced with new
MSA-DCS | WA3255370 | Education room 9 - courtyard door lock facing court yard faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 11:30:00 | Pass | job completed - On site replace barrels and lubricate lock
MSA-DCS | WA3255380 | Education, student kitchen - lights faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-29 15:00:00 | Pass | Repaired faulty lights in education kitchen. Waited for access
MSA-DCS | WA3255381 | Unit 6, Cell B6- Sink is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-05 14:18:00 | Pass | Checked over sink no leaks outlet and cold tap leaking
MSA-DCS | WA3255386 | Unit 6, A Wing- 1st cubicle drain is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-04-30 17:00:00 | Pass | Unblocked shower drain large clump off hair blocking it
MSA-DCS | WA3255406 | Security MPC, cell 2 - toilet not flushing & water dispenser faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-04 09:30:00 | Pass | Completed incorrect start time started 8:30am
MSA-DCS | WA3255408 | front gate key control Door Closer Broken | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 09:22:06 | 2020-06-15 14:30:00 | Fail | Replaced door closer to outer gate - keywatcher
MSA-DCS | WA3255421 | Unit U6 cell C10 Tongue jammed unable to lock | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 09:26:50 | 2020-04-29 12:00:00 | Pass | replaced faulty mortice lock
MSA-DCS | WA3255448 | Unit 6, A & C- Sink is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-06 09:00:00 | Pass | Tighten kitchen sink waste pipe to stop leak
MSA-DCS | WA3255464 | Unit 10, control room - door jamming/sticking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 09:24:22 | 2020-04-30 11:30:00 | Fail | supplied and installed door closer and limit stop
MSA-DCS | WA3255471 | Stores Building outside the Prison, Prison Industries building- Split air con not working, has power | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 09:42:58 | 2020-04-29 13:32:00 | Pass | Checked found the condenser fan motor wire is stuck in the fan blade, fixed the wire proper and started the unit.
MSA-DCS | WA3255513 | Unit 4A, Cell 34- Window runners damaged | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 10:09:33 | 2020-05-04 10:45:00 | Fail | WINDOW RUNNERS REPAIRED/RESET
MSA-DCS | WA3255541 | Jasper, C Wing- Damaged hallway gyprock ceiling | Banksia Hill Detention Centre | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-08-07 12:50:00 | Fail | CEILING REPAIRED (TWICE) AND PAINTED- SEE WORK LOG NOTES
MSA-DCS | WA3255553 | Admin, female toilet - lighting not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-01 10:00:00 | Pass | Replaced faulty light in Admin female toilet
MSA-DCS | WA3255579 | Unit 10, Cell A3- Sink broken away from wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 10:52:11 | 2020-04-30 14:30:00 | Fail | Attend site could not get escort till 12pm to start job
MSA-DCS | WA3255581 | Boiler House - Plant-Room boiler no1 SITE COST leaking/boiler no2 not igniting | Casuarina Prison | WSM-BR-SITE | Mechanical Services | Boilers (MS) | Boilertronics | 0 | CLOSE | 29 Apr 2020 | 2020-04-29 14:55:04 | 2020-04-29 15:00:00 | Fail | Went to site signed in and got my tools checked. Went to plant room. Checked boiler for leeks. It looked OK water looked to be coming from smoke box at back of boiler when they were running it up from cold. I recommend putting a 1/2 drain on the smoke box to the drain next to the boiler. Would need 1/2 male flare 1/2 copper and a few 1/2 clips and pipe benders and a few 1/2 elbows.
MSA-DCS | WA3255592 | Boiler House - Plant-Room boiler faulty/no hot water | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-04-30 10:30:00 | Pass | Signed in as required.Removed both the flow switches on units 1&4. On fitting them tested ok and adjusted set point on unit 1 from 70 to 80the same as other units.
MSA-DCS | WA3255596 | Unit 5 - D Wing cell D12 bottom bunk reading light not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-01 08:30:00 | Pass | Repaired faulty lights in unit 5 d12
MSA-DCS | WA3255603 | Gate house - lock on door 4 going to east Crip is damaged and preventing the door from closing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 29 Apr 2020 | 2020-04-29 15:06:04 | 2020-04-29 17:00:00 | Fail | job completed - Install repaired lock, replace hinges and relocate strike to align with lock.
MSA-DCS | WA3255610 | Unit 1 - A5 aerial socket faulty | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-01 14:30:00 | Pass | Job completed - Attended site. Checked Unit 1 A5 TV Point, found already been replaced by Site Maintenance. Tested TV Point signal, all OK.
MSA-DCS | WA3255655 | Unit 13, Cell A7- Bed light is faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-06 15:00:00 | Pass | Replaced damaged cell switch in unit 2
MSA-DCS | WA3256386 | Unit 14, A Wing, Cell A6- Drain Blocked in shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-01 12:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test
MSA-DCS | WA3256421 | kitchen bakers oven not working properly | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 12:36:44 | 2020-06-04 10:29:00 | Fail | Sourced prices for a new damper motor. Original supplier no longer supplies them.found another supplier who can supply them.Contacted site to see if they are still having issues, which they are not.Motor not ordered. Mark as complete.
MSA-DCS | WA3256427 | kitchen prover not heating | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 12:39:08 | 2020-04-29 17:00:00 | Pass | Kitchen prover oven not heating. Check oven & controls. Reset time clock and set to auto. Repair water inlet valve & float. Run cycle, adjust water level. Report to staff.
MSA-DCS | WA3256440 | front gate - fault transponder 06, SCEF,G,H is in alarm(duress system) | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Apr 2020 | 2020-04-29 20:43:19 | 2020-04-30 15:05:00 | Fail | Complete as per work notes.
MSA-DCS | WA3256450 | recreation change timers in basket and squash courts faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 09:30:00 | Pass | Reprogrammed timers
MSA-DCS | WA3256456 | Unit 5, A16 - light in cell broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 09:00:00 | Pass | Repaired light
MSA-DCS | WA3257011 | Unit 6 - D7 lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-01 10:00:00 | Pass | Repaired faulty lights in d7 u6
MSA-DCS | WA3257012 | health centre, consulting room 8 - cannot lock door (AC Lock) | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-01 16:00:00 | Pass | Serviced lock, tightened handles and replaced cylinder
MSA-DCS | WA3257020 | Unit 3, A & C - Hot water is now workin in units but there is no cold water coming out of showers & | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-29 15:00:00 | Pass | Inspect cold water service, locate a cold water valve which has been turned off by an inmate. Turn back on
MSA-DCS | WA3257025 | Unit 10, B10 - Concrete deteriorating around toilet | Hakea Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-01 12:00:00 | Pass | TOILET IS LOOSE - REQUIRES PLUMBER
MSA-DCS | WA3257034 | PDS workstation monitors keep dropping in & out | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-05 14:00:00 | Pass | checked extenders & found faulty cat 5 cable, broken cores on cable. reterminated & tested. operation all mok. job complete
MSA-DCS | WA3257037 | Unit 9, Cell A1- Cannot turn off stop tap in duct | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-05 15:15:00 | Pass | Changed out tap washers
MSA-DCS | WA3257114 | JJT Office Room - Ceiling light is flickering | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 15:30:00 | Pass | Replaced lamps and control gear as required.
MSA-DCS | WA3257135 | Cameras are not tracking to fence alarms | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Apr 2020 | 2020-04-29 19:48:25 | 2020-04-29 17:45:00 | Pass | Rectified and fixed the alarms from indigo, job completed.
MSA-DCS | WA3257166 | L3 zone 3 lights keep turning off after a period of time | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 16:22:44 | 2020-04-30 09:30:00 | Pass | Investigate lights - require Lynx to attend to reprogram touch screens
MSA-DCS | WA3257189 | Boiler House - Plant-Room-BMS Converter faulty/needs cabling replaced. | Casuarina Prison | GMP-BR- HO | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Datatel Communications | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-21 12:00:00 | Fail | Fibre tested, working and repoort supplied to Andre
MSA-DFES | WA3255253 | Between room 17-18 - water leaking through wall causing rising damp | CFRS Ellen Brook | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-06-25 14:48:00 | Fail | As per BRAF
MSA-DFES | WA3255453 | Lower dam, pump 1 - issue – Insight to liaise with Zambezi to rectify fault | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-08 11:35:00 | Fail | Signed in onsite at 1415Have communicated with Dominic the control technician about works that need to be completed and has understood was Jamie From DFES would like done. The issue is that the VSD is blown and a replacement control system is in the works. All parties have been notified and will contact to provide a solution. Left site at 1515
MSA-DFES | WA3255565 | External rear of building sink that supplies the washing machine, tap is running | Butler Career Fire Station | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 16:00:00 | Pass | Repaired leaking tap.
MSA-DTAG | WA3255487 | ground ladies staff toilet-First cubicle flush buttons only the half button works every now and then | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-06-03 09:37:00 | Fail | Complete
MSA-DTAG | WA3255563 | Court room 2 - The court is freezing cold despite changing the tempartures manually. | Joondalup Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-11 11:30:00 | Fail | Attended site and reprogrammed with controls technician.
MSA-DTAG | WA3255566 | ground male public toilet Flushing Button missing for urinal | Mandurah Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-01 10:35:00 | Pass | Investigated missing urinal button to find it had been snapped off and stolen. Sourced new parts from supplier and installed and made sure in good working order
MSA-DTAG | WA3255693 | Ground floor, back door - Door will only open a little, think hinges are jammed | Perth Children's Court | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-05 13:00:00 | Fail | NEW DOOR CLOSER/ DOOR STOP INSTALLED
MSA-DTAG | WA3256464 | L1 Upper custody toilet hot and cold water taps dripping constantly | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 13:45:00 | Pass | COMPLETED
MSA-DTAG | WA3257101 | Custody cell 3-Person in custody displayed flu like symptoms -see notes | Supreme Court | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 17:40:00 | Pass | Job done as per Work Order.
MSA-DTWD | WA3255240 | A Block, Lvl 3- Lab Operations- replace light tubes | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-04 11:04:00 | Pass | Repalced multiple fluros out throughout labs level 3 A block .
MSA-DTWD | WA3255266 | Level 1, Exterior - Soak well partly collapsed on Richmond St side of A Block North Single Section | Leederville Campus | GMP-BR | Building | External Walls (BU) | AWB Co. | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-06 09:00:00 | Pass | Attend site and call site contact. Get shown area of suspected collapsed soak well. Dug up area to around 800-1000mm deep and was unable to come across anything other than the dirt being very soft and in compacted. Used prodder to try find anything deeper then the meter I had dug to but was unable to feel anything in the area. Backfill the hole and went to Bunnings to get some yellow sand to top up the hole, put back garden edging.
MSA-DTWD | WA3255356 | canteen Gas HWS pilot light is low and just burning. May be blocked or needs adjusting. | Rockingham Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 15:36:00 | Pass | Multiple issues with hws fixed
MSA-DTWD | WA3255469 | Western entry door A Block - Door lock not operating properly, bolt jamming open. | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 11:35:00 | Pass | Job completed - replaced latch
MSA-DTWD | WA3255537 | Western end J Block- Broken window pane | Rockingham Campus | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 09:30:00 | Pass | REGLAZED BROKEN GLASS PANEL 6.38 CLEAR LAMINATED SAFETY GLASS 1 - 463 X 8942.4 L/M OF RUBBER REPLACED
MSA-DTWD | WA3255559 | Grounds, Main student front car park- Dead tree has fallen over | Bentley Campus | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 12:15:00 | Pass | Tree removed. Mulching carried out. Dead branches in tree removed.Onsite 7.45 am 30042020. Departed 9am 30042020. Labour 3 staff x $125 = $375. Material Chipper truck and wood chipper $125. Total this session $500.Onsite 11.30 am 30042020. Departed 12.15pm 30042020. Labour 5 staff @ $75 = $375. Material Chipper truck and wood chipper plus cherry picker $150. Total this session $525.Budget $1,000. Actuals $1,025. Claim $1,000 plus GST
MSA-DTWD | WA3255561 | B Block, Room B2417- Light fitting is faulty | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 29 Apr 2020 | 2020-05-06 17:00:00 | 2020-05-05 14:49:00 | Pass | Repalced faulty lampholder and Fluro to light in B block. Tag and tested coffee machine as well. Removed faulty gpo in LSK .job completed
MSA-DTWD | WA3255618 | block 4 & 5 , ground & first floor - plant rooms - A/c’s not working in first floor plantrooms | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 15:00:00 | Pass | Bms issue and icon logic already attending site tomorrow. They will check
MSA-DTWD | WA3255669 | BLD 839 and BLD 832, level 1, Board room - Various lights faulty | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 12:00:00 | Pass | Replaced faulty lights
MSA-DTWD | WA3256895 | A Block, South Entry Door- Door is not operating correctly, possible sensor issue | Leederville Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 29 Apr 2020 | 2020-04-29 17:19:21 | 2020-04-29 14:51:00 | Pass | Replaced faulty internal sensor and tested all ok at time of test.
MSA-DTWD | WA3256983 | T Block- 4 faulty door locks, difficulty when locking with a key, Room numbers listed below | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 11:35:00 | Pass | Repaired lock & cyclinder
MSA-DTWD | WA3257142 | B Block, Room BG15.A- Light fitting not working | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 16:10:00 | Pass | Reinstated lift fitting to Bag15A. Repaired broken conduit to machine B block. Repalced faulty tombstone and tubes to light AG27. Repalced ballasts. And tubes to light ET09. Job completed
MSA-MRWA | WA3255271 | G floor, Unisex toilet- hand basin slow draining please rectify | Heavy Vehicle Services | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-04-30 11:42:00 | Pass | Unblocked basin drain
MSA-MRWA | WA3255332 | Level seven, Office 729 - Exit sign not illuminated | Don Aitken Centre MRWA Head Office | GMP-BR | Signage | General Signage (SI) | MR - Handyperson - PFM | 1 | COMP | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-29 09:23:00 | Pass | Replaced tube with new
MSA-MRWA | WA3256433 | Level 4, female cubicle - L4 Female toilet next to ambulant flush mechanism failed please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 08:33:00 | Pass | Replaced faulty flushing mechanism and outlet washer
MSA-MRWA | WA3257077 | External- Outside lights need fixing- see below for further information | Jandakot Depot | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 29 Apr 2020 | 2020-05-04 17:00:00 | 2020-05-04 15:00:00 | Pass | Attend site and signed in. Replace 8x faulty lamps by the kitchen court yard.
MSA-DCA | WA3257999 | Reverse Osmosis unit in fault | Shipwreck Galleries-Main Building-Ground Floor-Wet Room - Conservation Department | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-04-30 14:30:00 | Pass | Attended site. RO plant system in fault. Applied tests and checks to find issue with pump. Disassembled pump and Inspected impeller and internals. Investigation found pressure tank bladder to have collapsed. Replaced pressure tank and tested operation. Investigation found pump faulty. Job to be closed and separate quotation to be submitted to replace RO pump.
MSA-DCA | WA3259082 | 1st floor, office near boardroom - Temperature is very cold | Collection and Research Centre Welshpool | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-01 08:30:00 | Pass | Attended site. AC system on eastern side of building adjacent to boardroom upstairs in administration building to not be heating. Applied tests and checks to find system wall controller set to 22c cooling ? Adjusted wall controller and checked system operation. System operating correctly.
MSA-DCA | WA3259142 | all levels lift 5 out of service | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-04-30 19:01:00 | Pass | When responding to the callback dated 30.04.2020, the Schindler Technician found a problem with your equipment. Electroniccomponents were faulty. Following our attendance, the equipment was left in service.
MSA-DCS | WA3257855 | Unit 4, Toilet - staff toilet leaking and occasionally flush button sticks | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-01 13:00:00 | Pass | Realign push button assembly in cistern.
MSA-DCS | WA3257859 | Unit 3, C wing shower - to repair 2 shower heads (the first two closest to the door | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-01 11:00:00 | Pass | Clean out calcium build up in shower heads and test
MSA-DCS | WA3257916 | Unit 2, Cell 21 - appears that a substance similar to toothpaste has been pushed into speaker face | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 07:44:00 | Pass | Removed cell callCleaned. Re terminatedReplacedTested ok
MSA-DCS | WA3257933 | unit 1, C7 - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 08:39:28 | 2020-04-30 13:30:00 | Pass | Repaired light
MSA-DCS | WA3257943 | Unit 2, A & B Wing- PA System is not working correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-04-30 12:00:00 | Pass | Scope, improve design, acquire parts, prefabricate, install and test new PA installation in the NE corner of Unit 2. Report defects in the Pole integrity to prison
MSA-DCS | WA3257947 | Unit 3, C6 - Cell window cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 08:44:32 | 2020-04-30 16:30:00 | Pass | WINDOWS RE GLAZED IN C4 & C5
MSA-DCS | WA3257968 | Entry building keywatcher comms fault | Bandyup Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Apr 2020 | 2020-04-30 12:51:25 | 2020-04-30 11:30:00 | Pass | Fixed and clear the alarm from keywatcher, job completed.
MSA-DCS | WA3258007 | Unit 3, D Wing- Cleaning cupboard pipes making noise | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-04 09:00:00 | Pass | Inspect pipework, run all showers, basins. No issue found. No noise heard.
MSA-DCS | WA3258028 | Gatehouse - Can we please have the sensors on the automatic key control door assessed as faulty | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-25 09:00:00 | Fail | Tested operation of Auto door on “Keys” (East) side of Gatehouse. Confirmed correct operation of Exit PIR Detector, Entry Button and safety beam sets. Unable to fault door operation.
MSA-DCS | WA3258055 | Unit 2B, Abultions- 3x fans not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-04 12:00:00 | Pass | Replaced faulty exhaust fans
MSA-DCS | WA3258070 | Fault with the PIR in Unit 2 located next to cell 17 | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-31 12:00:00 | Fail | PIR seems over sensitive and straight into AlarmCable okGoes to DGP 3 SO officeSuggest order new inter logic 1116AM
MSA-DCS | WA3258207 | Bakery - Workshop internal flashing to freezer has been damaged | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-01 09:22:00 | Pass | Arrived on site and signed in tools, straightened flashing and resecured with rivets and sealed with silicone,also adjusted door so closes properly.
MSA-DCS | WA3258273 | Gatehouse computer has fault error " L3S35Z11ST" | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 11:04:06 | 2020-04-30 13:45:00 | Pass | Fault from fire alarm panel, not our scope of work.
MSA-DCS | WA3258277 | kitchen main coolroom Fans are spitting foreign matter ( Dust Like ) over the food | Hakea Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 11:06:45 | 2020-05-01 09:30:00 | Pass | Foreign particles do not originate from operation of cool room. Unit clean.
MSA-DCS | WA3258324 | kitchen Probe Thermometer from 1st Rational Oven broken off | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 11:35:49 | 2020-05-11 15:40:00 | Fail | 11/05/20 - Called as requested to job with a new core temp probe, fitted & tested, all working ok.
MSA-DCS | WA3258395 | Boiler house - reconnect drier to compressor line | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-05 12:30:00 | Pass | Repaired air drier
MSA-DCS | WA3258399 | Gym- Bracket hanging from ceiling. Hanging dangerously | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-13 13:00:00 | Fail | Resecured Cages in gym with the use of a specialist scissor lift .
MSA-DCS | WA3258657 | U10 C12 Door hinge requires retaping | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 15:15:00 | Pass | Rehung door. New hinges supplied and fitted
MSA-DCS | WA3258662 | Unit 6, A Wing, Cell A5- Door is difficult to lock, possible door hinge issue | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-07 10:00:00 | Pass | Replace hinges, door plate and lock. Attend site weld on strike plate.
MSA-DCS | WA3258701 | Unit 8 staff toilet Fitting broken new lamp holder required and new light switch | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 12:31:29 | 2020-05-04 12:00:00 | Fail | Replaced light
MSA-DCS | WA3258752 | Unit 5 - Door lock faulty. Door located between the SO office and staff toilet. will not lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-01 11:00:00 | Pass | Removed paint from lock, service and replace bolt throw
MSA-DCS | WA3258804 | SHU (9) - East Hot water unit (Urn) leaking. East Wing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-06 11:05:00 | Fail | Replace silicon vent tube between drain connection and tank.
MSA-DCS | WA3258915 | Gatehouse computer has fault error " L3S35Z11ST" | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 13:18:56 | 2020-05-01 13:15:00 | Pass | 1/5/20 MBReplaced faulty smoke detector in block 2B room 20 (L3 S35).Reset and left system in normal working order.
MSA-DCS | WA3258927 | Unit 5, Cell B12- Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 12:30:00 | Pass | Repaired light
MSA-DCS | WA3258938 | Unit 3, Cell B15- Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 10:00:00 | Pass | Repaired light
MSA-DCS | WA3258958 | Unit 5 A23 Light hanging from ceiling | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 13:42:22 | 2020-04-30 16:00:00 | Pass | Repaired light
MSA-DCS | WA3258975 | Unit 2 Wing A Camera 204 is unavailable due to the server | Melaleuca Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Apr 2020 | 2020-04-30 17:49:09 | 2020-04-30 17:00:00 | Pass | Camera back online. Fixed the forced open alarm from crisis care door as per client request. Job completed
MSA-DCS | WA3258987 | Cameras 241 through to 285 are not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 13:58:06 | 2020-05-07 17:01:00 | Fail | Investigated camera faults, traced to maxpro subrack and trunk lines. Repaired faults with subrack located in unit 5 and communication equipment. Tested OK. Job Complete
MSA-DCS | WA3259000 | MPU (8)- P Trap broken under sink in laundry room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-04 11:00:00 | Pass | Replace broken 50mm P trap in laundry. (Supplied by prison)
MSA-DCS | WA3259004 | SOP, Shower Block- Extreme water preasure when all shower taps turned on. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-04 12:00:00 | Pass | Clean out calcium buildup in shower heads and test
MSA-DCS | WA3259005 | Eastern Oval - 2 x Solenoid Boxes Damaged and full of water | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Pumps n Pipes | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-05 14:00:00 | Pass | REPLACED 2 BROKEN SOLENOID BOXS
MSA-DCS | WA3259008 | Unit 3, D Wing- Service Duct between D3 and D4 leaking water (tap inside) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-01 14:00:00 | Pass | Repack packing gland on isolation valve in plumbing duct
MSA-DCS | WA3259012 | Unit 5, B & D- flue and door faulty on regi oven | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-04 10:30:00 | Pass | Dismantle right side & lid to access vent operator. Dismantle vent, clean, lube, reassemble, adjust & test operation of vent ok. Reassemble covers & refit door. Adjust door latch to make sure door is operating ok. Left unit working ok.
MSA-DCS | WA3259018 | Unit 5 - Court Yard-Two drain/air vents leaking and a stench is eminating from them.-see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-04 13:00:00 | Pass | Recharge dry Gullies outside unit by prevent sewer smell emanating from drains.
MSA-DCS | WA3259160 | Front gate - duress alarm - east gate fence tamper M point 26 | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-04 15:38:00 | Pass | completed as per signature slip notes
MSA-DCS | WA3259320 | Power outage to the whole community | Casuarina Prison-Administration | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 30 Apr 2020 | 2020-04-30 23:08:23 | 2020-05-07 14:00:00 | Fail | Investigated fault on generator. Found and replaced on delay start timer. Waited access for electrical drawings stored in PFM store
MSA-DFES | WA3258044 | Office & Kitchen- Ant infestation | CFRS Osborne Park | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-01 12:45:00 | Pass | Carried out a service for ants at Osborne Park Fire Station. There were reports of ants located in the kitchen and office. Applied ant gel to all active ant trails. Dusted the wall cavitys outside these rooms as well spot treating all ant nests in the area
MSA-DFES | WA3258242 | L3 plant room boiler for the building not working failing to start | DFES Cockburn Emergency Services Complex | GMP-BR | Mechanical Services | Boilers (MS) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-05 16:00:00 | Fail | Meet D&A hot water on site. Access boiler on roof. Manual override boiler call. Found boiler to start but no pilot light. Dismantle boiler and check pilot light pipework. Found orifice in pilot tube to be blocked. Unblock orifice. Clean igniter and flame probe. Reassemble boiler and test operation. Found boiler to now start and operate as normal. Monitor operation, boiler cycled off at temp setpoint, working ok.
MSA-DTAG | WA3257719 | level 1, room 1.11 - Paddle is not working consistently, staff are getting locked in the room | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 30 Apr 2020 | 2020-04-30 17:00:00 | 2020-05-07 17:00:00 | Fail | Replaced Level 1, Room 1.11 Press to Exit Button .Tested multiple times, all OK
MSA-DTAG | WA3258026 | All levels door issues | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 30 Apr 2020 | 2020-04-30 13:11:11 | 2020-04-30 19:00:00 | Fail | Job completed - System manually failed over to slave at SAT. Once database rebuild occurred began re-initialising all controllers. Network slow due to ongoing Eski issues across both sites. System up and running again.
MSA-DTAG | WA3258127 | L31-13 Director General Suite Directors door keeps opening and closing on it's own | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-06-20 09:30:00 | Fail | Repairs to reader
MSA-DTAG | WA3258197 | Level 29, Opposite Lift F - doors will not close | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 30 Apr 2020 | 2020-04-30 14:25:37 | 2020-04-30 13:30:00 | Pass | Reset Break Glass, removed alarms from programming. Test, all OK.
MSA-DTAG | WA3258209 | Ground level, male toilet - Male public toilet blocked – opposite Caffisimo | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-01 08:30:00 | Pass | plunged toilet clear
MSA-DTAG | WA3258816 | All levels temperature throughout the building is very cold | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 30 Apr 2020 | 2020-04-30 16:54:46 | 2020-05-01 16:00:00 | Fail | Return to site and check building temp. Found temps to be 21 to 24 accross whole building. Check duel duct AHUs and found heating valves open and operating as normal. Vav AHUs suppling minimum of 14 degree air. Plant is working as normal.
MSA-DTAG | WA3259122 | Ladies toilets near main kitchen - water is flooding from toilets | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-04 10:00:00 | Fail | Hot water unit needs replacing. Waiting for approval
MSA-DTAG | WA3259137 | Ground Floor - Office Registry entry door is not automatically closing | Armadale Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-01 09:00:00 | Pass | Door closer adjusted
MSA-DTWD | WA3257705 | B1, Facilities Office door - Will not key lock reported by security guard | Murdoch Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 1 | CLOSE | 30 Apr 2020 | 2020-04-30 17:00:00 | 2020-04-30 13:35:00 | Pass | Job completed - replace Mortice lock
MSA-DTWD | WA3257888 | B Block Tech w/shop change room. - Broken light switch | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-05 07:30:00 | Pass | Attended site and signed in. Spoke to pfm and located faulty light switch. Found we needed a new cover plate as well. Got new cover plate and replaced switch and plate. Tested all ok. Job complete.
MSA-DTWD | WA3257895 | B Block Tech w/shop change room. - Blocked urinal drain. | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 16:27:00 | Pass | Unblocked drains
MSA-DTWD | WA3257901 | A Block rear courtyard - Water feature pump has stopped working | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-04 12:30:00 | Pass | Reset timeclock to pump. Job completed
MSA-DTWD | WA3258084 | block 1 L1 1F21 Key lock not working | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-04-30 14:15:00 | Pass | Lock not working to Block 1 - Room 1F21.Lock replaced/repaired.
MSA-DTWD | WA3258112 | A Block, Plant Room- Boiler pumps not working | Leederville Campus | GMP-BR | Mechanical Services | Boilers (MS) | Precise Air Group | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-06 09:30:00 | Fail | Attended site and assisted nrp with boiler pump faults,found switchboard to have a faulty phase failure relay causing pumps not activate. Nrp to pick up parts today,replace and check system is functioning correctly
MSA-DTWD | WA3258284 | A Block,SE end near office A7- Fault 4' double fluro light fitting, replace with LED | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-05 09:00:00 | Pass | Spoke to pfm and found which light was out. Replaced old faulty fluro lights with new led batten. Tested all ok. Signed out job complete.
MSA-DTWD | WA3258310 | C block, Room C016- 3x broken window latches | Joondalup Kendrew Campus | GMP-BR | Building | Windows (BU) | M Construction (WA) | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-25 12:40:00 | Fail | Job complete
MSA-DTWD | WA3258312 | Front entrance - replace broken glass window | Perth Campus B7 | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-04-30 15:00:00 | Pass | REGLAZED BROKEN GLASS PANEL 6.38 CLEAR LAMINATED SAFETY GLASS 1 - 957/918 X 193 2.33 L/M OF PUTTY USED 6X SPRIGS
MSA-DTWD | WA3258405 | AT207 faulty door lock | Kwinana Automotive Centre | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-04 08:00:00 | Pass | Replaced faulty lock
MSA-DTWD | WA3258976 | N Block, Room N129- lights are faulty | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-06 12:45:00 | Pass | Repalced multiple lamps out as requested by site. Job completed
MSA-DTWD | WA3258985 | D block, Level 3 - aircon lost commication - Greenskills BMS.... L3 - AC - 01 to 07 offline | East Perth Campus | GMP-BR | Air Conditioning | Package (AC) | Building Automation & Electrical Services Pty Ltd | 3 | CLOSE | 30 Apr 2020 | 2020-05-07 17:00:00 | 2020-05-04 00:00:00 | Pass | No Charge
MSA-DTWD | WA3259088 | b block, ground floor, staff room - billi hot water unit leaking | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 30 Apr 2020 | 2020-05-05 17:00:00 | 2020-05-01 11:23:00 | Pass | Machine off on arrival. Water continuesly running to the overflow. Level sensor failure and inlet solenoid failure. Machine has a lot of scale. Also replaced tap that was full of scale and rust
MSA-DTWD | WA3259090 | B block LT-S fault coming up on the panel | Murdoch Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-01 15:00:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochSite contact: Mike Day - 0407 476 354Work Order Number: WA3259090 Call out Date: 30/04/2020Target finish: 01/05/2020 17:00Original information: B block LT-S fault coming up on the panelFIP B Blockattending to LT-S faultA40425061BAttended site:Date:30/4/20Start Time:16.00Finish Time:17.00Techs on Site: 1Works Carried Out:Analog fault on l2s2 in admin office. Couldn’t find the zone monitor. Isolated fault output and need to return tomorrow morning Return to site:Date:1/5/20Start Time:7.30Finish Time:15.00Techs on Site: 1Works Carried Out: Looked for zone monitor. Found it in roof space. Traced fault on cable. Found faulty detector. Replaced detector. All OKMaterials and Equipment Used: 1 x smoke detector and base
MSA-DTWD | WA3259143 | Block 2, 1st Floor- Blocked sewer | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-11 10:15:00 | Fail | Replace isolation valve after unblocking sewer. Campus tried to isolate water when toilets were blocked in case people kept using them
MSA-DTWD | WA3259171 | BLD 822 ground boiler room Copper pipe leading to boiler pump leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 1 | CLOSE | 30 Apr 2020 | 2020-05-01 17:00:00 | 2020-05-06 15:06:00 | Fail | Repairs to leaking copper water pipe non return valves and pump connections to boiler room Building 822
MSA-DCA | WA3264188 | upper/eastern plant room, Faulty actuator on Cooling Tower CT2-see notes | Perth Concert Hall-Main Building-Level 4 - Cooling Tower Room - Plant East | GMP-BR | Air Conditioning | Cooling Tower (AC) | Precise Air Group | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-13 15:15:00 | Fail | Attend aire and complete pre start safetry checks. Investigate fault with cooling tower 2 isolation valves. Test microswitches on actuator - all ok. Found loose connection at controller. Tighter connection and test, all ok.
MSA-DCA | WA3264254 | Reverse Osmosis leaking | Collection and Research Centre Welshpool | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-07-08 16:30:00 | Fail | Job to be closed out with quotation to be submitted for applicable outlined repair works via IBIS technologies.
MSA-DCS | WA3262723 | SITE COST Internal and external microwave in zone 20 and 21 is not functioning and in constant alarm | Hakea Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 May 2020 | 2020-05-01 09:38:33 | 2020-05-01 11:55:00 | Fail | Checked microwave power and senstar module voltage.All appear ok. Adjusted internal microwave sets and tested.Control confirmed activation and securing.External microwaves in constant alarm.Re-terminated and replaced resistors.Aligned and tested.Control advised microwave working.Monitored for false alarms.Confirmed no false alarms for 1 hour.
MSA-DCS | WA3262831 | mechanical w/s machine room lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 May 2020 | 2020-05-07 17:00:00 | 2020-05-04 11:30:00 | Pass | Investigate and repair/replace lights in mechanical machine shop
MSA-DCS | WA3262833 | kitchen side entry lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 May 2020 | 2020-05-07 17:00:00 | 2020-05-04 15:00:00 | Pass | Investigate and replace lights at kitchen entry
MSA-DCS | WA3262835 | unit 2 cell 49 - GPO broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 May 2020 | 2020-05-07 17:00:00 | 2020-05-04 08:30:00 | Pass | Investigate and replace gpo in unit 2 cell 49
MSA-DCS | WA3262838 | wwtp pit sump pump faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 May 2020 | 2020-05-07 17:00:00 | 2020-05-01 15:00:00 | Pass | Investigate wwtp sump pump. Found to be faulty. Replace with spare from site.
MSA-DCS | WA3262868 | unit 2, outside lower landing - hot water unit to showers not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 11:30:00 | Pass | COMPLETED
MSA-DCS | WA3262873 | POT HOLE on driveway between gate house and admin | Karnet Prison Farm | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 3 | CLOSE | 01 May 2020 | 2020-05-07 17:00:00 | 2020-05-04 08:30:00 | Pass | 04/05/20Repair pot hole
MSA-DCS | WA3262884 | Unit 14, control room - the cell call system registering network error | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 May 2020 | 2020-05-05 17:00:00 | 2020-05-01 12:30:00 | Pass | Multiple alarms on the cell call system, site wide, due to installation of new equipment in new units. No warning ofwork starting to officers in units or advise when work completed. Some alarms in for days. This has been referred to Seme management for referral to PFM & DoJ.
MSA-DCS | WA3262910 | Unit 5 Cell A21 Flooring lifted around sink and toilet | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-09-11 13:15:00 | Fail | lifting vinyl repaired
MSA-DCS | WA3262911 | Unit 1, Cell a19 - repair 1.5 sqaure meters vinyl is ripped up. | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 01 May 2020 | 2020-05-02 08:14:13 | 2020-05-13 15:30:00 | Fail | replaced damaged vinyl
MSA-DCS | WA3262913 | Unit 1 B07 - Personal lock not locking | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-06 12:00:00 | Pass | replaced hinges, door plate,lock and adjust strike.
MSA-DCS | WA3262936 | Unit 4, D wing - lihgt broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-01 11:30:00 | Pass | Repaired light
MSA-DCS | WA3262937 | Gatehouse - Equipment room - Unable to download footage, unable to acccess indigo vision network | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 May 2020 | 2020-05-01 12:29:51 | 2020-05-01 14:00:00 | Fail | Rectified issue with camera recording failure, restored rights within configuration. Tested fully operational.
MSA-DCS | WA3262961 | Front gate, control pad - CCU Entry Door False Alarming | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 May 2020 | 2020-05-02 08:42:50 | 2020-05-01 13:30:00 | Pass | Rectified and fixed faulty door sensor, job completed.
MSA-DCS | WA3262967 | OPD, control room - PDA system activated unable to re-set | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-29 09:00:00 | Fail | Replaced two failed button mechanisms as per signature Slip.Quote to replace Duress annunciators in units 1 - 7 has been submitted
MSA-DCS | WA3262974 | Unit 5, The duress alarm in the control room has been set off due to the power outage last night | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-06-26 14:30:00 | Fail | Mobile Duress annunicators in Unit 5 failed following upgrade of MDAS head end equipment by Honeywell techs bringing new units in precinct on-line. Options for reinstatement / replacement being forwarded to PFM.
MSA-DCS | WA3262987 | Security Area - Security Office-download footage in MPU | Casuarina Prison | WSM-GR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-01 11:00:00 | Pass | Attended MPU, accessed DVR, located video required, downloaded to memory stick and delivered to Security SO Mr deMonk.
MSA-DCS | WA3262991 | Control room - cameras not working | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-01 15:30:00 | Pass | monitors going into sleep mode when not used. Reconfigured to never do so. Visits internal camera 2 offline. Camera had lost configuration. Reconfigured and tested, all good
MSA-DCS | WA3262994 | Control room - cameras 7 will not tilt and pan | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-01 14:30:00 | Pass | Camera fully operational
MSA-DCS | WA3262996 | Unit 4 S/O office Air Con and Heater not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-01 14:30:00 | Pass | Tested unit in all modes. Checked over all components. Unit running correctly. No fault present.
MSA-DCS | WA3263001 | ont the Control room camera the east wing rec yard is working then not | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-06-26 15:30:00 | Fail | From service terminal in the Gatehouse Control Room we checked the video from all SHU and MPU/IOU Cameras, including those in exercise yards. All cameras showing good video with good colour balance. Unable to identify any problem cameras.
MSA-DCS | WA3263004 | Unit 2 C7 broken toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 May 2020 | 2020-05-02 09:03:58 | 2020-05-01 14:20:00 | Pass | Replaced faulty inlet valve
MSA-DCS | WA3263040 | Unit 7 cell E8 Light in cell broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-04 11:00:00 | Pass | Repaired light
MSA-DCS | WA3263044 | Laundry - Speed queen washing machine faulty/cannot operate | Casuarina Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 01 May 2020 | 2020-05-02 09:13:49 | 2020-05-01 11:00:00 | Pass | Laundry Speed queen washing machine faulty. Check machine & controls. Found machine full of water not draining. Replaced drain valve, unable to test due to main water supply to site not in service. Returned, water supply now on, machine all working correctly.
MSA-DCS | WA3263051 | Unit 1, B13 - Tap broken, will not turn off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 May 2020 | 2020-05-02 09:27:32 | 2020-05-12 16:26:00 | Fail | Push button at basin faulry.Replaced faulty push button
MSA-DCS | WA3263062 | Level 3 - 3 lights flashing on water tap in main kitchen on level 3 | East Perth | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 13:43:00 | Pass | All working on arrival Pressure test system all okayCleaned level sensorsEverything seems okay Unit is 10 years old
MSA-DCS | WA3263786 | front & lobby doors when open/shut display for secure/insecure dont change on display | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 May 2020 | 2020-05-02 11:22:43 | 2020-05-06 19:00:00 | Fail | Job complete
MSA-DCS | WA3263795 | unit 1 A and B SITE COSTED site common area camera 14 is down | Melaleuca Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 May 2020 | 2020-05-01 15:30:47 | 2020-05-01 15:37:00 | Fail | Rectified and fixed video loss cameras from unit 1 A and B wing common area. Job completed.
MSA-DCS | WA3263875 | Unit 3, B3 - water in cell light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 May 2020 | 2020-05-02 11:39:55 | 2020-05-01 14:30:00 | Pass | Replaced light.
MSA-DCS | WA3263888 | Unit 14, C2 - shower dairn blocked - fully blocked up again and fills right up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 16:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3264021 | Unit 4 - B & D-Unit 4 , B/D hot water urn ,tap broken . | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-06 09:55:00 | Pass | Replaced broken tap. All ok
MSA-DCS | WA3264166 | unit 3, A5 - toilet cistern faulty | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-01 18:40:00 | Pass | Replaced faulty cistern
MSA-DCS | WA3264169 | Unit 3 cell A12 toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-06 11:30:00 | Pass | Replaced outlet washer
MSA-DCS | WA3264170 | unit 3, A4 - toilet cistern faulty | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-06 12:38:00 | Pass | Replaced cistern
MSA-DCS | WA3264262 | Unit 3 D wing dayroom Lock and doorhandle damaged | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 08:45:00 | Pass | Replaced faulty handle.
MSA-DCS | WA3264265 | Unit 8 C/D dayroom store room Lock Faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-11 12:00:00 | Fail | replaced lock
MSA-DFES | WA3262845 | Disabled toilet - leaking mini stop | CFRS Osborne Park | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 01 May 2020 | 2020-05-01 17:00:00 | 2020-05-01 15:00:00 | Pass | Replaced Leaking mini stop.
MSA-DFES | WA3264012 | Damage to workshop panel - Photo to be sent | O'Connor Fleet Storage | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 12:30:00 | Pass | Repairs made to panel and all in good working order now
MSA-DTAG | WA3262929 | Grounds - Garden around building - Water is coming out of all sprinklers at really high pressure | Perth Children's Court | GMP-BR-HO | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 1 | CLOSE | 01 May 2020 | 2020-05-04 17:00:00 | 2020-05-04 14:00:00 | Pass | Retic Repairs
MSA-DTAG | WA3263003 | Level 2A Lift 2 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 01 May 2020 | 2020-05-04 17:00:00 | 2020-05-01 14:10:00 | Pass | Lift ROA. Tested, no fault found. Security unaware of any issues with lift of late. Lift in service. Chargeable.
MSA-DTAG | WA3263123 | LEVEL 10 - please resolve issue accessing the Gallagher Command card access system. | Westralia Square | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 09:35:00 | Pass | Reported fault "LEVEL 10 - please resolve issue accessing the GallagherCommand card access system. Despite multiple attemptsoverthe past 2 days we are unable to login. Also received thefollowing message; Connection to 192.168.0.24 failed."Fault investigated appears to be related to works undertaken by another security contractor moving Gallagher Server. Security Certificateissue copied from Gallagher server onto workstation, Server time also adjusted retested working ok. Client requested and giveninstruction in running current cardholder report for level 10. Job completed.
MSA-DTAG | WA3263198 | Legal Aid to back court yard - Door handles for double doors need tightening | Perth Children's Court | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 13:30:00 | Pass | DOOR HANDLES TIGHTENED
MSA-DTAG | WA3263941 | L3 1.The entry door to the office (closest to the lifts) is extremely loud | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 14:30:00 | Pass | HINGES CLEANED/ LUBRICATED
MSA-DTAG | WA3263945 | female toilet door slams extremely loud-see notes | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 15:00:00 | Pass | Door closer adjusted
MSA-DTAG | WA3264215 | level 13, foyer - Slide door won’t open when button pressed | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-06-04 18:00:00 | Fail | Reset reader and re-initialized door controller. Upload slow due to ongoing issues with SQL database and Pacom Unison Write speed to SAN unit. Also reset auto door. All OK.Job completed.
MSA-DTAG | WA3264258 | L12 Magistrates Chambers 12.04 Lights flickering in Magistrates Chambers | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 11:30:00 | Pass | Job complete
MSA-DTAG | WA3264283 | 1903 basement female toilet Disconnect failed HWU and reconnect new unit -see notes | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 01 May 2020 | 2020-05-04 17:00:00 | 2020-05-04 07:40:00 | Pass | Disconnected hwu system and reconnected once new hwu installed
MSA-DTWD | WA3263071 | BLD 840 switchroom Faulty light timer | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 12:00:00 | Pass | Job completed - replaced faulty light timer
MSA-DTWD | WA3263128 | L2 FIP on fault | Perth Campus B6 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 01 May 2020 | 2020-05-08 17:00:00 | 2020-05-29 10:30:00 | Fail | Attended site to investigate fault on panel 8 May.Reattended 29 May to install new detector, expander wireless detector.
MSA-DTWD | WA3263142 | B block, room BG17, ET17 Window - Window frame falling apart and glass dropping out of frame | Carlisle Campus | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 01 May 2020 | 2020-05-04 17:00:00 | 2020-05-01 12:30:00 | Pass | ATTENDED SITE, SECURED TIMBER FRAME WITH ANGLE 25 X 30 1 @ 1000, 4X SCREWS AND SILICONE AND MEASURE FOR REPLACEMENT PANEL
MSA-DTWD | WA3263171 | A block, level 1, fire booster cabinet - Roof support has broken | Leederville Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-04 14:00:00 | Pass | Installed 2 new hardie sheets to fire c=booster cabinet and waterproofed - take away broken sheets
MSA-DTWD | WA3264010 | F block Maintenance Compound – Faulty Tap Set | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-06 12:45:00 | Pass | Replaced taps in workshop
MSA-DTWD | WA3264013 | A block A4 Cleaners Store – Leaking Tap | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 01 May 2020 | 2020-05-06 17:00:00 | 2020-05-06 13:30:00 | Pass | Replaced leaking tap
MSA-MRWA | WA3263111 | Level 5, 548 - Flickering Light, please attend and remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 01 May 2020 | 2020-05-04 17:00:00 | 2020-05-01 15:00:00 | Pass | Replaced tube with a new one
MSA-DCS | WA3264536 | Cell 24 block 1 fire alarm is false reporting | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 02 May 2020 | 2020-05-06 17:00:00 | 2020-05-04 11:45:00 | Pass | Replaced two faulty detectors in Unit 1 rooms 22 and 24 (L4 S 22 and 24).Cleaned two dirty detectors in rooms 20 and 23.
MSA-DCS | WA3264606 | Karnet Prison farm- toilet blocked in Unit 1 SITE COSTED | Karnet Prison Farm | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 02 May 2020 | 2020-05-02 11:53:20 | 2020-05-02 12:20:00 | Fail | One toilet out of a row of five was blocked by an entire roll of toilet paper. Removed roll of toilet paper and plunged toilet.
MSA-DCS | WA3264607 | Unit 9 cell B2 SITE COST has a significant water leak coming in through the roof | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 02 May 2020 | 2020-05-02 11:54:58 | 2020-05-02 13:02:00 | Fail | Cut out section of failed water pipe due to corrosion
MSA-DCS | WA3264624 | Personal duress system located in the special handling unit SHU will not reset | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 May 2020 | 2020-05-02 12:23:19 | 2020-05-07 17:02:00 | Fail | Investigated duress fault in SHU, found duress activates correctly but display not working. Checked communication systems and hardware and found duress servers have been recently replaced by another contractor and there appears to be integration issues between duress servers and duress displays Recommend following up with other contractors.Job Complete
MSA-DCS | WA3264642 | TTZ13 &23 camera are not working SITE COSTED | Melaleuca Prison | WSM-BR-SITE | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 May 2020 | 2020-05-02 12:45:23 | 2020-05-02 13:15:00 | Fail | Reload the settings of camera from EBI due to lost of video, job completed.
MSA-DCS | WA3264763 | Unit 4 cell D11 & B4 cell call are not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 May 2020 | 2020-05-03 12:06:27 | 2020-05-05 14:45:00 | Fail | Cell call point in D11 found vandalised, removed CI-CC cell call point and replaced with new style CI-CC slimline point, backing plate required adjusting and cutting to suit. New point is mounted sealed and tested operational.Cell call point in A4 found vandalised, removed CI-CC cell call point and replaced with new style CI-CC slimline point, cell intercom required rear packing and new rivit points added to meet new style requirement. Cell intercom point is mounted sealed and tested operational.
MSA-DCS | WA3265119 | Control room Camera fault -6PTZ,Spinning and iits not stop | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 May 2020 | 2020-05-03 09:52:51 | 2020-05-03 09:15:00 | Pass | Rectified and fixed the faulty PTZ camera 6 , job completed.
MSA-DCS | WA3265170 | Hakea Prison- front door not operating | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 May 2020 | 2020-05-03 11:21:34 | 2020-05-03 09:00:00 | Pass | Attended site checked and found front door No.3 not working. Checked no power to door lock. Traced cable back to equipment room. Checked cable connections and reset the relay control the door. Tested door working ok after work.
MSA-DCS | WA3265252 | Unit 8 - A wing - SITE COST Hot water system is leaking and not functioning. | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 03 May 2020 | 2020-05-03 13:26:27 | 2020-05-05 16:03:00 | Fail | Renew 325 lt hwu Wait 2 hours for escort
MSA-DCS | WA3265259 | UNIT 10- Cell C2- Water leak coming from the wall. leak is constant. | Hakea Prison-Unit 9 64 Cell Prison Living | GMP-BR- HO | Building | Materials (BU) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 May 2020 | 2020-05-04 09:37:55 | 2020-05-04 13:20:00 | Fail | Make safe water leak caused by failed spindle to basin Order in new part from supplier
MSA-DCS | WA3265431 | One of the cameras in the Crisis Care unit, unable to view. | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 May 2020 | 2020-05-03 17:48:49 | 2020-05-03 15:45:00 | Pass | Rectified and fixed the lost of video from Monitor, job completed.
MSA-DTWD | WA3266682 | retrospective works ** A block - broken window - Job attended 03/05/2020 | Rockingham Campus | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 03 May 2020 | 2020-05-04 17:00:00 | 2020-05-19 16:48:00 | Fail | ATTENDED SITE AFTER HOURSREGLAZED 3 BROKEN WINDOWS6.38 CLEAR LAMINATED SAFETY GLASS2-815 X 10256.38 GREY LAMINATED SAFETY GLASS1-815 X 1025PATCHED TO SECURE ANOTHER BROKEN WINDOW (REQUIRED PUTTY TESTING FOR ASBESTOS6.38 CLEAR LAMINATED SAFETY GLASS2-1220 X 800AND 2 SQM OF SECURITY FILM2 TUBES OF SILICONE USEDPUTTY TEST NEGATIVE FOR ASBESTOSRETURNED LATER DATE TO REGLAZE6.38 CLEAR LAMINATED SAFETY GLASS1-1580 X 1090PLUS SILICONE2 MEN REQUIRED
MSA-DCA | WA3266788 | Alexander Library Building,Outside, west side building(corner near exit from stairwell 5) - Graffit | State Library of WA-Main Building-External Area | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-05 09:45:00 | Pass | Removed graffiti
MSA-DCS | WA3265805 | Unit 5 AWing Regi Oven continuously cutting out | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 May 2020 | 2020-05-06 17:00:00 | 2020-05-04 10:00:00 | Pass | Tested regi oven
MSA-DCS | WA3265819 | Unit 2 Cell D8 Cell call faulty | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 07:07:23 | 2020-05-04 11:00:00 | Pass | Replaced damage and faulty cell call, job completed.
MSA-DCS | WA3265825 | Unit 8 Laundry 4 Floor tiles require replacing | Hakea Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-08 17:00:00 | 2020-10-28 10:33:00 | Fail | REMOVE BROKEN TILES AND REPLACE WITH NEW - GROUT NEW AREA
MSA-DCS | WA3265828 | Unit 10 Control Lunch room new light ballast required | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 10:00:00 | Pass | Repaired light
MSA-DCS | WA3265834 | Unit 8 LHS B/C wing showers Dripping showers | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 13:28:00 | Pass | Replaced 1 quator turn spindle on c side waiting for more spindles to arrive at tradelink todo b sideReturned to replaced other spindle
MSA-DCS | WA3265837 | Zone 10 in constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 07:22:23 | 2020-05-04 12:00:00 | Pass | Attend site, investigated fault & found zone 10 constantly activating. cable join has been damaged, replaced join with new splice kit & retested. all tested & working ok. job complete11/5/20 job recalled by site, found all tests continued working ok. checked end of line resistors & all tested ok. job complete.
MSA-DCS | WA3265867 | Unit 6 Control room door closer not shutting properly | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 04 May 2020 | 2020-05-06 17:00:00 | 2020-05-06 11:30:00 | Pass | Adjusted door closer.
MSA-DCS | WA3265899 | Unit 6 Cell C8 Cell lock getting stuck and no opening at times | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 04 May 2020 | 2020-05-06 17:00:00 | 2020-05-06 12:45:00 | Pass | Adjusted strike plate and fitted new lock
MSA-DCS | WA3265925 | Site Cost Boilerhouse glass is broken on pressure guage for main compressor | Hakea Prison | WSM-BR-SITE | Equipment | Compressors, Generators (EQ) | CLEVELAND COMPRESSED AIR SERVICES | 2 | CLOSE | 04 May 2020 | 2020-05-06 17:00:00 | 2020-05-07 10:01:00 | Fail | Job completeQuote to follow for new compressor
MSA-DCS | WA3265934 | Medical Admin Lock barrell missing from bottom drawer of cabinet | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 04 May 2020 | 2020-05-08 17:00:00 | 2020-05-29 15:30:00 | Fail | Supplied and Installed required locks
MSA-DCS | WA3265940 | Kitchen main coldroom 4 fluorescent lights broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 May 2020 | 2020-05-08 17:00:00 | 2020-05-08 15:00:00 | Pass | Replaced lights
MSA-DCS | WA3265977 | Unit 10, A/B dayroom - Industrial toaster keeps tripping | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 May 2020 | 2020-05-05 08:12:16 | 2020-05-04 12:00:00 | Pass | Checked tripping power.
MSA-DCS | WA3265985 | Textiles - security flyscreen door handle has fallen apart | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-05 13:30:00 | Pass | Replaced broken handle on Security Screen door to Recreation Lock kit comes complete with handles and lock
MSA-DCS | WA3266002 | Unit 5, D wing, Cell D2 - Night light (observation light) not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 08:30:00 | Pass | Repaired faulty lights in unit 5 d2
MSA-DCS | WA3266007 | CCU (11) - Control Room download footage for CCU/Security | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 15:19:00 | Pass | Searched footage on old system, extracted data and converted data into a usable modern format, provided to security.Job Complete
MSA-DCS | WA3266011 | Unit 3, C10 - cikd tap water dripping may need new washer | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 16:30:00 | Pass | Remove and replace 1/4 turn spindle on basin in Cell.
MSA-DCS | WA3266025 | Unit 4 - B9 spring to stop window from opening/shutting is broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 13:15:00 | Pass | double up of WA3266153, spiral balances replaced
MSA-DCS | WA3266049 | Unit 4 - D Wing - Cell fire (heat) detection button has been compromised | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-13 09:30:00 | Fail | Checked in unit and found to be paper and toothpaste packed into sprinkler head. Will require fitter to attend drain down and clean.13.05.20CHarrived onsite and went into prisonfound sprinkler covered in toilet paperisolated system and cleaned sprinklerde isolated system and all ok
MSA-DCS | WA3266051 | Unit 1, A wing shower, closest to the door - is not operational | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 08:00:00 | Pass | Inspect shower, de-isolate hot water at TMV to return hot water supply.
MSA-DCS | WA3266057 | Unit 7 - Control room - B Wing Camera not working on screen | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-08 11:32:00 | Fail | Replaced faulty video decoder.Tested OK.
MSA-DCS | WA3266061 | Unit 14, A8 - WAter leaking from bottom of Basin A8 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 11:00:00 | Pass | Replace faulty quarter turn spindle in plumbing duct
MSA-DCS | WA3266064 | Unit 1 - B Wing grill working intermittently | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-11 09:00:00 | Fail | Due to ongoing problems with this grill control equipment in Maxpro we cutover this wings grill control ahead of the scheduled replacement cutover. Grill was operating correctly when used via the Gallagher based controller.
MSA-DCS | WA3266067 | Education comms room HWS is leaking over the floor | Bandyup Prison | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 May 2020 | 2020-05-05 08:59:08 | 2020-05-05 11:18:00 | Fail | Attended site,Drained and removed old failed hws,Supplied and installed a new 50L storage hot water unit including hot and cold expansion valves. Temp set to 60 degrees as requiredTested works on completion and disposed of old unit. Electrician required to reconnect
MSA-DCS | WA3266069 | Unit 5, A wing, A9 - window needs to be re-sprung (not closing/opening properly | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-14 14:00:00 | Fail | SPIRAL BALANCES RENEWED
MSA-DCS | WA3266081 | Unit 3, C11 - cell call alarm turns on occasionally by itself and making noises | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-04 13:15:00 | Pass | Rectified and fixed the fault on cell call unit, job completed.
MSA-DCS | WA3266090 | Unit 3, C13 - window not working needs repairing | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 10:00:00 | Pass | replaced spiral balances
MSA-DCS | WA3266096 | Unit 3, C12 - window not working needs repairing | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 09:15:00 | Pass | replaced spiral balances
MSA-DCS | WA3266115 | INF (10), Dispensary room - Main lock not functional | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-15 11:30:00 | Fail | Replaced lever pack & service
MSA-DCS | WA3266125 | Kitchen - brat pan ignition switch faulty | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-22 16:00:00 | Fail | 07/05/20Attended Bratt pan, found faulty thermostat, didn't play up when cold, but started working intermittently when about 70 degrees.And found damaged ignition probe leads and a loose earth probe.Parts required 1 x Electronics thermostat kit1 x High Limit1 x Sparkelectrode1 x Ignition cable1 x tube of High temperature silicone 22/5/20Attended Bratt panHad to wait until staff were finished using unit.Removed thermostat and installed new thermostat.The existing was damaged from someone forcing it.Removed bent spark electrode and installed new.Had to grind off some corroded screws to install new overtemp.Checked thermostat calibration, unit is working fine.
MSA-DCS | WA3266134 | Unit 7 - C Wing C6 windw is not staying open, slowly sliding closed | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-07-03 13:00:00 | Fail | NEW WINDOW BALANCES & FEET FITTED
MSA-DCS | WA3266142 | Abattoir WWTP tank isolation valves faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 12:00:00 | Pass | Completed. Picked up parts from suppliers and delivered to site for others to install.
MSA-DCS | WA3266146 | Unit 14, D16 - blcoked shower, has been plunged a couple of times to o avail | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 10:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3266153 | Unit 4, B wing, Cell B9 - window is not holding up | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 13:00:00 | Pass | replaced spiral balances
MSA-DCS | WA3266154 | Administration outdoor lighting is very poor or none at all when leaving prison after lock up muster | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 10:30:00 | Pass | Repaired faulty lights in admin building. Picked up replacement flood for admin gate. Installed and tested
MSA-DCS | WA3266158 | Cleaning store room - sink leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 10:00:00 | Pass | COMPLETED
MSA-DCS | WA3266159 | Unit 1, POD 2, Kitchen - hot water is leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 09:45:05 | 2020-05-05 14:18:00 | Fail | Plumber required and was on site. Hot water system not under bench IT WAS THE MIXER TAP AT THE SINK LEAKING NOT THE DRINKING WATER SYSTEM
MSA-DCS | WA3266162 | Unit 4, Cell D16 - Door lock faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 13:45:00 | Pass | Attend site, remove lock and components from unit 4 cell D16 door, service lock and components then reinstall lock for correct operation
MSA-DCS | WA3266166 | Unit 2 Cell C3 Sink tap broken | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 May 2020 | 2020-05-05 09:47:33 | 2020-05-04 12:28:00 | Pass | Basin hot tap was hard to use from dirt and grim build up. Pulled apart cleaned and re installed
MSA-DCS | WA3266167 | Unit 3, A wing - oven not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-13 11:00:00 | Fail | Unit 3A Oven not working. Check oven & controls. Dismantle stove, locate broken oven door switch. Remove broken switch, no parts available. Bypass switch, remake safe wiring connection. Report to staff.
MSA-DCS | WA3266170 | Unit 2, C-15 - shwer & sink blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 May 2020 | 2020-05-05 09:49:13 | 2020-05-04 11:38:00 | Pass | Sink and shower blocked from hair and food Removed shower grate removing hair pulled apart and empty basin trap
MSA-DCS | WA3266182 | Hotham Laundry & Kitchen both sinks blocked badly | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-04 15:18:00 | Pass | Laundry and kitchen sink blocked
MSA-DCS | WA3266192 | Kitchen, Blast chiller 2 - Not working correctly, switching problem | Hakea Prison | GMP-BR- HO | Refrigeration | Chiller (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 11:00:00 | Pass | Blast chiller operating as normal
MSA-DCS | WA3266203 | Gate House- Door 9 faulty lock, hard to open from inside air lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-04 12:30:00 | Pass | job completed - replace bolt throw and back case screws.
MSA-DCS | WA3266205 | Hakea staff car park - two light poles not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 08:00:00 | Pass | Repairs to car park lights
MSA-DCS | WA3266224 | Unit 1 Cell A8 Cell door jamming wont close | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 May 2020 | 2020-05-05 10:06:23 | 2020-05-06 11:30:00 | Fail | Realigned door.
MSA-DCS | WA3266244 | Eyre Unit - Laundry has no hot water | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 May 2020 | 2020-05-05 10:11:23 | 2020-05-04 13:33:00 | Pass | Called in for no hot water hwu was switched off re switched on works fine
MSA-DCS | WA3266247 | Gate House- Door 3 slamming, door closer faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 21:00:00 | Pass | remove door, replace floor and top pivot, re install door and install door closer.
MSA-DCS | WA3266260 | Jeelia Unit A Wing no hot water kitchen & laundry | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 May 2020 | 2020-05-05 10:19:17 | 2020-05-04 14:28:00 | Pass | Hwu switched off once turned back on waited and tested fixtures hot water works fine
MSA-DCS | WA3266261 | Bakery- Bun rounder is faulty,broken bolt | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 04 May 2020 | 2020-05-05 10:16:28 | 2020-07-07 12:30:00 | Fail | ALL WORKSHOP REPAIRS - NO SIGNED PAPERWORKDate - 05/05/20Make - Daub Model - DR3M-03-00Serial - 140571Technician - WS. Called as requested to the BDR arm broken. Found the blade release arm ripped out of securing now unable secure will require a new locking plate and blade release mech. Workshop repair. Parts required 1x locking plate1x blade release bolt 1x bush 04/07/20 WS. Stripped and cleaned the BDR head then assembled with new parts set and the tested all working ok. Unit requires new wheels (VERY DANGEROUS) will obtain and fit.Parts required4x wheels07/07/20 WS .Fitted new wheels tested all ok.rapped and packed ready for shipping.
MSA-DCS | WA3266265 | Unit 3, A4 - Vent above sink leaking water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 14:30:00 | Pass | Replace 20mm copper service in plumbing duct.
MSA-DCS | WA3266267 | Unit 1 - A Wing middle shower is running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-05 15:00:00 | Pass | Replace missing split pin in shower spindle in plumbing duct.
MSA-DCS | WA3266283 | Unit 4 - A Wing cell A13-window is not holding up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 11:30:00 | Pass | replaced spiral balances
MSA-DCS | WA3266290 | Unit 4, C wing, C03 - Main cell light is flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 10:00:00 | Pass | Repaired faulty lights in unit 4 c3
MSA-DCS | WA3266294 | Unit 4 - A Wing Cell A11 window is not holding up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 12:15:00 | Pass | replaced spiral balances
MSA-DCS | WA3266296 | Main Kitchen- Cool Room door handle is damaged, further details below | Nyandi Training Academy | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-12 10:45:00 | Fail | Quoted for new door handleAll ok finished
MSA-DCS | WA3266299 | Unit 3, control room - aircon not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 14:33:00 | Pass | Arrived on site and signed in, checked over aircond found remote code had been changed,reset remote and set up to proper code,turned on and tested all running ok at present.
MSA-DCS | WA3266308 | Gatehouse, control room - fire alarm fault (see notes) | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-20 08:45:00 | Fail | Attended site and found the following problems.1: M1-37 Kitchen MCP, M1-35 Infirmary, M1-36 Infirmary, Industries MCP, M1-100 Dental store all in fault due to building works.2: learning centre issues with in going battery fault will need to fit new brigade board and power supply to panel. 3 hours to attend and fit to panel.Ampac Fire Finder S/N 1001513-2. 25/3/10Fitted new PSU and brigade board and left normal.
MSA-DCS | WA3266309 | Jasper, A Wing- Air Con not working (no power) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-06-25 16:31:00 | Fail | System is running Beware rodent issues
MSA-DCS | WA3266310 | Unit 1 - A & C, C Wing store light switch is hanging off the wall. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 08:30:00 | Pass | Replaced damaged switch in unit 1 store
MSA-DCS | WA3266315 | Unit 5 - B Wing Cell B13 window is not closing/opening properly | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-14 12:30:00 | Fail | RENEW SPIRAL BALANCES & RE FIX PULL HANDLE
MSA-DCS | WA3266318 | Unit 1 Return water tank is faulty | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 May 2020 | 2020-05-05 10:51:42 | 2020-05-19 16:55:00 | Fail | Works complete
MSA-DCS | WA3266334 | Unit 5, Cell C1-Window rivets broken off | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-14 11:15:00 | Fail | SPIRAL BALANCES RENEWED
MSA-DCS | WA3266352 | Unit 1, Control Kitchen- no water supply | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-21 08:50:00 | Fail | Job completed by others
MSA-DCS | WA3266360 | Unit 13. Cell A9- Leaking coming from shower screen | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-06-03 12:00:00 | Fail | REPLACE SHOWER SCREEN
MSA-DCS | WA3266365 | Unit 2, B WIng, Cell B3- Internal cell light switch has broken & wires exposed | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 May 2020 | 2020-05-05 11:12:41 | 2020-05-05 08:00:00 | Pass | Replaced damaged light switch
MSA-DCS | WA3266378 | House 6 -Fire Panel unplug the correct core and modify any alarms that may be triggered | Boronia Pre-release-AK23 - Prisoner Accommodation House 6 and 7 | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 08:16:00 | Pass | Attended site as requested - performed test no spare cables for data contractor
MSA-DCS | WA3266388 | Unit 14, A & C - the vesda system Fault (see notes) | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 08:18:00 | Pass | Attended site and found the followingUnit 14 wing A/C cells 3&4 found low flow in pipes 2 and 3 checked sample points and pipes but found all clear. Increased fan speed and renormalised and managed to clear fault.Vesda unit is showing signs of wear
MSA-DCS | WA3266399 | Unit 2, D16 - sink broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 May 2020 | 2020-05-05 11:29:40 | 2020-05-05 10:25:00 | Pass | Replaced smashed basin and pillar tapToilet seat And flush button
MSA-DCS | WA3266417 | Unit 2, D16 - cell window damaged | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 04 May 2020 | 2020-05-05 11:38:14 | 2020-05-05 14:30:00 | Fail | WINDOW & OBS PANEL REGLAZED, DOOR REPAIRED
MSA-DCS | WA3266443 | Unit 1 Control Kitchen - Water filter unit is leaking onto floor | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 12:02:00 | Pass | Removed internal filter due to leak , replaced with new capex asset - external maxi scale filter system . Dry machine and all ok
MSA-DCS | WA3266464 | Unit 4, control room - water filter to sink not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 13:00:00 | Pass | There was no filter water tap as for there is nothing wrong
MSA-DCS | WA3266495 | sallyport back of assessments - faulty light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 10:00:00 | Pass | Replaced light
MSA-DCS | WA3266516 | All areas, pump house - no domestic water/VSD faulty SITE COST | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 04 May 2020 | 2020-05-04 16:25:47 | 2020-05-05 04:00:00 | Fail | Removed and installed new vsd in pump house. Reset alarms on power shut down on 5/5/20
MSA-DCS | WA3266529 | All areas, pump house - no domestic water/VSD faulty SITE COST | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 04 May 2020 | 2020-05-04 16:32:21 | 2020-05-04 15:00:00 | Pass | Check Pumphouse, VSD has failed. Switch prison over to mains water supply by RPZD, Isolate the Ring main and flush system by RPZD outside the laundry. De-isolate ring main and test.
MSA-DCS | WA3266648 | Monitor room - MDAS displaying fault notification on monitor | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 13:12:59 | 2020-05-04 15:30:00 | Pass | Attended site checked and found TR 7 Receiver Fence line south of shade house was showing fault on MDAS. checked the receiver locally and measured the power voltage and data line voltage are ok. Clean and dry up the receiver enclosure. Tested all ok after work.
MSA-DCS | WA3266655 | Monitor room - camera 37 no vision | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 13:18:17 | 2020-05-12 13:34:00 | Fail | job to be invoiced at cost.
MSA-DCS | WA3266658 | Monitor room - controller 1 to 6 are offline | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 May 2020 | 2020-05-04 17:20:44 | 2020-05-05 10:45:00 | Fail | Replace damage 8 input expansion board, rectified and fixed off line controller, configured the admin 1 controller. Job completed.
MSA-DCS | WA3266715 | Roof is leaking - Just inside the front door and | Midland (North East Metro) | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 04 May 2020 | 2020-05-04 17:35:52 | 2021-02-25 10:00:00 | Fail | MULTIPLE LEAKS/ VISITS - BOX GUTTERS REPAIRED, FLASHING REPLACED, LEAKS SESALED
MSA-DCS | WA3266735 | kitchen pot wash taps broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-14 13:00:00 | Fail | COMPLETED
MSA-DCS | WA3266749 | Make sure everything is operational following the VSD replacement | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 May 2020 | 2020-05-05 13:57:24 | 2020-05-04 18:00:00 | Pass | Ensure Pumphouse is operational and does not over pressurised during the VSD replacement.
MSA-DCS | WA3266821 | ODP, Room 1- above desk light is flickering non stop | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 15:00:00 | Pass | Repaired faulty lights in odp room 1
MSA-DCS | WA3266832 | PTZ 5 camera is out of focus when it is 12 x magnification and below | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-05 15:00:00 | Pass | Checked PTZ 5 found image blurry, auto focus not connecting image. Rebooted camera, confirmed image has restored.
MSA-DCS | WA3266864 | Canteen, goods store - roof leak | Wandoo Rehabilitation Facility | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 04 May 2020 | 2020-05-05 14:43:15 | 2020-05-22 10:00:00 | Fail | ROOF REPAIRED, PATCHED & PAINTED
MSA-DCS | WA3266892 | Unit 2, Day Room, A & B side over the stairs - Roof leak | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Schlager Construction Group | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-09-24 11:51:00 | Fail | Attended site and assessed what repairs where required.Due to height and pitch EWP required to carry out these works safely. BRAF Submitted and Works have been declined.
MSA-DCS | WA3266898 | Main Kitchen- Circuit white fix is tripping & wont reset | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 04 May 2020 | 2020-05-05 15:05:14 | 2020-05-05 10:00:00 | Pass | Reset and tested power in kitchen
MSA-DCS | WA3266909 | Level 9 WSQ -meeting Rm 9.4 –globe blinking. | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 13:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3266915 | Unit 9, Staff Lunch Room - Zip Tap not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 09:17:00 | Pass | Unit 9 zip hydrotap was working on arrival. Both tanks taking a long time to fill. Filter was almost completely blocked and causing system to go in and out of faults. Returned to car to get correct filter. Replaced filter, flushed and reset counters. Further tests, normal operation
MSA-DCS | WA3266937 | Unit 10, Cell A4 & A5- Sinks keep blocking up | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 15:38:00 | Pass | Food and hair build up in traps and drain
MSA-DCS | WA3273481 | Replace faulty keys for Programmed Store at Casuarina | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 04 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 12:05:00 | Pass | Job completed - Supply only Gen 6 B restricted keys
MSA-DFES | WA3266110 | Applied training grounds - on the intermediate pad – storm water grate rusted through | FESA RHQ - Forrestfield | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-06-03 14:00:00 | Fail | Works are now completed and the new grate is installed - refer to photo's attached
MSA-DFES | WA3266131 | Front sliding gate- not opening or closing correctly | CFRS Canning Vale | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-04 14:15:00 | Pass | Found gate staying open, not closing. Checked PE beams and loop detector working fine. Nomechanical issues found with gate. reset operator and gate started working properly. Carried outfull test of operation ok. Suspect access control issue! If issue reoccurs then access people willhave to attend.
MSA-DFES | WA3266982 | Electric fence engerizer not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-22 14:30:00 | Fail | Complete
MSA-DTAG | WA3265952 | cameras not working - no visual | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 04 May 2020 | 2020-05-04 11:58:43 | 2020-05-04 11:30:00 | Pass | Reset switch on Level 9. Checked all work stations. CCTV all OK.Job completed.
MSA-DTAG | WA3265969 | Unable to open doors remotely via unison at DMJC and SAT. | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 04 May 2020 | 2020-05-04 12:04:58 | 2020-05-04 10:30:00 | Pass | Reset switch on Level 9. Switched Pacom to standby server. Checked CCTV and Access Control, all OK.
MSA-DTAG | WA3266238 | Ceiling light in Justice Mazza’s Chambers has failed | Supreme Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-04 10:25:00 | Pass | Replaced faulty lamps to justice mazza chambers
MSA-DTAG | WA3266254 | level 4, plantroom - Lightings in south/west plantroom have failed | Supreme Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-04 11:25:00 | Pass | Replaced faulty blown lamps in plantroom
MSA-DTAG | WA3266398 | 1903, External - Security unable to see vision on Extrnal PTZ Camera due to dirt build up | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 14:00:00 | Pass | Cleaned cameras 6, 49, 85 & 99 as requested by client
MSA-DTAG | WA3266644 | Ground floor front doors sensor is not working properly, doors opening but not closing | Perth Children's Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-07 15:02:00 | Fail | Found door working on arrival. Plant stood by door sensor that would move when the wind blew through the doorway is likely causing reactivating on of door. Moved plant away and tested. Door controls are very old, track wheels heavily worn, floor guides lose and need replacing. Drive chain and motor sprocket heavily worn causing chain to slap and doors to judder in closed position occasionally. Recommend 301 power train. Very large aluminium doors to be lifted off to replace guides and track wheels. Door operation ok short term. Braf is being raised
MSA-DTAG | WA3266683 | 1987 Building - Sheriff's Office lights in basement storeroom not working | Supreme Court | WSM-BR-SITE | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 07:15:00 | Pass | Inspected lights in sheriffs office store and replace blown lights in hallways
MSA-DTAG | WA3266904 | Basement - Door closer has detached from frame – aluminium door leading to underground car park | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 14:00:00 | Pass | Door closer adjusted
MSA-DTAG | WA3266917 | Level 10 - Faulty light in male staff toilet | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 09:15:00 | Pass | Job complete
MSA-DTWD | WA3265962 | A Block west, ground level - East auto external door not functioning correctly | Joondalup Kendrew Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-04 12:11:00 | Pass | Found that the mode switch was faulty and has caused the unit to fail, replaced faulty switch and tested, all ok.
MSA-DTWD | WA3266123 | Block C Childcare broken window to the staff office | Rockingham Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 0 | CLOSE | 04 May 2020 | 2020-05-04 13:25:02 | 2020-05-04 14:21:00 | Fail | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-990 X 553
MSA-DTWD | WA3266211 | North Block, Plant Room- Anodes to chiller 3 faulty | Perth Campus B1 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-14 11:22:00 | Fail | PICK UP REPLACEMENT END PLATE GASKETS FOR CHILLER 1,2 AND3. PICK UP REPLACEMENT ANODES FOR CHILLER 3. SIGN IN AND COMPLETE TAKE 5. REMOVE PLUGS FOR ANODES. SUPPLY ANDINSTALL 7 NEW ANODES INTO CHILLER 3 CONDENSER END PLATES. CHECK FOR LEAKS WHEN CHILLER IS RE FILLED OK. COMPLETE PAPERWORK.
MSA-DTWD | WA3266289 | A block East. Gutters on South side are leaking causing eaves lining damage | Joondalup Kendrew Campus | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-07-02 11:00:00 | Fail | Box gutter install and eave repairs as per BRAF works and CSS attached
MSA-DTWD | WA3266321 | C Block, level 1, staff room A116 - door card reader not working it was replaced on the 05/02/20 | Munster Campus (ACEPT) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-19 15:00:00 | Fail | 04/05/2020, 1530-1605Re terminated wiring and tested card reader for C-Block Level 1 staff room, A116 door15/05/2020, 1500-1545Report of card reader C Block Staff room not workingTested card reader Working okCable tested ok.No equipment fault found with cable or reader.19/05/2020, 1355-1500Issue is that the door sometimes fails to openInvestigation shows that the reader does read the card but sometimes the data reported is corrupted and does notmatch system data and therefore does not open the door.Reader in question is for door 39.Door is connected to a 4 door controllerRebooted door controllerBatteries on door controller tested ok.Initialised (defaulted) door controller and downloaded programming.Issue still evident.Concluded the data is getting corrupted between the reader and the door controller. This could be due to a cable fault ordue to cable getting induction from electrical sources whcih corrupts the data.Recommend recable.Client however opted to have the
MSA-DTWD | WA3266373 | E Block, E36 Pantry Store – Exhaust fan not running | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 12:30:00 | Pass | Job completedAwaiting return of signature slip via email due to covid 19
MSA-DTWD | WA3266475 | Museum building- Rodents in building | Perth Campus B7 | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 12:40:00 | Pass | Baited for rodents with 14 ditrac blocks
MSA-DTWD | WA3266720 | M Block, Male Toilet- Leaking toilet | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 15:59:00 | Pass | Tried repairing cistern, needs replacing
MSA-DTWD | WA3266752 | F Block, Room FT02 - Water dripping down walls above windows. | Carlisle Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-06-03 18:00:00 | Fail | Rusted box Gutter removed and new one installed
MSA-DTWD | WA3266754 | A Block Admin Office bad roof leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 0 | CLOSE | 04 May 2020 | 2020-05-04 17:51:38 | 2020-05-05 11:30:00 | Fail | A Block, outlet insufficient to cope with deluge of water, removed fascia board and added new overflow outlet at opposite end to oultlet
MSA-DTWD | WA3266790 | A block, Room AF20- Air conditioners not heating | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 04 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 15:00:00 | Pass | Arrived on site signed in and checked in with Karina. Inspected heater locations. Picked up required ladders from supplier, returned back to site sorted access, gathered tools and equipment assisted by dave, checked Heater Banks and relays. Two Banks not accessable due to location over sealed ceiling areas. Checked all control's, report to be completed. Cleaned up and returned ladders back to supplier. Completed paperwork and signed out.
MSA-DTWD | WA3266796 | A block, Room AF20- Wooden frame window leaking into lecturer area | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-07-27 13:30:00 | Fail | Installed marine Ply at site request and painted
MSA-DTWD | WA3266810 | A Block Admin Office check electrical circuits due to water leaks | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 07:45:00 | Pass | Inspected power in admin. No water ingress safe to use. Job completed
MSA-DTWD | WA3266833 | M Block - roof leaking in variuos areas | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 13:30:00 | Pass | M Block, downpipe blocked and second roof dish charging into same gutter, unblocked gutter and modified outlet from 2nd roof to reduce water flow and seal around apron flashing split-resealed
MSA-DTWD | WA3266837 | P Block - Roof leaking in P021,P022 & P023 | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 16:30:00 | Pass | Installed small flashing to stop water washing over box gutter -box gutter not coping with the volume of water - leaks at expansion joint if persists maybe join box gutter.
MSA-DTWD | WA3266841 | M Block - Fire alarm fault due to roof leak im M Block. | Balga Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-26 15:30:00 | Fail | Reattended site and replaced conventional smoke and remote with new.1x ampac conventional smoke1x ampac remote
MSA-DTWD | WA3266842 | C Block, Room CG10- Door Closer broken- further details below | Carlisle Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-05 16:30:00 | Pass | Repaired door closer. Job complete.
MSA-DTWD | WA3266879 | M block - Check lighting and electrical circuit due to water leaks in M Block passageway | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 10:06:00 | Pass | Inspected water ingress to M block corridor. Lights and power not efffected. Job completed
MSA-DTWD | WA3266880 | P Block Check lighting and electrical circuit due to water leaks in P021,P022 & P013 | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-05 09:41:00 | Pass | Isolated lights which are water effected in P022. Checked others areas in P block all safe to operate power and lights. Job completed
MSA-DTWD | WA3266891 | Stores and painting area - water leaks | West One Services | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-06-09 12:15:00 | Fail | Supply and install 4 x fibreglass skylights to replace existing
MSA-DTWD | WA3266981 | damaged bike shed door | West One Services | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-06 10:15:00 | Fail | LOCATION - 1 PROSPECT PLACE, WEST PERTH.06.05.20 - ATTENDED SITE, CARRIED OUT REPAIRS TO ONE (1) ROLLER DOOR,REINSTALLED CURTAIN INTO GUIDES, LUBRICATED DOOR, CHECKEDOPERATION, ALL OK.
MSA-DTWD | WA3267019 | P Block Carpets in rooms P021,P022 & P023 need drying due to roof leaks | Balga Campus | GMP-BR | Cleaning | Cleaning (CL) | Workzone Pty Ltd | 1 | CLOSE | 04 May 2020 | 2020-05-05 17:00:00 | 2020-05-06 15:00:00 | Fail | Removed water from carpets, blowers left onsite overnight to dry carpets.. Returned following day to clean carpets and dry again.
MSA-MRWA | WA3266189 | L5, 549 - please inspect & rectify light fitting next to window above craig sheltons work station | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 08:05:00 | Pass | Repalced faulty tube and starter. Job completed
MSA-MRWA | WA3266509 | External toilets - Investigate odour and report or remediate in and around external portable toilets | Office and Warehouse-Malaga | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 10:52:00 | Pass | No visible signs of cracking pipes or seals around the plumbing fixtures. Cleared kitchen gully(there wasn’t just water sitting there), siliconed around the pan collars and tightened all the screw caps on sewer pipes around the container. Tightened traps nuts at the urinal and 2x basins. Wall behind the urinal and the floor have stains which I believe it’s urine and it smells as well.
MSA-DCA | WA3267814 | Rat infestation in the cleaners store, please eridicate | Perth Cultural Centre Precinct - Cleaners Store and Distribution Room | GMP-BR | Pest Control | General Pest (PC) | Allpest WA | 0 | CLOSE | 05 May 2020 | 2020-05-05 14:11:08 | 2020-05-05 11:30:00 | Pass | Triple baited existing empty box and added a second box to the store area.
MSA-DCA | WA3267910 | Kitchen - Lift has stopped working | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-Tea Prep Room - East Side | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 15:58:00 | Pass | Lift 1 Art-Geared :Lift stopped on middle floor, doors jammed half way open, powered down, still jammed (mechanically), requires 2 people to lift brake to next floor to further investigated, shut lift down and informed Building manager.To be closed out at $0
MSA-DCA | WA3268610 | level 1, Conservation lab - Water leaking from ceiling/roof in Conservation lab | Shipwreck Galleries-Main Building-Level 1-Laboratory - West | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 05 May 2020 | 2020-05-06 17:00:00 | 2020-06-10 13:15:00 | Fail | Attended site and located leak, unable to access the roof due to inclement weather. Will need to return when weather permits to complete inspection/repair24/7 - No further leaks reported. Job completed
MSA-DCA | WA3269227 | Level 4 Plant Room - flame failure alarm on boilers | Art Gallery of WA - James St-Main Building (Block B)-Level 5 - Roof-Pump Room - Next to Diesel Generator | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 05 May 2020 | 2020-05-06 03:13:56 | 2020-05-06 01:28:00 | Pass | Arrived to site.Checked in with Security.Shown location of plant on level 4.Found Boiler 2 in fault.Reset flame failure.Fault cleared and system back online.Advised security of findings.
MSA-DCS | WA3267244 | Karnet Prison Farm - Kitchen - SITE COSTED Power is tripping out in the new kitchen office. | Karnet Prison Farm-Main Complex External Area | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 05 May 2020 | 2020-05-05 09:51:15 | 2020-05-05 08:00:00 | Pass | P0 call outInvestigate and repair fault tripping rcd in kitchen office
MSA-DCS | WA3267416 | Reception Water coming in from louvers above X ray machine | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 05 May 2020 | 2020-05-06 07:26:43 | 2020-07-30 14:30:00 | Fail | ROOF REPAIRS TO AREA TO ALLOW LOUVERS TO OPEN AND CLOSE WITHOUT CATCHING ON FLASHING AND FRAMEWORK.
MSA-DCS | WA3267460 | construstion office A/C keeps tripping the power | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 May 2020 | 2020-05-11 17:00:00 | 2020-05-21 15:30:00 | Fail | Installed new wms aircon in construction office. All operational at time of departure.
MSA-DCS | WA3267503 | Kitchen - roof leaking in dry store | Wooroloo Prison Farm | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 05 May 2020 | 2020-05-05 12:13:21 | 2020-07-27 10:13:00 | Fail | REPAIRED WITH NEW BOX GUTTERS
MSA-DCS | WA3267549 | Kitchen Brat Pan burners rusty | Wooroloo Prison Farm | SPA-GR | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-06-03 12:00:00 | Fail | Kitchen Brat Pan burners rusty. Check burners, order new parts. Pick up burners. Return, dismantle pan, remove faulty burners, and install new parts. Assemble & test.
MSA-DCS | WA3267556 | A side dishwash area roof leaking | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 13:00:00 | Pass | located leak and rectified
MSA-DCS | WA3267566 | ODP, room 1 (Sentence Planning) - Fluro tube flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-06 09:30:00 | Pass | Repaired faulty lights in Odp
MSA-DCS | WA3267574 | Visits area, visits Non contact area - booth 5 non-contact was giving off a loud feedback sound | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-06 15:17:00 | Pass | Attended site, repaired intercom faults and tested OKJob CompleteParts:Consumables
MSA-DCS | WA3267588 | Unit 14, - B/D bottem landing mop storage hot water tap doesn't turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 16:00:00 | Pass | Remove and replace 1 X quarter turn spindle in hot tap in cleaners store
MSA-DCS | WA3267601 | A wing rear grille - lock is not working | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 05 May 2020 | 2020-05-06 08:47:46 | 2020-05-05 14:15:00 | Pass | Lock adjusted and frame strike adjusted
MSA-DCS | WA3267605 | rear door to medical - door lock not working | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 05 May 2020 | 2020-05-06 08:49:57 | 2020-05-05 14:45:00 | Pass | adjusted lock and handles on Rear door to medical
MSA-DCS | WA3267608 | entry building sallyport door - GRUB screw to pull handle | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 05 May 2020 | 2020-05-06 08:51:18 | 2020-05-05 15:15:00 | Pass | New thread tapped into handle and new grub screw fitted
MSA-DCS | WA3267614 | INF, B wing, Cell B4 - Toilet button getting stuck | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 12:00:00 | Pass | Remove corrosion buildup from push button assembly, reinstall and test.
MSA-DCS | WA3267634 | Y point pond pump contactor faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 13:00:00 | Pass | Investigate Y point pond contactor. Contactor requires replacement
MSA-DCS | WA3267693 | unit 5, Control - Ventilation system showing fault on panel | Hakea Prison | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-13 12:30:00 | Fail | Replaced pressure switch and housing. All operational at time of departure
MSA-DCS | WA3267854 | Psych Services Hallway & Stat Office- Foul smell coming from ceiling above various rooms | Walcott Centre (Central West Metro ) | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 12:05:00 | Pass | 6 odour bags placed between 2 office areas
MSA-DCS | WA3267917 | Kitchen Highbay light above blast chiller not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-06 12:00:00 | Pass | Repaired light
MSA-DCS | WA3267930 | Unit 4 - Staff toilet leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 10:00:00 | Pass | Remove and replace faulty Inlet valve and test.
MSA-DCS | WA3267942 | Edvoc 1, Class 2- Light not working suspected ballast | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-13 14:00:00 | Fail | Repaired one light Edvoc 1, Class 2
MSA-DCS | WA3267977 | Unit 8, A Wing- Wing light ballast is damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 13:00:00 | Pass | Repaired light
MSA-DCS | WA3267979 | Unit 10, Cell C2- Leaking tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 11:38:00 | Pass | adjusted pressure to sink and cleaned filter
MSA-DCS | WA3267993 | Unit 10, A & B cleaning cupboard - Leaking tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 10:35:00 | Pass | Pulled apart dripping tap and replaced washer and valve
MSA-DCS | WA3268029 | Unit 2, Cell B6- Sink is broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 May 2020 | 2020-05-06 11:45:01 | 2020-05-06 10:30:00 | Pass | Removed broken basin reinstalled new one
MSA-DCS | WA3268075 | second floor, flight of stairs - round lights faulty/flashing | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 14:00:00 | Pass | Replaced faulty lamps on stairs
MSA-DCS | WA3268098 | Unit 4, Control room- Network error on cell call system | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-05 16:46:00 | Pass | Investigated fault, checked all systems, traced fault to new construction unit. Other contractors are currently upgrading system.Job Complete
MSA-DCS | WA3268243 | Laundry - low water pressure | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 13:30:00 | Pass | COMPLETED
MSA-DCS | WA3268535 | Rear Yard Office Camera has gone down | Broome Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 May 2020 | 2020-05-06 13:54:42 | 2020-05-09 08:11:00 | Fail | Re terminated RJ45 plug camera input to PoeTested ok
MSA-DCS | WA3268599 | Unit 1, POD 2, Kitchen - hot water is leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 May 2020 | 2020-05-06 14:13:45 | 2020-05-07 14:30:00 | Fail | Complete
MSA-DCS | WA3268608 | PE Beam is constantly activating | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 05 May 2020 | 2020-05-05 18:17:38 | 2020-06-08 11:30:00 | Fail | Realigned all 6 pairs of PE Beams in Ed Voc Area. Tested ok.
MSA-DCS | WA3268627 | ISU B Wing - Camera 5 is not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 May 2020 | 2020-05-06 14:32:35 | 2020-05-06 09:00:00 | Pass | Attended site and checked camera video feed from gatehouse and all checked ok. Attended ISU unit and reset camera from comms cupboard and testedbwith video monitor. All tested ok, monitor showing correct video feed. Job complete
MSA-DCS | WA3268632 | Unit 2,D Wing, Cell D13 - Window is damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-14 10:30:00 | Fail | RENEWED SPIRAL BALANCES
MSA-DCS | WA3268637 | Education 2, Class 3- Smashed window on entry door approx 650x650 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 12:30:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3268758 | Unit 6, A10 - Outlet washer required as faulty/damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 09:32:00 | Pass | Replaced outlet washer
MSA-DCS | WA3268877 | Unit 6, A19 - Outlet washer required as faulty/damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 08:30:00 | Pass | Replaced outlet washer and inlet valve
MSA-DCS | WA3269040 | PC S Office - water coming through ceiling | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 05 May 2020 | 2020-05-06 15:08:53 | 2020-06-12 13:03:00 | Fail | located leak and rectified
MSA-DCS | WA3269098 | Main building- section of roof flashing has come off due to winds | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 05 May 2020 | 2020-05-06 16:03:43 | 2020-05-06 06:45:00 | Pass | located leak and rectified
MSA-DFES | WA3267864 | Front sliding gate- not opening or closing correctly, may need reprogramming | CFRS Canning Vale | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 1 | CLOSE | 05 May 2020 | 2020-05-06 17:00:00 | 2020-06-03 13:42:00 | Fail | 05/05/2020, 1315-1345Could not program opening time for front gate, couldn't access Gallagher panel and onsite laptop is dead. Station OfficerTony Nicholas wants this rectified as soon as possible.14/05/2020, 1050-1205 (two technicians)Confirmed the following;1. Vehicle gate open close and times are controlled by the Gallagher system2. Intercom at gate is connected to the Gallagher system as egress input3. Neatrol keypad is connected to the Gallagher system as egress input.Issues onsite.1. Gate open close timing.i. Gallagher software laptop does not turn on.- found laptop battery faulty, preventing turn on. Replaced battery, laptop now operating correctly.ii.. Once laptop operational reset Gallagher system clock and changed gate open close times as directed by BruceJohnston to open between 700 - 805 and 1700 - 1805.iii. gate timing now correct.2. Intercom systemi. intercom confirmed as operating the gate open function correctly.ii. gate station unit needs replacing as
MSA-DFES | WA3267956 | Main Workshop- lighting issues in the below locations | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-06 11:00:00 | Pass | Arrived onsite and signed in. Located wash bay and light circuit had tripped RCD. Reset RCD and tested circuit including security light on PE cellon side of shed. Circuit stayed on and couldn’t replicate fault. Found broken corrugated conduit in wash bay pit, no water in light but replaceconduit between lights, glued and siliconed. Siliconed around PE cell and cable entries for security light and PE on side of shed. Let circuit runwhile completing another job and fault didn’t reoccur. Informed staff of work completed.
MSA-DFES | WA3269133 | Plant Room - Smoke detector faulty | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 18:30:00 | Pass | Investigate fault on panelFaulty detector in plant roomReplaced detector with newReset Panel
MSA-DFES | WA3298612 | Retrospective WO - ZONE 41 MRS ENTRY 2 DOOR - attended 05/05/2020 17:43 | VFRS Mandurah | GMP-BR | Security | Guards (SE) | Securex Security Systems & Services | 1 | CLOSE | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 18:03:00 | Pass | ZONE 41 MRS ENTRY 2 DOORINTERNAL & EXTERNAL CHECK CARRIED OUT. ALL APPEARS SECURE. NO OFFENCE DETECTED. NO OFFENCE DETECTED. STAFF ONSITE. OFFICER LIITIGINER #031810 PANEL RESET AND MONITORING ADVISED - KYE
MSA-DTAG | WA3267631 | Lvl 3, Court 37, Flickering light | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-08 08:30:00 | Pass | Job complete
MSA-DTAG | WA3267687 | Lvl 15, Foyer- Slide door wont open when button pressed | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 16:00:00 | Pass | Job completed - tested Rex Button at Level 15 Sliding Door, found it to be working ok.
MSA-DTAG | WA3267706 | Level 2, Sheriffs office - Front doors continually malfunctioning. | Supreme Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 05 May 2020 | 2020-05-05 13:25:02 | 2020-05-05 12:01:00 | Pass | The law library entrance. Found left hand door leaf dragging and jamming in floor. In order to raise door leaf the aluminium packers needed to removed. Straightened out left hand belt bracket that was found to be jamming in the tormax win drive lock mech. Tested battery pack. Cleaned and tested safety beams. Reduced motor open and closed forces and speeds to prevent too much door twist. Operation ok.
MSA-DTAG | WA3267903 | Lift #3 - the doors of the lift are opening and shutting | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 15:17:00 | Pass | Car doors occasionally cycling found damaged car hanger roller. Sourced and replaced hanger roller for car door (left handfront).Lift back in service
MSA-DTAG | WA3268228 | mutiple faulty lights (please see see notes for loactions) | Rockingham Justice Complex | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 12:15:00 | Pass | Replaced faulty lamps and light fittings in corridoors toilets and courtrooms
MSA-DTAG | WA3269086 | G Floor, Public toilets- No hot water | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 11:00:00 | Pass | Replaced rheem 80lt storage electric HWU, also installed and tested new tempering valve for unit
MSA-DTWD | WA3267547 | B block, Level 2, Female Toilet - Basin leaking below sink | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 12:30:00 | Pass | Complete
MSA-DTWD | WA3267746 | A Block, 1st Floor, Room AF2.14- Billi unit not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 12:43:00 | Pass | Replaced faulty dual solenoid BILLI QUADRA A402010365REPLACED SOLENOID LOCATED MARITIME L1 EXEC KITCHEN.
MSA-DTWD | WA3267763 | 6, Painting and Decorating, ground level,Passage way north entrance - faulty lights | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 13:42:00 | Pass | Removed faulty un required light. Was advised by site to remove and make safe. Completed
MSA-DTWD | WA3267984 | E Block, Room E201- Fridge door seal is damaged | Mount Lawley Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 09:00:00 | Pass | Attended site and found small drinks fridge inside room e201 to have its door seal to have poped out of the groove,re fitted door seal into groove and tested operation and seal function.left all ok
MSA-DTWD | WA3267999 | O Block, Storeroom/workshop- Roof Leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 15:00:00 | Pass | O Block, 2 leaks rear into store shed, found blocked downpipe, lifted sheets and found broken seal in box gutter, resealed, leak over roller door and blocked downpipe and broken seal where one gutter discharges into another. resealed
MSA-DTWD | WA3268051 | F1 office - Roof leak around extractor system penetration next to sink in the office | Murdoch Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-08 13:30:00 | Fail | Located leak and sealed with roof and gutter silicone
MSA-DTWD | WA3269092 | M Block, Roof leak in office M18 down internal window. | Bentley Campus | GMP-BR | Roofing | Tiled Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 05 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 10:30:00 | Pass | Works are now completed - Please see photos attached
MSA-DTWD | WA3269109 | A Block, Room AT04A- 1st cubicle toilet is leaking | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-05 17:32:00 | Pass | Repaired cistern
MSA-MRWA | WA3267494 | Level 7, 708 - flickering light, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 10:30:00 | Pass | Replaced tube with new
MSA-MRWA | WA3267529 | Level 7, 716 - flickering light, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-05 10:30:00 | Pass | Replaced tube with new
MSA-MRWA | WA3267659 | Lvl 6, 3rd cistern from door has a “dripping sound” inside cistern. Please investigate & remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | MR - Handyperson - PFM | 1 | COMP | 05 May 2020 | 2020-05-06 17:00:00 | 2020-05-06 10:29:00 | Pass | Found leak internally will need plumber to fully repair
MSA-MRWA | WA3268634 | Level 2, L2.163 adjust monitor arms as per user request. | Road Network Operation Centre (RNOC) | GMP-BR | Furniture | Indoor Furniture (FU) | MR - Handyperson - PFM | 2 | COMP | 05 May 2020 | 2020-05-08 17:00:00 | 2020-05-06 15:31:00 | Pass | Adjusted monitor arms for occupant
MSA-DCA | WA3269871 | Laundry room - HWS leaking | His Majesty's Theatre-Theatre Building-Level 1-Laundry Area | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 12:15:00 | Pass | Found 25lt storage HWU to be cracked and leaking water when under pressure, must be replaced under warranty
MSA-DCA | WA3269949 | Corporate Office (under Nathan & Kens Desk) 2 x Power points are damaged & unable to receive a plug | His Majesty's Theatre | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 13:30:00 | Pass | Assessed damaged gpos on level 2. Isolated and tested then replaced with new gpos and mounting blocksTested and labelled accordingly.
MSA-DCA | WA3270251 | Foyer/Box Office Dirty smoke detector in the Box Office area: M4-190 | State Theatre Centre (Heath Ledger Theatre) | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Critical Fire Protection & Training | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-29 15:03:00 | Fail | Tech attended
MSA-DCS | WA3269658 | 4 PTZ Camera's 28, 29, 35& 36 have vision but not moving | Boronia Pre-release | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 May 2020 | 2020-05-06 11:37:12 | 2020-05-06 12:40:00 | Fail | Travelled to Boronia Prison, found PTZ cameras 28, 29, 35, 36 with no PTZ functions, checked individual cameras ok. PTZ functions are available within indigo software but unable to be controlled via indigo keyboard / joystick. Traced issue to workstation (video wall) running extreamely slow, reset workstation conducted cleanup and de fragmentation and ran workstation with indigo software running at full capacity whilst utilising server monitor software. System appears to be functioning correctly without any failures and keyboard / joystick functions have been restored. No further action is required at this time.
MSA-DCS | WA3269676 | External light pole in zone 18 has fallen over | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 06 May 2020 | 2020-05-06 11:48:29 | 2020-05-06 15:00:00 | Fail | Zone 18 Perimeter light down, rethreaded bolt hole, hire boom and got pole back up. Replaced 2 x light covers
MSA-DCS | WA3269692 | Unit 2 Control Main announcement intercomm not working | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 May 2020 | 2020-05-07 07:57:57 | 2020-05-06 12:00:00 | Pass | Attended site and found buttons on unit 2 3210 not working. Reset main power and retested voltage levels. All tested ok and all reset ok. All systems working correctly. Job complete
MSA-DCS | WA3269701 | Unit 1 A Wing Shade Sail post has snapped off at the base | Bandyup Prison | GMP-BR- HO | Building | External Walls (BU) | Schlager Construction Group | 2 | CLOSE | 06 May 2020 | 2020-05-08 17:00:00 | 2020-08-04 13:45:00 | Fail | Attended site, and quoted works.
MSA-DCS | WA3269721 | Unit 7, E6 - Roof leaking, water dripping on to upper bunk | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 06 May 2020 | 2020-05-07 08:01:13 | 2020-06-19 13:04:00 | Fail | BOX GUTTER RUSTED AREA REPLACED
MSA-DCS | WA3269768 | Unit 1, C3 - Vesda Burnt in fire | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 May 2020 | 2020-05-07 08:27:07 | 2020-05-07 08:04:00 | Pass | Installed new sampling point as requested
MSA-DCS | WA3269773 | Unit 1, B7 - Vesda Burnt in fire | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 May 2020 | 2020-05-07 08:29:40 | 2020-05-07 08:10:00 | Pass | replaced burnt sampling point
MSA-DCS | WA3269796 | Hotham, A5 - Window leaks | Wandoo Rehabilitation Facility | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-06-12 11:00:00 | Fail | DOUBLE UP OF WA3357263 - COMPLETED
MSA-DCS | WA3269811 | Unit 2, D8 - Faulty cistern, still running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 11:00:00 | Pass | Replaced faulty outlet rubber and test.
MSA-DCS | WA3269847 | Farm - 2 sheds have sheeting damage | Wooroloo Prison Farm | WSM-BR-SITE | Building | External Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-07-02 14:00:00 | Fail | NEW ROOF SHEETS INSTALLED
MSA-DCS | WA3269852 | Reception roof leaking in MPC Foyer & storeroom | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-06-12 13:05:00 | Fail | located leak and rectified
MSA-DCS | WA3269855 | Kitchen dishwash machine B side faulty | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 11:00:00 | Pass | B side Dishwasher faulty not starting. Check washer & controls. Dismantle, repair inlet water supply line, clean out, rinse jets. Drain tank to clear pressure switch. Assemble & test.
MSA-DCS | WA3269861 | Unit 3, A Wing, Between cells 3 & 4- roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-06-12 13:04:00 | Fail | located leak and rectified
MSA-DCS | WA3269888 | Unit 13, Cell D9- Blocked toilet, drains but very slowly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-08 09:00:00 | Pass | Plunge toilet to clear blockage. Test several times.
MSA-DCS | WA3269896 | Switchboard area- Blown fluro glove above switchboard | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 11:30:00 | Pass | Repaired faulty lights in admin switchboard area
MSA-DCS | WA3269906 | Ground floor, reception and managers office desk area - Camera system, unable to access login error | Welshpool | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 May 2020 | 2020-05-07 09:10:30 | 2020-05-06 11:24:00 | Pass | Recovered indigo database then reset camera all came back online and tested ok
MSA-DCS | WA3269907 | Unit 4 - A & C- Entry door on day room, knob is loose | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-06-18 12:30:00 | Fail | New Handle fitted
MSA-DCS | WA3269910 | Unit 3, A Wing - cleaning cuboard leaking pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 08:00:00 | Pass | Inspect all pipework in cleaners closet run all showers but no leak could be found.
MSA-DCS | WA3269914 | Unit 4, Cell D2- toilet cistern button is faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-06 15:30:00 | Pass | Remove excess paint buildup from flush button inside cell.
MSA-DCS | WA3269918 | Administration, Lunch Room - Hot water in tea room is cold | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 12:00:00 | Pass | Inspect hot water service, hot water element has split and requires electrician to replace. Job has been raised for helwigs electrical.
MSA-DCS | WA3269924 | COG skills door has sticky lock(internal door between U12 and COG). | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-15 10:30:00 | Fail | replace handles, lever pack, bolt throw and service.
MSA-DCS | WA3269932 | Textiles front door lock is hard to open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 10:30:00 | Pass | replaced lock, lever pack bolt throw and hinges.
MSA-DCS | WA3269940 | Unit 1, Cell C3- 2x GPO's burnt, not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 10:00:00 | Pass | Replaced gpo
MSA-DCS | WA3269942 | Unit 1, Cell B7- 1 x GPO and light switch damaged | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 08:30:00 | Pass | Unit 1, B7 replaced fire damaged GPO & light switch
MSA-DCS | WA3269945 | Unit 2, D Wing- Floor has vinyl lifting making it a trip hazard | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-10-08 13:22:00 | Fail | SUPPLY AND INSTALLED NEW VINYL FLOORING TO AREA X2
MSA-DCS | WA3269950 | control - PTZ 20 camera not working | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 May 2020 | 2020-05-07 09:25:14 | 2020-05-06 13:00:00 | Pass | Attended Equipment room in Gatehouse and access camera via IndigoVision console. Was able to see video from camera and operate all PTZ functions on camera. No fault found.
MSA-DCS | WA3269951 | Unit 5, B & C Wing- Roof Leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-06-12 12:59:00 | Fail | located leak and rectified
MSA-DCS | WA3269959 | PTZ 8, 9 & 10 & omnitrax lost connection | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 May 2020 | 2020-05-07 09:31:23 | 2020-05-07 14:00:00 | Fail | Travelled to site, attended site and investigated camera faults.Reset PTZ fiber modems and power for 8,9 and 10. All reset and tested ok. Walk tested omnitrax zones and checked all alarms, all activated and cleared correctly. Issue prior possibly related to excess rain throughout the day. Job complete
MSA-DCS | WA3269987 | Textiles prisoners toilet flush pipe rubber leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-08 08:00:00 | Pass | Remove and replace one faulty 50mm flush cone on flush pipe
MSA-DCS | WA3270072 | Remote control for front gate broken and needs repair/ Replace | Karnet Prison Farm | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 11:30:00 | Pass | Supplied and programmed two (2) airkey remotes into the dual swing gate at the Sally port. Test operation, all okay
MSA-DCS | WA3270105 | Unit 6, Cell B2 & B12- Taps are constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-07 13:30:00 | Pass | Remove and replace 1x quarter turn spindle in a Cell.
MSA-DCS | WA3270122 | Unit 2, B Wing- Cleaning cupboard has leaking faucet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-08 10:00:00 | Pass | Remove tap and lock seal thread on spout outlet to seal leak.
MSA-DCS | WA3270132 | Gym - Fluro tube is not working, storeroom north | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-07 11:30:00 | Pass | Repaired faulty lights in gym
MSA-DCS | WA3270224 | Visits playground/Rear Com Rooms 1&3 - Shade sails (x2) damaged by strong o/night winds | Boronia Pre-release-External Area-Ground Floor-Children Play Area - Near Visitor Canteen | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-14 09:15:00 | Fail | shade sail repaired
MSA-DCS | WA3270236 | Unit 1, Zip urn tap is faulty | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 12:30:00 | Pass | Replaced damage tap J11483
MSA-DCS | WA3270245 | Unit 2, A & C Wing- Power point panel detached from wall, wires exposed | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 06 May 2020 | 2020-05-07 10:58:24 | 2020-05-07 08:30:00 | Pass | Replaced damaged gpo blank plate in unit 2
MSA-DCS | WA3270255 | Education building - faulty isolator switch on Hot water unit | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 06 May 2020 | 2020-05-07 11:05:12 | 2020-05-06 14:00:00 | Pass | Replaced damaged isolator switch in education
MSA-DCS | WA3270268 | Unit 1, B wing - Shower door lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-12 14:00:00 | Fail | cut out old lock and install new lock.
MSA-DCS | WA3270300 | Unit 1, Cell B1- Toilet flusher not filling | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 09:30:00 | Pass | Realign push button assembly in cistern in plumbing duct
MSA-DCS | WA3270407 | INF(10)- Cell B1- Window shutter is not closing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-09-01 13:30:00 | Fail | stainless steel vent grill repaired
MSA-DCS | WA3270441 | Staff Toilet adjacent to rear of Industries- Door lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 11:00:00 | Pass | Replaced faulty lock
MSA-DCS | WA3270467 | Cleaning Workshop Stores Roller door not closing | Hakea Prison | GMP-BR- HO | Building | Roller Shutters (BU) | UNIVERSAL DOORS | 1 | CLOSE | 06 May 2020 | 2020-05-07 12:39:37 | 2020-05-11 07:50:00 | Fail | Job completed - ATTENDED SITE, CARRIED OUT REPAIRS TO THE FAULTY ROLLERSHUTTER, REWELDED GUIDE FEEDS, CHECKED OPERATION, ALL OK
MSA-DCS | WA3270534 | Unit 1, Common Areas - Vinyl is lifting | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-08-17 14:22:00 | Fail | VINYL FLOOR & SKIRTING REPAIRS COMPLETED
MSA-DCS | WA3270541 | Unit 1, Exit Doorways both Wings - Vinyl is lifting | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-08-17 14:18:00 | Fail | Flooring repairs completed
MSA-DCS | WA3270543 | Unit 1, Air Lock Areas- Vinyl is lifting | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-08-14 09:30:00 | Fail | Flooring repairs completed
MSA-DCS | WA3270562 | Video links, waiting room - roof leak through ceiling | Bandyup Prison | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-06-19 11:00:00 | Fail | Attended site and carried out repairs to the roof area where it was leaking
MSA-DCS | WA3270565 | PCS 6, assessments area - roof leak through ceiling | Bandyup Prison | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-06-19 14:00:00 | Fail | Attended site and carried out repairs to the roof area that was leaking.
MSA-DCS | WA3270642 | Hakea Training Facility Booster Pump outlet 1219909 (A402573171) cover requires attention | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 10:00:00 | Pass | CH & ALarrived onsite and found cap stuck on booster.isolated and drained booster linemanaged to get cap offfilled system and found booster washer passing which was causing cap to pressurise and not be able to come offdrained line took apart and servicedre assembled and filled systemall ok and working as should
MSA-DCS | WA3270658 | Admin - Hub Room - no power to computer equipment | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 06 May 2020 | 2020-05-06 17:59:58 | 2020-05-06 17:00:00 | Pass | Repair fault on power rail in Admin Comms room
MSA-DCS | WA3270662 | Kitchen, Cool room 3- Fridge in alarm | Banksia Hill Detention Centre | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 10:00:00 | Pass | Complete
MSA-DCS | WA3270672 | Reception Roof louvres above X Ray machine are stuck opened | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 06 May 2020 | 2020-05-07 14:06:43 | 2020-05-07 14:00:00 | Pass | Roof louvres not working , not an electrical issue - let maintenance know
MSA-DCS | WA3270713 | DDU- TV has been damaged due to storm | Hakea Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 11:00:00 | Pass | Job completed - Attended site. Repositioned and secured fallen TV antenna in DDU. Tested signal, OK.
MSA-DCS | WA3270844 | POD - major lag on CCTV systems | Bandyup Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 May 2020 | 2020-05-06 19:53:26 | 2020-05-06 18:30:00 | Pass | Video wall indicating large amount of lagg on cameras streams, checked workstation stats extreamely high, rebooted workstation and tested fully opedational and no longer lagging.
MSA-DCS | WA3270856 | Unit 6, Stores ( old reception showers ) - Roof leaking | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 13:00:00 | Pass | located leak and rectified
MSA-DCS | WA3270858 | Unit 6, North Wing- Lock rusted on LHS door & padlock rusted on metal drop bar & cannot be unlocked | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 13:00:00 | Pass | Forcibly remove rusted padlock and replace.
MSA-DCS | WA3270862 | Unit 7, Cell H2 - Broken light switch | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-07 15:00:00 | Pass | Replaced light switch
MSA-DFES | WA3269396 | Leanned 1300793722 FAMS - Fire panels have gone into No communitiion (No COMS) | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 06 May 2020 | 2020-05-06 08:30:59 | 2020-05-06 15:00:00 | Fail | Investigate panel fault due to power lossChange out drained batteries due to power lossInvestigate generator not powering FIPInvestigate PSU faultRectify
MSA-DFES | WA3269670 | 000 Call Centre - A/C is offline | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Ducted Split System (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 06 May 2020 | 2020-05-06 17:00:00 | 2020-11-12 12:30:00 | Fail | works completed
MSA-DFES | WA3269869 | spare hose store (rear of yard) - lighting isnt working and may have water in the fitting | CFRS Claremont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 12:30:00 | Pass | COMPLETED
MSA-DFES | WA3270192 | No power - 500kva Generator Transportable to be supplied | DFES Cockburn Emergency Services Complex | GMP-BR | Equipment | Compressors, Generators (EQ) | Australian HVAC Services Pty. Ltd. | 0 | CLOSE | 06 May 2020 | 2020-05-06 14:36:00 | 2020-05-06 18:00:00 | Fail | Ring primary generator supplier Coats hire, no available generators. Ring secondary generator supplier Aggreko Organise hire of diesel generator to be delivered straight to site asap. Only available unit is 1250kva that can be dialed down to 500kva. Organise paperwork. Meet generator and delivery truck onsite. Position generator in driveway of complex close to switchboard connections. Leave insight electrical to carry out connection.
MSA-DFES | WA3270195 | Connect transportable generator | DFES Cockburn Emergency Services Complex | GMP-BR | Equipment | Compressors, Generators (EQ) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 06 May 2020 | 2020-05-06 14:41:24 | 2020-05-11 09:15:00 | Fail | Complete
MSA-DFES | WA3270346 | Level 2 - the billie Zip unit, is not working (may have happend after power outage) | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 10:43:00 | Pass | Replaced power/contro pcb,inlet and dual solenoids
MSA-DFES | WA3270393 | Fault coming from Fire Panel | CFRS Vincent | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 13:50:00 | Pass | Power outage due to storm
MSA-DFES | WA3270535 | Between Dorm 4& 5, hot water is evident in the cistern, outside trough & garden hose | CFRS Hope Valley | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-07-14 12:14:00 | Fail | Fit new tmv valves in roof space
MSA-DFES | WA3270582 | Glass sliding door to Gym has large crack | CFRS Hope Valley | GMP-BR | Building | Doors (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-11 11:39:00 | Fail | ATTENDED SITE, REGLAZED BROKEN GLASS TO DOOR 6.38 CLEAR LAMINATED SAFETY GLASS 1 - 1986 X 850MOTIF SUPPLIED AND FITTED
MSA-DFES | WA3270786 | Replace damaged light & siren tower with a suitable pole and re-install lights & siren | VFRS Kalamunda | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 12:30:00 | Pass | Locate faulty tower. Tony advised what they would like to do for a replacement pole. Tony would like to move the location of the pole. Take photos and measurements of the work areas. Take photos of the lights. The light look okay we are assuming they are in working order. The siren works but it is damaged and will need replacement. The siren needs to be high up so it can be heard from as far away as possible. The original tower was around 16 to 20 meters height.
MSA-DTAG | WA3269736 | The intercom on Hay Street is buzzing | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 06 May 2020 | 2020-05-06 12:14:57 | 2020-05-06 09:30:00 | Pass | Reset switch on Level 9. Checked all work stations on all levels
MSA-DTAG | WA3270082 | Lvl 3, Court 37- Light flickering | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 10:00:00 | Pass | Job complete
MSA-DTAG | WA3270159 | Stirling Gardens Complex,1903 Building, Custody Centre- Light tubes not working | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 08:30:00 | Pass | Replaced faulty lamps to custody and hallway
MSA-DTAG | WA3270313 | Custody, Male Change Room - Fluro light not working | Midland Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 15:00:00 | Pass | Replaced tubes and starters for light fittings
MSA-DTAG | WA3270318 | Ground & Level 1- 3x fluro lights not working, locations below | Midland Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 14:00:00 | Pass | Replaced light fittings with LEDs
MSA-DTAG | WA3270452 | Level 16, Operations New door - Staff unable to access room, | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-06-08 12:00:00 | Fail | No access from Card. Area in alarm. Disarm area and program reader to allow access in arm area.
MSA-DTAG | WA3270462 | Family Violence Offices - smell of sewage | Rockingham Justice Complex | GMP-BR-HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-07 09:00:00 | Pass | Complete
MSA-DTAG | WA3270466 | Lvl 12,Entry to Magistrates Chambers-Lights just inside entry door dont come on when swtich turn on | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 12:00:00 | Pass | Job complete
MSA-DTAG | WA3270508 | Entry to central law courts- front revolving door, heavy brush has fallen off | Central Law Courts | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 15:28:00 | Pass | Refitted glazing brush profile back on door. Taped wiring loom to glass. Secured in place with screw to prevent happening again.
MSA-DTAG | WA3270509 | Level 1 Disabled toilets Hot & Cold water taps cannot be closed, water is constantly trickling | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-08 08:30:00 | Fail | Complete
MSA-DTAG | WA3270520 | Door handle screw is missing from Court 7 Judges entry door | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-07 13:30:00 | Pass | SUPPLY & FIX NEW SCREW TO HANDLE
MSA-DTAG | WA3270522 | Several carpet tiles in linked walkway corridor are worn | Supreme Court | GMP-BR-HO | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-08 11:35:00 | Pass | REPLACED WORN CARPET TILES TO STEPS AND WALKWAY
MSA-DTAG | WA3270700 | Ground level (Level 2) Mens toilets - The second toilet is blocked and won’t flush. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-08 16:00:00 | Fail | Complete
MSA-DTAG | WA3270712 | Level 5, Near Court 56 seating area, just around the corner - Hole in wall | Central Law Courts | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-28 09:51:00 | Fail | Wall patched, court painters to paint/wall paper
MSA-DTAG | WA3270764 | Lvl 5, Near court 56- Wall paper is peeling from the panel below 2 water fountains, see below | Central Law Courts | GMP-BR-HO | Painting | Internal (PA) | PPM Project Painting & Maintenance | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-08 16:00:00 | Pass | Repair Wall & Paint
MSA-DTAG | WA3270770 | FIP- Technician required to attend & assist HVAC Saturday 9 May from 07.00am until 15.00pm | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-09 15:00:00 | Pass | WEEKEND WORKS TO ISOLATE AND DE-ISOLATE FIRE SYSTEM FOR HVAC WORKS
MSA-DTWD | WA3269626 | T Block - both lifts are not working, one stuck on 2 and the other on ground | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 06 May 2020 | 2020-05-06 11:14:10 | 2020-05-06 14:30:00 | Fail | Technician found that one of the components had been affected by an external influence. Mains power failure/fluctuation to the equipment was identified . Following our attendance, the equipment was left in service. Works due to external influence are not covered under the terms of your maintenance agreement, therefore this site visit will be chargeable
MSA-DTWD | WA3269738 | Child care - power tripping out | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 06 May 2020 | 2020-05-06 12:14:41 | 2020-05-06 13:30:00 | Fail | Side security light needs replacing with led bunker. Rear flood/ sensor light needs replacing
MSA-DTWD | WA3269792 | Carpark in front A Block lights went out last night during storm | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 14:57:00 | Pass | Attended site and signed in. Located A block carpark. Found lights to be tripped. Investigated to broken light fitting on another work order. Repaired the light fitting and retested circuit. All okay. Carpark lights working fine. Job complete
MSA-DTWD | WA3269831 | Carpark a super large tree has come down due to storm | Mandurah Campus (formerly Peel) | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-06 12:30:00 | Pass | Fallen tree removedLabour 4 staff @ 2.5 hours $1,000Materials chipper truck/chipper, cherry picker 2.5 hours $500Budget $1,000. Actuals $1,500. Claim $1,000
MSA-DTWD | WA3269870 | C block, Room C117- Mouse sighted in room and requires bating | Joondalup Kendrew Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 13:05:00 | Pass | Installed 4 large rodent cardboard boxes and 12 Ditrac Blocks
MSA-DTWD | WA3270040 | H block ground - Retic on back turf has been stuck on, wont allow shut off from control box | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Materials (PD) | WESTERN IRRIGATION PTY LTD | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 11:00:00 | Pass | Locate and replace faulty solenoid valve, test and commission.
MSA-DTWD | WA3270114 | Level 1 - Replace blown/faulty lights as requested | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 11:04:00 | Pass | Repalced multiple fluros out to various locations as requested by site. Resecured hanging light fitting in B6. Job completed
MSA-DTWD | WA3270273 | Grounds security/ walkway pole light, between A & D Blocks the dom has blown off the pole | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-06 14:15:00 | Pass | Dome had been blown off by intense wind. Dome was reinstalled securely and silicon applied to the rim for more support and ingress protection.
MSA-DTWD | WA3270373 | I Block - broken tree branch has damaged the roof and guttering | Balga Campus | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-07 11:45:00 | Pass | Fallen main stem removed. Site cleaned up after mulching.Onsite 10.15 am 07052020. Departed 11.45 am 07052020. Labour 5 staff x $150 = $750. Material Chipper truck and wood chipper $300. Total $1,050.Budget $1,000. Actuals $1,050. Claim $1,000 plus GST
MSA-DTWD | WA3270381 | Block 9, 8F60, Library- Water leak near column | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-20 12:30:00 | Fail | Replaced downpipe with longer section and spreader. No further leaks reported. Job complete
MSA-DTWD | WA3270397 | Block 6, 1st Floor, Vehicle Body Building project store- Water damaged ceiling | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-06-23 15:00:00 | Fail | Have attended site and assessed damage to ceiling. A section of the ceiling will need to be replaced - Will require BRAF preparation 26/5 Attended site to begin works on storeroom ceiling to find the roof leak was still active. Have removed damaged ceiling and will assess roof leak when weather permits 23/6 Sanded joints in gyprock and painted ceiling. Job finished
MSA-DTWD | WA3270403 | Block 6, G Floor- Brick laying pug mill- water leak from down pipe | Thornlie Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-07 10:00:00 | Pass | KPI 2. Attended site and located issue, will need to return in clement weather to resolve.
MSA-DTWD | WA3270414 | Block 10, G & 1st Floor, walkways- no lights at night | Thornlie Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-05-21 10:30:00 | Fail | Replaced all lights. All now working
MSA-DTWD | WA3270419 | Block 2, G & 1st Floor, Lunchroom- faulty light switch | Thornlie Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-07 13:50:00 | Pass | Replaced faulty light switch. All now working.
MSA-DTWD | WA3270423 | Block 1, G Floor- Room 1G32- Faulty door lock | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 14:30:00 | Pass | Lock repaired - Room 1G32
MSA-DTWD | WA3270428 | Car Park 2, Damaged fence panels – 1 panel collapsed and 2 panels fractured | Thornlie Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 06 May 2020 | 2020-05-07 17:00:00 | 2020-06-05 10:45:00 | Fail | Attended site and installed temp fence to secure fence line. Will need to wait for Risk Cover decision regarding fence repairs. Job remains open pending further direction 9/6 Works are now completed - Fence panels collected at client request
MSA-DTWD | WA3270435 | G Floor, 3G1 Metals Finishing room- Faulty door lock | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 14:30:00 | Pass | Lock repaired Room 3G1 - metal finishing room.
MSA-DTWD | WA3270474 | F Block- Workshop door blown off hinges & cant be secured | Naval Base | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 06 May 2020 | 2020-05-06 16:46:03 | 2020-05-28 10:00:00 | Fail | Works are now completed and the door is in working order
MSA-DTWD | WA3270497 | 1st Floor- Room 8F60- water leak | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-26 16:00:00 | Fail | KPI 6 - Roof leak has been repaired - will need to follow up after next rain Confirmed leak fixed by site rep
MSA-DTWD | WA3270584 | B Block North and South - rusted gutters to be replaced | Murdoch Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-06-22 15:15:00 | Fail | Removed and replaced 28m of rusty gutter with new gutter. Job completed
MSA-DTWD | WA3270614 | Level 3, AMEP - Ports incorrectly labelled | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-06-11 17:00:00 | Fail | All damaged data cabling removed and new consolidation point installed in the ceiling to feed desks
MSA-DTWD | WA3270653 | D Block, Room D4- Metal Verandah post has rusted and broken away from awning | Fremantle Campus (formerly WA Maritime) | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-07-08 14:00:00 | Fail | KPI 3. Fault inspected and Temp make safe carried out - Works will require preparation of BRAF. Replaced corroded struts8/7 - Job completed -demolished end bay of D4 verandah, suspended electrical cable attached to building, verandah bay replaced with new materials
MSA-DTWD | WA3270681 | A Block, Lvl 2- ladies toilet is not flushing | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 10:00:00 | Pass | New inlet valve and unblock air hose
MSA-DTWD | WA3270735 | E Block, Kitchen E58- Oven in kitchen is not working- no power to oven | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-15 14:45:00 | Fail | Installed new feeds as required for Ovens in LSK
MSA-DTWD | WA3270783 | BLD 822, Gas burner on boiler faulty | Muresk Institute | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 10:30:00 | Pass | Gas burner on the boiler failed due to water ingress from a leaking water pipe, which has been repaired.Replaced faulty control box and gas pressure switch on the gas burner and tested for correct operation.Verbal approval received from ERIC to carry out repairs whilst on site so as to avoid the cost of a second trip. BRAF attached for total value.Gas boiler in Dempster Hall - no asset number on unit or associated components
MSA-DTWD | WA3270840 | E Block, E75 Kitchen - 2x damaged GPO's | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-26 08:00:00 | Fail | Attended site, replaced two faulty gpos hanging off wall. Tested all working properly. Job complete.
MSA-DTWD | WA3270843 | D Block, D37 Meat Trades – Faulty Gas Hose (oven) | Bentley Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 09:30:00 | Pass | Repaired cooktop in butchers kitchen
MSA-DTWD | WA3270845 | Campus - 6x Damaged Gate Padlocks | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 06 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 09:30:00 | Pass | 6 x padlocks damaged.Padlocks repaired
MSA-DTWD | WA3272150 | G Block Foyer- Main fuse box can not be locked or even closed properly | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 06 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 11:30:00 | Pass | 13/5/20 : Attendance Including 1st 1/2 hour labour to make keysto suit electrical box and lock shut. Key dropped into sturdentservices
MSA-DCS | WA3271035 | Social Club next to staff car park - burst water pipe, north eastern corner | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 07 May 2020 | 2020-05-07 07:16:48 | 2020-05-07 06:20:00 | Pass | Investigate burst pipe , burst found on retic, isolated water. Will need reticulatioj contractor to attend
MSA-DCS | WA3271178 | Internal Primitive Fence Line - Microwave Alarm B- 3 is not alarming | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 May 2020 | 2020-05-07 10:47:18 | 2020-05-07 15:03:00 | Fail | Intwrnal microwave zone B3 failing to activate, checked mocrowave operating correctly, found tecom equipment non responsive traced issue to latched relay on tecom equipment, cycled and tested now operational.
MSA-DCS | WA3271199 | Official visits Non Contact Cell Static on the new speaker | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 May 2020 | 2020-05-08 07:04:19 | 2020-05-07 20:04:00 | Pass | Feedback noise due to vandal proof metal enclosure installed on top of the intercom unit, advice maintenance if they can replaced it with non metallic cover.
MSA-DCS | WA3271227 | Abattoir no water supply to taps in smallgoods area | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 14:00:00 | Pass | COMPLETED
MSA-DCS | WA3271237 | Abattoir 1 broken switch and 1 broken power point on slaughter floor | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 09:30:00 | Pass | Investigate and replace broken switches and gpo in abattoir
MSA-DCS | WA3271258 | Bakery - Workshop-INTERNAL BAKERY FREEZER MOTOR HAS ICED UP not getting to temp | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 07 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 08:30:00 | Pass | Arrived on site and signed in tools, checked over freezeroom found down to temperature and no ice on coil,pressures ok,and sytem running ok at present.
MSA-DCS | WA3271265 | Administration - Court Yard-2x fluro lights blown-see notes | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 12:00:00 | Pass | Investigated admin building external lights. Found construction site electricians had disconnected them. Had a meeting with them. Site to rectify
MSA-DCS | WA3271272 | Unit 14 - B7 Main light switch cover plate inside cell door is broken, needs replacing. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 10:00:00 | Pass | Replaced damaged cell switch in unit 14 b7
MSA-DCS | WA3271281 | Unit 14 - A2-shower sceen leaking-see notes | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 May 2020 | 2020-05-13 17:00:00 | 2020-05-28 13:00:00 | Fail | SHOWER SCREEN REPAIRED
MSA-DCS | WA3271288 | Amenities - Staff toilet cistern not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 May 2020 | 2020-05-13 17:00:00 | 2020-05-08 15:30:00 | Pass | Pick up parts from supplier, remove parts and install new.
MSA-DCS | WA3271294 | Unit 1 - B & D Door handle to yard broken off | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 07 May 2020 | 2020-05-11 17:00:00 | 2020-05-27 14:00:00 | Fail | door handle to B&D door replaced/installed
MSA-DCS | WA3271300 | Unit 1 - B5 Fire damage to cell floor | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-09-15 10:00:00 | Fail | DAMAGED FLOOR UPLIFTED, PREPARED & NEW VINYL LAID
MSA-DCS | WA3271308 | Unit 3 - A Wing Ablutions door won't close in A Wing | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-06-08 10:00:00 | Fail | shower door re fitted
MSA-DCS | WA3271329 | Kitchen - Workshop water hose on kettle leaking middle kettle | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-08-10 09:12:00 | Fail | JOB IS CANCELLED AS THE ISSUE WAS ATTENDED WHILST ON SITE FOR ANOTHER JOB FOR PROGRAMMED.
MSA-DCS | WA3271386 | Metal Shop, workshop - light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-06-16 17:00:00 | Fail | Repaired and replaced multiple faulty lights in metalshop
MSA-DCS | WA3271399 | Reception entry door - swipe card readers not working and white button to overread isnt working | Rockingham Justice Complex | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 May 2020 | 2020-05-07 12:40:37 | 2020-05-07 11:37:00 | Pass | Reported fault reception every not working. Door tested, working as per normal from Security System. Auto Door set to sensor only open. Recommend door contractor ASSA ABLOY attend to reprogram/rewire to open on swipe and rex without sensor.
MSA-DCS | WA3271427 | unit 1 C3 Cell door has been kicked in and has a split on the door | Hakea Prison | SPA-GR | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 May 2020 | 2020-05-08 08:53:39 | 2020-06-24 12:30:00 | Fail | supplied and installed replacement cell door.
MSA-DCS | WA3271438 | Gardens cucumber shed heater 1 tripping RCD | Karnet Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-26 15:30:00 | Fail | Investigate cucumber shed fault. Found heater fan requires replacement. Sourced replacement parts, replace and test.
MSA-DCS | WA3271445 | Staff Tea room - Bain Marie not working. No power from unit-refrigeration fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 07 May 2020 | 2020-05-07 12:59:34 | 2020-05-12 09:15:00 | Fail | Replaced carel controller and temp probes, unit is now operating correctly and temp probes are reading correct temperature
MSA-DCS | WA3271483 | East side of prison, external fence H1- D2 if offline | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 May 2020 | 2020-05-07 13:19:05 | 2020-05-07 15:07:00 | Fail | Energised fence zones H1 onward found offline, traced issue to mode in bunker, modem reset and system restored, cleared alarms and tested ok.
MSA-DCS | WA3271507 | L3 zone 3 lights keep turning off after a period of time | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | LYNX INTEGRATED SYSTEMS | 1 | CLOSE | 07 May 2020 | 2020-05-08 09:29:21 | 2020-05-08 17:00:00 | Fail | Upon investigation appears that there has been a recent environmental disruption to the lights. Altered programming to ensure system does not enter into after hours mode during the day.
MSA-DCS | WA3271508 | next to work shop external PTZ 7 gone down due to lightning strike | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 May 2020 | 2020-05-08 09:30:44 | 2020-05-07 15:00:00 | Pass | Reset PTZ fiber modems and power supply. All reset and camera functions tested ok. Job complete
MSA-DCS | WA3271516 | Visits Centre - CCTV Cameras are down, | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 May 2020 | 2020-05-08 09:34:37 | 2020-05-07 15:30:00 | Pass | Network switch failed after power lost on site due to maintenance works, rectified and fixed. Job completed
MSA-DCS | WA3271567 | Admin, Operations - Damaged power point | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 11:00:00 | Pass | Replaced damaged power point in Admin
MSA-DCS | WA3271594 | Gate Control, Zone 4 shunted - constant alarming | Roebourne Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 May 2020 | 2020-05-07 18:11:39 | 2020-05-07 17:00:00 | Pass | Job complete
MSA-DCS | WA3271597 | gate Key 21 in key press cannot be retrieved-see notes | Roebourne Regional Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 May 2020 | 2020-05-07 18:13:39 | 2020-05-07 19:00:00 | Fail | Job complete
MSA-DCS | WA3271602 | Health Centre, Vaccination Fridge is in alarm & seems to be faulty | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 07 May 2020 | 2020-05-08 10:13:36 | 2020-05-07 15:00:00 | Pass | Found unit running on arrival reaching set point. Tested several times and reach set point with no fault. Cleaned out coils and tested all components to ensure optimum performance. All operational at time of departure.
MSA-DCS | WA3271624 | Squash Courts- Roof leaking on the right court | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-07-22 11:59:00 | Fail | CLEANED OUT LEAF LITTER, CLEANED ROOF
MSA-DCS | WA3271640 | Unit 4, Cells 38 & 39 door locks faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-08 13:00:00 | Pass | Attended site to repair locks to unit 4 cells 38 & 39, also replaced internal spindles and springs for correct operation. Date on site: 08/05/2020 Time on site: 12:00pm - 01:00pm
MSA-DCS | WA3271645 | INF (10) Fluro light in disabled showers needs replacing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 15:00:00 | Pass | Repaired faulty lights in infirmary toilets
MSA-DCS | WA3271655 | Unit 5, Control Room - Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 13:30:00 | Pass | Replaced 2 faulty hallway lights and broken light switch in Unit 5, Control room
MSA-DCS | WA3271660 | Admin Tearoom- hot water service element is faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-07 15:30:00 | Pass | Investigated hwu in admin. Found faulty element. Picked up replacement and installed
MSA-DCS | WA3272023 | Unit 4 - Day Room UNIT 4 BD/AC NO WATER TO OVENS | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-08 11:00:00 | Pass | Remove ovens and check for blockage, no blockage found. Identify isolation valve and turn water supply back on.
MSA-DCS | WA3272047 | Above Toby - Flickering light | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 15:00:00 | Pass | Replaced globes/lamps as required
MSA-DCS | WA3272069 | Unit 1, house 2. cell 2- cell tampered-removed | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-19 19:38:00 | Fail | Sourced parts from seme stock.Replaced 5x reed switch in unit 1 house 4,5 living room and external doors.
MSA-DCS | WA3272114 | Unit 3, outside kitchen near office- Hot water urn not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 09:30:00 | Pass | Removed old unit due to tank leek and badly rusted. Replaced with new zip . All tested new capex Asset installed
MSA-DCS | WA3272143 | ISU(Harding) Kitchen- Water cooler not working | Banksia Hill Detention Centre | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 10:25:00 | Pass | Swapped over coolers and commissioned. installed new maxiflow filter system A40190496M and partner cc bt refrigerated cooler 19081930320054 new assets tested. removed old to tip
MSA-DCS | WA3272263 | Control room - cell call system is frozen | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 May 2020 | 2020-05-08 14:57:11 | 2020-05-08 08:00:00 | Pass | Investigated fault, found Tecera PC not communicating with virtual server PC. Reset and reconfigured virtual machine to correctly communicate to Tecera PC. Retested multiple cell calls and confirmed for correct operation. All tested and working ok, job complete
MSA-DCS | WA3272288 | Kitchen, central - Sink Tap Won’t turn off leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 May 2020 | 2020-05-08 15:15:47 | 2020-05-08 12:15:00 | Pass | Pulled apart stanless basin straighten the bent parts Regreased moving parts and reinstalled
MSA-DCS | WA3272291 | CCU,Holding cells common area outside yard - Repair broken tap | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 13:15:00 | Pass | Replaced tap and repaired in wall
MSA-DCS | WA3272299 | Kitchen, Rational Oven No 3 - Not draining correctly. Draining from cabinet and not waste pipe. | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-25 16:15:00 | Fail | 11/05/20 - Called as requested to the oven not working correctly not drain correctly. Found the drain blocked with fat so cleaned and tested all ok. Also found the door striker and latch badly warn so will require replacement. 25/5/20 - Returned to site, liaise with reception, walk to the kitchen, identify faulty oven, isolate remove faulty parts, install and reassemble all components and test for correct function okay.
MSA-DCS | WA3272304 | Kitchen,Entrance Door - Bottom Locking Drop Bolt Mounting Plate Has Stripped Threads | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 16:00:00 | Pass | Repaired lock as required
MSA-DCS | WA3272367 | Kitchen, Central -Wash Down Hose Spray Tap Is Broken | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-11 13:45:00 | Pass | Replaced sprayer with new hose and sprayer
MSA-DCS | WA3272383 | Unit 9, Cell 10- Vinyl is damaged & lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2021-01-07 14:30:00 | Fail | NEW VINYL INSTALLED TO 5X AREAS
MSA-DCS | WA3272410 | unit 9, C10 - New bed light required to be installed | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 11:30:00 | Pass | Installed new bed light
MSA-DCS | WA3272412 | Emergency Generator starter battery amp meter reading higher than normal | Boronia Pre-release | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 1 | CLOSE | 07 May 2020 | 2020-05-08 15:46:50 | 2020-06-08 16:00:00 | Fail | Starter motor replaced
MSA-DCS | WA3272455 | Reception, Disabled Toilet/Shower- Ballast is damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-11 11:00:00 | Pass | Repaired light
MSA-DCS | WA3272473 | Eastern Gym- Damaged power points to be removed | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-06-23 11:00:00 | Fail | Removed gpos
MSA-DCS | WA3272480 | Lights to towers outside the back of U9 are not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-07-02 11:00:00 | Fail | Repaired lights
MSA-DFES | WA3271337 | Power outage please check security system due to power outage | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | General Electrical (EL) | SONTEC WA PTY LTD | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 15:30:00 | Pass | 7/5/20 - Dylan Parslow, Joshua ParkInvestigated stairwell alarm event. Advised monitoring response is to dispatch security.Investigated issue with vehicle gates. Power cycled controllers and tested. Faults appear to be cleared.
MSA-DFES | WA3272037 | BA service area 2x taps fallen off and one tap stiff, old FF shower reses HW tap stiff | CFRS Claremont | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-05-08 14:23:00 | Pass | Repair shower taps and fit new flick mixer to basin and ba room. Also fitted mini stops to sinks.
MSA-DFES | WA3272250 | Applied traning - pumps 2 has now failed. Pump 1 has also failed, currenlty no pumps working | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-08-03 07:24:00 | Fail | pump repairs completed by Malcolm Thompson pumps all tested all OK spoken with chis from applied training and confirmed all works complete and operating
MSA-DTAG | WA3271334 | ground, plumbing duct - Disconnect old HWU & re-connect new HWU | Perth Children's Court | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-07 10:15:00 | Pass | Job complete
MSA-DTWD | WA3271306 | E block, Ground level, stores area - Blast chiller and entry to store require GPO's to be repaired | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 09:30:00 | Pass | Attend site and inspect stores gpos. One power point for the blast chiller was being held back to the wall with sticky tape as the gyprock had broken around the power point so we removed the gpo and moved it down a 100mm where the gyprock was not damaged. The wall has been left with a hole where the gpo used to be and will need to be patched. There was also a power point loose in the stores entrance and the male toilet which we tighten the screws to refix back to the wall.
MSA-DTWD | WA3271320 | L2 D208 Leak on the ceiling | Perth Campus B4 | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-06-09 12:15:00 | Fail | Arrived at site, set up tools. Laid drop sheets. Cut out damaged section of ceiling. Surrounding ceiling was sagging quite badly because of an aircon vent and chopped battens. Reinforced battens and re-supported aircon duct. Pulled whole ceiling support up to level out section. Installed battens for fixing points. Tidy area pulled up drop sheets, vacuumed and packed away tools.Picked up material on way to site. Arrived at site, measured cut and fit plaster to ceiling section. Flushed with first coat, cleaned area and packed away tools.Arrived at site, setup work area. Final sand. Cleaned and applied first coat of paint.Arrived at site, set up work area. Filled gaps, taped edges and painted final coat. Tidy area packed away tools.
MSA-DTWD | WA3271390 | Science lab BLD 830 Wet and Dry labs Heater A/C faulty | Muresk Institute | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | CDA Air & Solar | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-06-25 12:57:00 | Fail | 2x relays faulty, replaced. Operation ok
MSA-DTWD | WA3271415 | S/W & S/E external ring road - Blocked road sumps | Midland Campus | GMP-BR | Roofing | Guttering (RF) | High Tech Maintenance | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 11:00:00 | Pass | Unblocked road sumps at North Metro TAFE Midland Campus
MSA-DTWD | WA3271711 | Ladies toilet tower level 3 flush button sometimes sticking | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 13:15:00 | Pass | Complete
MSA-DTWD | WA3271757 | block 7 ground kitchen Grease pit in canteen not draining | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-05-08 16:07:00 | Pass | Unblocked lines behind canteen
MSA-DTWD | WA3271805 | L block lift Lift out of service-see notes | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 12:45:00 | Pass | Not chargeable
MSA-DTWD | WA3271877 | Large gum tree snapped in half, need arborists to cut up and remove | Mandurah Campus (formerly Peel) | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 09:47:00 | Pass | Tree removed.On site 7.15 am, completed work order 9.47 am 08052020Labour 4 staff 2.5 hours @ $100 per hour = $1,000Materials. Chipper truck/chipper, cherry picker 2.5 hours @ $100 per hour per uniit = $500BRA $2,800. Actuals $1,500. Claim $1,500
MSA-DTWD | WA3271991 | fire alarm panel showing several faults | West One Services | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 09:30:00 | Pass | Investigated issue and due to leak in roof all osid devices and modules will need to be replaced. There is 5 of each and due to leaks in roof there is no point fixing until leaks have been fixed.
MSA-DTWD | WA3272054 | E block L2 passage near lift Auto door to Library passage not working | Mount Lawley Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 09:55:00 | Pass | On arrival found door was not activating fron outside, found external sensor was faulty, replaced 1x microhead sensor, tested operator, all working fine.
MSA-DTWD | WA3272070 | A block Unable to set alarm system and is sending alarms to Education Security | Rockingham Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-05-08 11:15:00 | Pass | Attend site to investigate fault on System A not being able to arm. Have spoken to Ed Sec, they believe there is no fault to be looked at and have received closings for the past few days
MSA-DTWD | WA3272104 | D-Block 2nd floor plant room, the AHU water circulating pump motor, rear bearing faliure | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-05-11 09:30:00 | Fail | Fitted generic fan with grub screw drilled through centre bush ,
MSA-DTWD | WA3272117 | D block, Level 2, staff kitchen - high ceiling lights out, need replacing | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 09:30:00 | Pass | Attend site and inspect globes out in d block staff room. Source replacement and return to site and replace.
MSA-DTWD | WA3272399 | H Block, H15 Staff Room – Faulty light fitting over printer station | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-11 13:15:00 | Pass | Replaced faulty light fitting with new. Job completed
MSA-DTWD | WA3272406 | E Block- Entrance to E74 & E75 Kitchens- Water Damage to Ceiling | Bentley Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-06-17 14:00:00 | Fail | Resolved leak -Spoke with Brad Shilken (site) agreed we could close this job off and complete install of replacement compressed cement ceiling on WA3348426
MSA-DTWD | WA3272426 | M Block, M6 Staff Kitchen – Under bench Hot Water Unit is leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-05-08 13:15:00 | Pass | Leaking hot water unit was replaced.
MSA-MRWA | WA3271432 | Level 8, 8.30 - light flickering please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 07 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 13:47:00 | Pass | Replaced tube with new
MSA-MRWA | WA3271442 | Ground male toilets - Water leak from Ceiling in shower recess in Men’s Toilet. | Materials Engineering Branch | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 09:45:00 | Pass | Carried out initial repairs under breakdownFurther works required were detailed on the BRAF - Scott has requested the additional works be submitted as a quote
MSA-MRWA | WA3271697 | L2 TBC L2 - Locked document cabinet please unlock | Don Aitken Centre MRWA Head Office | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 07 May 2020 | 2020-05-08 17:00:00 | 2020-05-07 15:00:00 | Pass | open and supply keys to a locked cabinet
MSA-MRWA | WA3271771 | L1 - middle ladies toilet full flush button not working | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 08:20:00 | Pass | Replaced ripped rubbers on the mid cistern-female’s toilet
MSA-MRWA | WA3271867 | L6- third cistern in the service duct making dripping noise | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 07 May 2020 | 2020-05-14 17:00:00 | 2020-05-11 11:22:00 | Pass | Replaced faulty inlet valve
MSA-MRWA | WA3271975 | Asphalt Lab - Sink has leaked bitumen & solvent under the right hand side steel fume cabinet | Materials Engineering Branch | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 09:18:00 | Pass | Repaired leak under sink
MSA-DCA | WA3273411 | ground lift 5 not working | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 08 May 2020 | 2020-05-11 17:00:00 | 2020-05-08 15:55:00 | Pass | On investigation found JFIS unit tripped. Reset and check controller terminations. Run and monitor
MSA-DCA | WA3273857 | Aircon is not working in the Black Swan’s Office | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 2-Props Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 12:00:00 | Pass | Schedules ammended on BMS
MSA-DCS | WA3272734 | Gate Control - Main Control Room - No CCTV on Primitive Alarm | Albany Regional Prison-Security Perimeter | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 May 2020 | 2020-05-08 13:50:28 | 2020-05-08 18:00:00 | Fail | Travel to site, investigated fault, Found CCTV alarms not activating on Gallagher zone activations. Investigated Indigo and Gallagher settings and services. Found that USB device on indigovision workstation had lost its connection related to the integration module. Located PC and programmed into spare USB port and retested perimeter alarms. All had tested and programmed ok. Travel back to Perth. Job complete
MSA-DCS | WA3272837 | gardens small lettuce shed box gutter rusted out and leaking | Karnet Prison Farm | GMP-BR- HO | Roofing | Guttering (RF) | AFD Contracting | 3 | CLOSE | 08 May 2020 | 2020-05-14 17:00:00 | 2020-06-15 11:30:00 | Fail | 25/05/20Measure box gutters.Repairs required:Remove and replace a total of 20 lineal meters box gutters to gardens (lettuce shed). Replace in .6 Colorbond.BRAF to be submitted15/06/20Replace box gutter to small lettuce shed
MSA-DCS | WA3272899 | new canteen roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 08 May 2020 | 2020-05-12 17:00:00 | 2020-05-08 15:00:00 | Pass | located leak and rectified
MSA-DCS | WA3272910 | Unit 5 - D Wing Shower ( first shower) tap not turning off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 May 2020 | 2020-05-14 17:00:00 | 2020-05-08 14:00:00 | Pass | Install new split pin in spindle in plumbing duct and test
MSA-DCS | WA3272924 | Unit 14 - Control Room cctv reception to LCD screen is blurry and unstatic. Need to fix urgently. | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 10:30:00 | Pass | Unit 14 CCTV monitor replaced for new restored images and tested all ok.
MSA-DCS | WA3272984 | Unit 2 - A12 sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-08 12:00:00 | Pass | Plunge sink to clear blockage.
MSA-DCS | WA3272995 | Unit 1 - C5-toilet is not flushing the cell button doesn’t work | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-08 13:00:00 | Pass | Extend flush button assembly in plumbing duct
MSA-DCS | WA3273017 | BR control/computer room camera pre sets as they need to be re adjusted | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-08 12:00:00 | Pass | Rectified and fixed preset alarm from multiple ptz cameras, job completed.
MSA-DCS | WA3273061 | unit 4 cell H 21 ROOF LEAK | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-11-25 09:00:00 | Fail | CHECKED FOR SOURCE OF LEAK - COULD FIND NO POSSIBLE ENTRY POINTS
MSA-DCS | WA3273066 | gate house foyer light faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 12:00:00 | Pass | Investigate and replace light and pe cell for gatehouse foyer
MSA-DCS | WA3273069 | kitchen outside lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 14:00:00 | Pass | Investigate outside kitchen lights not working.Replace faulty lights.
MSA-DCS | WA3273074 | Unit 6 - Control Room Cell call alarm constantly going off in controll room | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 May 2020 | 2020-05-09 08:47:53 | 2020-05-08 12:33:00 | Pass | Unit 6 cell call system is i ndicating a node error / network error , this error is indicating throughout the entire site and is being caused by a node being offline, this has been traced to the new build / construction site and site has been informed.
MSA-DCS | WA3273086 | visits E area Down lights damaged requires replacing | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 May 2020 | 2020-05-09 08:51:43 | 2020-05-11 08:30:00 | Fail | replaced down light
MSA-DCS | WA3273137 | Main kitchen combi oven is noisy and has issue with gas flow | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 08 May 2020 | 2020-05-09 08:12:34 | 2020-05-27 13:00:00 | Fail | Found upper hotair burner causing this noise. Gas burner air intakes are all quite dirty with buildup, clean intakes. Make minor adjustments to minimise noise. Burner needs replacing. Will return once BRAF approved and received parts.Returned 27/5, replaced all 3 burners, adjust & test.
MSA-DCS | WA3273149 | Vegie Prep- Potato rumbler not working | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-06-08 11:00:00 | Fail | Veggie Prep Potato Peeler faulty. Check peeler, remove for repairs. Dismantle, repair motor & wiring. Fit new start switch. Repair seized motor, adjust. Assemble & test. Return to site.
MSA-DCS | WA3273154 | Stores- air bridge arm faulty/not lifting | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 10:00:00 | Pass | Stores - North end air bridge arm faulty/not lifting. Check pump and ram, remove ram, leaking seal. Repair seals. Top up oil tank. Refit ram, purge air from lines & test.
MSA-DCS | WA3273168 | Outside Stores freezer room Freezer door frame freezing at top-see notes | Hakea Prison | SPA-BR | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-11-03 12:30:00 | Fail | Works completed by sub contractors
MSA-DCS | WA3273184 | Outside Stores cool room Cool room coving & walls damaged in several areas | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-10-21 09:13:00 | Fail | advised to close off cost to date. new work order issued (WA3720150) 21/10/2020
MSA-DCS | WA3273186 | Vegetable Prep- washbay tap & hose damaged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 08:30:00 | Pass | Replace hose and damaged fittings.
MSA-DCS | WA3273219 | Reset Visits Centre Toilet Block, Female toilets- Auto lights not working | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 14:30:00 | Pass | Movement sensor has failed, will replace unit .Picked up new sensor and fitted it . Test ran ok.
MSA-DCS | WA3273335 | Unit 2, Cell C8- light not working,possible switch problem | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 08:30:00 | Pass | Repaired faulty lights in unit 2 c8
MSA-DCS | WA3273342 | Gymnasium - The Whole Unit Gymnasium recreation store doorlock & handle is damaged . | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-06-12 12:45:00 | Fail | Replaced handle
MSA-DCS | WA3273346 | Unit 5, Cell A15- Light broken in cell | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 09:30:00 | Pass | Repaired light
MSA-DCS | WA3273351 | unit 1 B15 Toilet Blocked, line needs to be rodded. Keeps blocking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 12:30:00 | Pass | Drain machine was used to unblock toilet and clean out line
MSA-DCS | WA3273357 | Reception - Store Light in southern clothing issue store flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 10:00:00 | Pass | Repaired faulty lights in reception store rooms
MSA-DCS | WA3273445 | Unit 1, S/O Office- Hole in ceiling | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-06-16 08:20:00 | Fail | HOLE PATCHED & PAINTED
MSA-DCS | WA3273447 | Possible problems to arise from Generator Test on Tuesday 12th May | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 10:30:00 | Pass | Checked and tested generator remote controls during generator test. All OK.
MSA-DCS | WA3273454 | Possible problems to arise from Generator Test on Tuesday 12th May | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 08:30:00 | Pass | Liaise with Schneider to get BMS system and VSD system running pumps back online
MSA-DCS | WA3273492 | Ablutions next to Rm 6 Male toilets, 2 toilets water constantly running & flows on floor when flushe | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 13:45:00 | Pass | Complete
MSA-DCS | WA3273501 | Main building rear of hall female toilets exhaust fan on wall not working | Nyandi Training Academy | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 15:45:00 | Pass | Replaced motor run capacitor , cleaned fan , exhaust duct and grill . Refitted fan and test ran ok.
MSA-DCS | WA3273508 | Rear of Hall, Female Toilet- Sink tap unable to turn on | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 11:30:00 | Pass | Complete
MSA-DCS | WA3273514 | Unit 14, B Wing, Cell B05- Shower Screen leaking onto matress | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-28 12:15:00 | Fail | REPAIRED SHOWER SCREEN
MSA-DCS | WA3273515 | Kitchen staff toilet cistern cracked and leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 May 2020 | 2020-05-09 12:24:29 | 2020-05-08 14:59:00 | Pass | Replaced broken cistern and pipe work
MSA-DCS | WA3273518 | Unit 14, B Wing, Cell B11- Shower Screen leaking onto matress | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-28 13:15:00 | Fail | repaired leaking shower screen
MSA-DCS | WA3273519 | Unit 14 - B Wing Showerhead constantly leaking B11 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 15:30:00 | Pass | Remove and replace 1/4 turn spindle in service duct
MSA-DCS | WA3273526 | Unit 1, Plant Room- Air Con extract fan alarm/wiring | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 12:30:00 | Pass | Liaise with seme contractor onsite to trace out and rectify damaged alarm cabling,found cables lead to air pressure switches on cell exhaust fans, also found another signal cable damaged by rats,seme is going to repair.
MSA-DCS | WA3273532 | Unit 1, Plant Room- Air con extract fan alarm /controlls faulty | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-18 09:00:00 | Fail | Repaired by soldier and heatshrink rodent damaged cable (three joints, and new cable added) in ceiling space.
MSA-DCS | WA3273543 | Make good defective camera pole to N/E roof on Unit 2 | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-12-07 09:05:00 | Fail | Repair defective pole by installing new supports and re sealing. Remove redundant rust PA speakers.
MSA-DCS | WA3273590 | Unit 1, Cell B16- Main lock is not functioning & key wont work | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 08 May 2020 | 2020-05-08 16:56:22 | 2020-05-08 15:15:00 | Pass | Rectified issue with lock.
MSA-DCS | WA3273623 | kitchen exhaust unit above cookers not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-15 15:00:00 | Pass | Investigate kitchen exhaust not working. Found belts had snapped. Sourced new belts and replaced.
MSA-DCS | WA3273629 | control MDAS message on screen no response R) fence line nth east of spiritual centre | Boronia Pre-release-External Area-Ground Floor | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 May 2020 | 2020-05-09 13:16:36 | 2020-05-11 12:45:00 | Fail | Pickup part and travel to site to replace the damaged receiver TR7B1R2, also found comms cable from receiver1 to receiver 2 white wire resistance measured faulty. Replaced it with spare wire in the cable. Tested it ok after.
MSA-DCS | WA3273632 | Unit 3, office toilet - Roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Tiled Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-22 09:00:00 | Fail | REMOVE VENT FROM OFFICE ROOF CLOSEST TO TOILET AND INSTALL ANOTHER DECTITE TO WATERPROOF
MSA-DCS | WA3273668 | kitchen pot wash area drain basket broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-14 14:00:00 | Pass | COMPLETED
MSA-DCS | WA3273719 | sewerage plant leaking water on the new insulation hopper | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | Daniel Chrisp Pty Ltd | 1 | CLOSE | 08 May 2020 | 2020-05-09 14:06:39 | 2020-05-09 13:11:00 | Pass | Watercon Employee attended site 08/05/2020 and completed job on 08/05/2020 (system would only allow me to enter 9th May?Watercon Priority One 0700 - 1700 weekdays (excluding Public Holidays) Minimum call out 6 hours (included travel within Metro) $960.00 (excluding gst).
MSA-DCS | WA3273748 | Unit 2 - A & C-Refrigerator in A/C dayroom not cooling-see notes | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 13:30:00 | Pass | Checked over fridge found to be running ok, checked compressor and temperature all ok.
MSA-DCS | WA3273810 | Crisis Care, Cell 6- Door hatch is not functioning | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 08 May 2020 | 2020-05-09 15:13:30 | 2020-05-09 09:15:00 | Pass | Lock on Crisis Care Unit Cell 6 - is non operational( Meal hatch )Lock replaced with new lock keyed to Prisons System
MSA-DCS | WA3273885 | NVR raid failure, no recordings | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-20 08:40:00 | Fail | job to be invoiced at costs to date
MSA-DCS | WA3273887 | MDAS slave server comms failure | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-15 07:35:00 | Pass | Reset system at gatehouseOfficers on nigh shift had experienced issues with cell call and had re booted psu in arunta room No fault evident poss intermittent fault
MSA-DCS | WA3273890 | Aurata UPS in alarm, no hold time | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-23 12:30:00 | Fail | Removed the 2 faulty UPS and replaced with 1 larger capacity rack mount UPS. All systems restarted ok. UPS load tested ok. Parts used:PSS XL+1000 (SEME stock)Consumables
MSA-DFES | WA3273734 | ground yard x Floodlight at southern end of drill yard not operational | CFRS Joondalup | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-20 09:15:00 | Fail | Complete
MSA-DFES | WA3292082 | Retrospective work order donot attend-intermittent fault with the ballast | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 08 May 2020 | 2020-05-14 17:00:00 | 2020-05-19 10:57:00 | Fail | Complete
MSA-DTAG | WA3272815 | Wireless transmitter near old library out of range | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 08 May 2020 | 2020-05-14 17:00:00 | 2020-05-08 15:30:00 | Pass | Programmed new Inovonics transmitter. Created system alarm for Receiver 6. Tested transmitter alarm and tamper. Confirmed working on Gallagher System.
MSA-DTAG | WA3273254 | L22-01 Amenities east door Door reader not working / reader died on going issue-see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-06-02 14:30:00 | Fail | restored Level 22 Break Glass Unit. Took Reader off card & pin, and changed to swipe only as perclients request.Job completed.
MSA-DTAG | WA3273439 | 1987 Level 3 public corridor leading to Courts 10 & 11 -Lift 1 is not responding | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 08 May 2020 | 2020-05-11 17:00:00 | 2020-05-11 11:30:00 | Pass | Not chargeable
MSA-DTAG | WA3273787 | 1987 carpark Fist size hole in ceiling outside Judges lift – patch & paint required | Supreme Court | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-06-08 13:00:00 | Fail | HOLE PATCHED & PAINTED
MSA-DTWD | WA3273113 | A block AG07 external Drains outside are blocked | Carlisle Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 16:25:00 | Pass | Unblocked drains in a block courtyard
MSA-DTWD | WA3273118 | B Block, BG25 Welding Bays- Roof leaking welding bays | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-08-10 15:15:00 | Fail | KPI 3 attended site and identified the source of the leak. Will require further direction from site before works can proceed
MSA-DTWD | WA3273141 | D-Block 1st floor Library, auto blinds on window are not retracting properly | Joondalup Kendrew Campus | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-06-05 11:00:00 | Fail | Repairs to blinds
MSA-DTWD | WA3273177 | Chiller Plant Room - Lights not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 09:31:00 | Pass | Replaced duality lamps and reset tripped rcd. Job completed
MSA-DTWD | WA3273202 | D Block, DG06- 4x faulty GPO's | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 15:30:00 | Pass | Attended site and signed in. Located outlets and cabling not compliant. Removed cabling and installed gpos and conduit between each bay. Tested all okay. Job complete
MSA-DTWD | WA3273491 | House 811, Gully trap overflowing | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-08 18:00:00 | Pass | Cleared blockage to gully and repair broken
MSA-DTWD | WA3273495 | House 810- Toilet and sinks blocked, plus replace all tap washers | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-11 12:00:00 | Pass | Cleared blockage to sewer line & replace washers to taps House 10
MSA-DTWD | WA3273626 | E Block- Gutter southside needs repair | Balga Campus | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 3 | CLOSE | 08 May 2020 | 2020-05-15 17:00:00 | 2020-05-28 12:45:00 | Fail | Measured E011Removed and installed gutter above E011 doorway side
MSA-DTWD | WA3273859 | Tree Lopping required – Close Vicinity/Danger to power lines | Bentley Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 08 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 11:30:00 | Pass | Labour: 5 staff $100 per hour for 5 hours $2,500Material: Chipper truck. chipper. Cherry Picker. 2 units at $200 per hour for 5 hours $1,000Budget $2,500. Actuals total rate $3,500. Claim $2,500.
MSA-MRWA | WA3273262 | L1 Investigate and locate source of odour within the toilet facilities. Remediate if possible. | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 08 May 2020 | 2020-05-08 14:22:24 | 2020-05-08 12:50:00 | Pass | Investigate smell to male toilets.Reseal open ended vent pipe in male toilets plumbing duct.
MSA-MRWA | WA3273571 | Lvl 1 Cafe door- door is opening but not closing | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 08 May 2020 | 2020-05-08 16:40:38 | 2020-05-08 15:15:00 | Pass | Replaced faulty pes as necessary, checked over and tested.
MSA-DCS | WA3274224 | Unit 1 cell B28 toilet is not flushing | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 May 2020 | 2020-05-10 09:11:55 | 2020-05-09 12:15:00 | Pass | Supply and install new toilet cistern inlet valve and outlet rubber( truck stock). Cistern now flushing A-OK
MSA-DCS | WA3274266 | Banksia Hill Detention Centre- in gatehouse camera 115 as no picture | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 May 2020 | 2020-05-10 10:34:42 | 2020-05-11 08:28:00 | Fail | Urquhart PTZ camera found offline, reset camera supply and camera restores, xhecked supply ok.
MSA-DCS | WA3274277 | SOG office Shower blocked outside the unit and won't turn off | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 May 2020 | 2020-05-10 10:56:30 | 2020-05-09 17:00:00 | Pass | Located isolation valve and re washer shower
MSA-DCS | WA3274333 | Broome Regional Prison- Gatehouse PDA system speaker is crackling | Broome Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 May 2020 | 2020-05-13 17:00:00 | 2020-05-23 14:30:00 | Fail | replaced audio jack on both sides of KVM, replaced speakers with seme stock Edifer R12U
MSA-DCS | WA3274337 | Broome Regional Prison- lagging camera in female unit due to old PC | Broome Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 May 2020 | 2020-05-13 17:00:00 | 2020-07-17 14:40:00 | Fail | Sourced Hdmi to DP cablesInstalled and programmed new workstation.Removed faulty workstation. Old workstation has been placed in Arunta room until advised how to dispose of equipment
MSA-DCS | WA3274353 | Unit 1- A Wing - Severall door lock issues fault in locking the doors - | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | ACE LOCK & SAFE | 0 | CLOSE | 09 May 2020 | 2020-05-09 16:30:35 | 2020-05-09 15:05:00 | Pass | various Locks reported in Unit A - not locking properlyIssue is with Locks and keys - D.O.J is aware of this Locks are secure - no action taken- will discuss further with D.O.J
MSA-DCS | WA3274400 | Bandyup Prison - unit 2 unable to unlock c & D door | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 May 2020 | 2020-05-10 13:27:16 | 2020-05-12 16:00:00 | Fail | Attended site and investigated the fault.After door frame was fixed, door still can not be operated remotely.Checked Gallagher system.Found that electric strike is faulty and requires replacement.Sourcing parts 12:15 till 13:45.Installed new electric strike Lockwood ES 9000 (supplied by SEME).Used sundries.Done modification on door frame to fit new strike.Conducted test.All back to normal and operational
MSA-DCS | WA3274486 | Jellia A/B unit - electric appliances giving shock when used | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 09 May 2020 | 2020-05-09 19:54:46 | 2020-05-14 10:00:00 | Fail | Investigate electric appliances and power to Jeelia A & B
MSA-DCS | WA3274547 | unit 1 cell A2 A3 - blocked toilets | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 May 2020 | 2020-05-10 17:43:35 | 2020-05-26 13:00:00 | Fail | Attended site,Used Jet wash to clear sewer line. Used sewer camera to identify a cracked junction at gully and locate drain converting to pvc at gully inspection opening. Removal of concrete and drain replacement to stack from existing pvc line including gully and 2 basin connections.Backfilled and cleaned up on completion
MSA-DCS | WA3274774 | Karnet Prison Farm- store camera 2 not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 May 2020 | 2020-05-10 11:29:41 | 2020-05-11 14:09:00 | Fail | *calloutLocated switch in canteen store where camera plugged into, swap ports on switch and fault followed, reboot switch and retest, all cameras back and online.
MSA-DCS | WA3274920 | Unit 7 Cell S 12 - Blocked toilet. | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 May 2020 | 2020-05-11 11:41:46 | 2020-05-11 08:48:00 | Pass | Replaced outlet washer and unblocked toilet
MSA-DCS | WA3275040 | Perimeter fence at the back of unit 3- Perimeter alarm- Zone is arming, but no audio and no camera | Albany Regional Prison-Prisoner Accommodation Unit 3 | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 May 2020 | 2020-05-10 22:28:04 | 2020-05-12 16:00:00 | Fail | Perimeter zone golf 1 found microwave receiver with internal ant infestation, removed receiver and dismantled internals removed ants, laced with insect repellent powder and sealed cable entry. Put receiver back together mounted and aligned. Microwave set now operating correctly.
MSA-DCS | WA3275084 | gas heater smells, potential gas leak. gas turned off. | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 May 2020 | 2020-05-11 15:41:52 | 2020-05-11 09:30:00 | Pass | COMPLETED
MSA-DCS | WA3275168 | Roebourne Regional Prison - Gatehouse - Alarm viewer is frozen and beeping. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 May 2020 | 2020-05-11 02:18:11 | 2020-05-10 19:30:00 | Pass | Alarm viewer frozen in alarming condition. Talked site through reset procedure as server latched frozen, after reset system checked fully operational.
MSA-DCA | WA3279523 | Plant room - BMS has multiple alarms after power shut down | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Equipment | Building Equipment (EQ) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 10:30:00 | Pass | Cleared all BMS alarms relating to late night electrical works. Reset all VSD's for AHU 9. Schedule correct but AHU's remaining unoccupied. Client controlling in manual until controls tech attends site for RM.Closed job as discussed with Programmed FM.
MSA-DCA | WA3280109 | AHU7, coils require chemical treatment and clean | Art Gallery of WA - James St-Administration Block (Block A)-Level One-AB1.04A - Plant Room | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-13 17:30:00 | Pass | Carried out chemical treatment coil cleans for AC 7 on reheat zones 7.1, 7.2, chilled water coil as first step to increasing airflow to unit. Unit operational airflow data to be retaken.
MSA-DCA | WA3280135 | Graffiti removal, photo's to follow in email | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 13:30:00 | Pass | Removed graffiti
MSA-DCS | WA3278492 | Gatehouse - network error on cell call system | Broome Regional Prison-Gatehouse Administration | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 May 2020 | 2020-05-11 10:57:05 | 2020-05-15 07:15:00 | Fail | Re booted psuReset cell call system in gatehouseCause unknown
MSA-DCS | WA3278683 | Unit 8, Cell D6- Tap will not turn off, water turned off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 May 2020 | 2020-05-12 06:56:59 | 2020-05-11 10:00:00 | Pass | Replaced hot and cold taps
MSA-DCS | WA3278740 | Unit 1, Cell B20 - Broken glass window | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 11 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 17:30:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3278747 | Eyre, Kitchen- Faulty smoke alarm | Wandoo Rehabilitation Facility | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 11 May 2020 | 2020-05-12 07:28:35 | 2020-05-11 09:30:00 | Pass | Client reported smoke detector not working in eyre block kitchen after smoke filled area due to burnt food. Upon investigation found all smoke detectors in kitchen corridor area to be thermal.
MSA-DCS | WA3278754 | Recreation, Program Room- Faulty door lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 11 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 08:45:00 | Pass | job completed - attended site to look at family door lock at recreation, program room checked, serviced and lubed both door locks. Tighten everything up but didn't find a fault with lock, maybe worn key
MSA-DCS | WA3278777 | Unit 14, Cell B8- Basin is leaking constantly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 08:00:00 | Pass | Remove and replace 1/4 turn spindle in the plumbing duct.
MSA-DCS | WA3278782 | INF (10)- Obs Cell 2- Prisoner water dispenser not functioning | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 11:30:00 | Pass | Check drink Basin, open plumbing duct and turn water valve back on
MSA-DCS | WA3278790 | INF (10)- Toilet at the rear of infirmary resus area leaking from rubber seal between cistern & bowl | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 13:00:00 | Pass | Pick up heart and replace split flush cone on toilet
MSA-DCS | WA3278793 | Unit 4, B & D Wings are not receiving any hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 10:30:00 | Pass | Investigate hot water in showers, no issue is found and hot water is present report back to maintenance.
MSA-DCS | WA3278796 | Unit 14, A Wing, Cell A6- water pressure in basin is low | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 14:30:00 | Pass | Remove restrictor from spout and clean. Reinstall and test
MSA-DCS | WA3278801 | INF (10), Obs Cell 4- toilet is leaking in service duct when flushed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 12:30:00 | Pass | Replace 2 x stopcock O-rings in plumbing duct
MSA-DCS | WA3278802 | unit 3 C Wing Shower Window needs fixing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-25 13:15:00 | Fail | new balances & feet fitted
MSA-DCS | WA3278806 | Unit 13, C Wing, Cell C3- Leaking tap in hand basin | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 13:30:00 | Pass | Replace wine quarter turn spindle in plumbing duct to Basin.
MSA-DCS | WA3278810 | Unit 14 - Staff male toilet tap leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 16:30:00 | Pass | Isolate water service. Remove and service mini stop. Reinstall and test.
MSA-DCS | WA3278815 | Unit 2 - A Wing Night lights not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-14 10:00:00 | Pass | Repaired multiple faulty lights in unit 2
MSA-DCS | WA3278821 | Unit 3, C Wing, Cell C11- Window viewing fram & flap broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-06-08 11:00:00 | Fail | VIEWING HATCH FRAME REPAIRED
MSA-DCS | WA3278832 | MPU (8) - East CCTV in the MPU is frozen - see notes | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-11 13:43:00 | Pass | MPU CCTV camera found with no picture, checked decoder ok power cycled camera with no change, reset port on network switch and comms restored, checked camera visual ok.
MSA-DCS | WA3278845 | front gate Air Con not working, fault light is on. | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 11 May 2020 | 2020-05-12 08:14:21 | 2020-05-28 15:30:00 | Fail | Replaced overload and contactor for condenser fan overload and contactor. Sub contractor replaced controls.Returned to site to test unit and commission. Unit fully operational at time of departure.
MSA-DCS | WA3279060 | foul smell coming from vents. smells like something has died in the air condition/ducting. | Midland (North East Metro) | GMP-BR- HO | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 11 May 2020 | 2020-05-12 09:39:33 | 2020-05-11 12:43:00 | Pass | Checked out smell coming for AC at the back of the office. Checked drain, vents and fresh air fans. Cleaned filters and applied antibacterial spray. No smell present at the time of inspection.
MSA-DCS | WA3279157 | Kitchen - Spout in pot wash leaking | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 14:00:00 | Pass | Kitchen Pot Wash spout spraying hot water. Check spout, weld up cracks causing leak, temporary repair. Return with new spout. Fit new parts & test.
MSA-DCS | WA3279183 | Unit 6, A & C day room - Oven needs new seal on oven door | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-13 10:00:00 | Pass | Replaced new doorseal
MSA-DCS | WA3279192 | Unit 6, C wing, Cleaning cupboard- light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-12 13:30:00 | Pass | Repaired damaged unit 6 store room
MSA-DCS | WA3279243 | Kaartdijin Mia - learning centre front doorlock & handle is faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-13 10:30:00 | Pass | Replaced and handles
MSA-DCS | WA3279285 | Gatehouse - Staff - Shower is leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-13 10:45:00 | Pass | COMPLETED
MSA-DCS | WA3279297 | Lenard, B wing - smashed window approx 1400-650 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-22 10:30:00 | Fail | WINDOW REGLAZED
MSA-DCS | WA3279360 | Boilerhouse, Reclaim tank pit - Water leaking into reclaim tank pit | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 13:18:00 | Pass | Inspected for leak following current water flow to relief valves and ports from boilers told maintance to advise boiler tronics to check there pipe work
MSA-DCS | WA3279366 | Unit 4, Control room - No hot water | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 14:08:00 | Pass | Checked over control room and boiler room located tap turned off turned back on worked fine
MSA-DCS | WA3279367 | Unit 2, C wing showers - tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-27 19:00:00 | Fail | Needs new tap have ordered in can take upto 5 days to arrive
MSA-DCS | WA3279429 | Crises care door 15 Service duct door between 5&6 cannot be locked | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 May 2020 | 2020-05-12 12:07:55 | 2020-05-11 14:00:00 | Pass | Service and repair duct door lock
MSA-DCS | WA3279453 | Unit 7 E8 Door hinge screws need retapping | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-18 16:00:00 | Fail | job completed - on site and replaced hinges
MSA-DCS | WA3279464 | Unit 14, D wing, D08 - main cell light not turning on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-13 08:30:00 | Pass | Repaired faulty lights in unit 14 d8
MSA-DCS | WA3279467 | Chapel - Lunch Room Door lock difficult to turn. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 12:30:00 | Pass | Replace bolt throw, service lock and replace worn hinges
MSA-DCS | WA3279468 | Unit 14, C wing - Tap leaking even when the taps are fully turned off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-12 15:00:00 | Pass | Remove and replace 1 times faulty quarter turn spindle in plumbing duct
MSA-DCS | WA3279478 | Unit 7, E8 & E12 - Ballasts need replacing/repairs | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-19 12:00:00 | Fail | Repaired lights
MSA-DCS | WA3279490 | Zone Control 2- Transformer in controller box is faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-11 15:00:00 | Pass | Installed new 24v transformer, Zone control #2
MSA-DCS | WA3279504 | Unit 6, Cell A19 & A20- Stop tap in service duct dripping and coming in to wing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 15:30:00 | Pass | Replaced with new top assemble
MSA-DCS | WA3279525 | CCU, linen Cupboard- Light ballast is faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-12 14:00:00 | Pass | Repaired light CCU Linen cupboard.
MSA-DCS | WA3279530 | Unit 10, Cell A5 - Broken tiles on floor around toilet | Hakea Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2021-04-20 15:00:00 | Fail | DAMAGED TILES REPLACED WITH NEW
MSA-DCS | WA3279579 | Indigo system keeps bringing up an alarm stating - see notes | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 May 2020 | 2020-05-11 21:03:22 | 2020-05-12 08:00:00 | Fail | Contacted site after leaving workstation on test and all had tested ok overnight and no issues with PC, Job complete
MSA-DCS | WA3280098 | Possible problems to arise from Generator Test on Tuesday 12th May | Casuarina Prison | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 10:30:00 | Pass | Performed phase failure test on generator. Checked and tested ATS controls. All ok
MSA-DCS | WA3280114 | Unit 6 - A & C- Exhaust fan not working/suspected dirty filters | Casuarina Prison | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-13 10:53:00 | Pass | Found to be switched off at circuit breaker, turned back on and tested ok.
MSA-DCS | WA3280132 | Metal shop and Cleaning shop- Cameras not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-11 15:30:00 | Pass | Traced fault to network switch on top of the spray booth in the metal shop. Repaired and tested ok.
MSA-DCS | WA3280144 | Unit 3, C wing, C4 - Cell osbervation light is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-18 08:30:00 | Pass | Repaired faulty lights
MSA-DCS | WA3280184 | L4 lights keep turning off after a period of time-see notes | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 11 May 2020 | 2020-05-12 14:53:09 | 2020-05-12 10:29:59 | Pass | Checked touch screen lighting controls for correct date/time of day. Checked for tripped circuit breakers in D/B, lighting operating correctly on arrival. Unable to alter incorrect day of week as screen is PIN protected, others to access (LYNX)
MSA-DCS | WA3280200 | Reception prisoners toilet Toilet won’t stop running | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 May 2020 | 2020-05-12 15:12:21 | 2020-05-12 10:00:00 | Pass | Once located cistern in wall Replaced outlet washer and inlet valve on invisis cistern
MSA-DCS | WA3280205 | unit 1 A3 Shower Drain & Sink Blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 11:18:00 | Pass | Removed hair and food unblocked basin and shower
MSA-DCS | WA3280207 | unit 1 B6 Sink Spout Broken water sprays onto the floor | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 12:30:00 | Pass | Removed broken air raider Replaced with new
MSA-DFES | WA3278909 | tunic room light does not seem to working at all | CFRS Armadale | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 11:00:00 | Pass | CompleteAttended site and located non working lights, replaced fluros and light fitting all in working order, notified staff and signed out at 11
MSA-DFES | WA3280296 | 1 and 2nd floor south west corner - maggots found | DFES Cockburn Emergency Services Complex | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 12:50:00 | Pass | Carried out a service for maggots at Cockburn Emergency Service Centre. There were reports of maggots on levels 1 and 2 in the south west corner of the building. Upon further inspection determined to be maggots coming from the wall cavity on level 2, most likely coming from a dead rodent located in the wall cavity due to a small odour in the area. Level 1 none could be located at time of inspection. Residually Sprayed attrathor at ground level In the effected area on level 2.
MSA-DFES | WA3285915 | RETROSPECTIVE WORK ORDER-Donot attend-EXTERNAL ALL APPEARS TO BE SECURE | CFRS Midland | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-11 09:20:00 | Pass | POWER FAIL TO MAINSEXTERNAL ALL APPEARS TO BE SECURE AND CORRECT NO SIGN OF FORCED ENTRY NO PERSON ON SITE
MSA-DTAG | WA3278655 | G Floor, Hallway- Plaster is coming away from the wall. | Perth Children's Court | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-07-15 12:36:00 | Fail | hole patched and painted
MSA-DTAG | WA3279145 | Level 6/7 Interanl staff stairwell metal step thread has lifted & bowed causing a trip hazard | Central Law Courts | GMP-BR-HO | Flooring | Concrete (FL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 14:00:00 | Pass | RE SECURED STAIR TREAD
MSA-DTAG | WA3279154 | Level 5/6 Internal staff stairwell Light flickering underneath the hand rail | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 11:45:00 | Pass | Job complete
MSA-DTAG | WA3279163 | Level 3 Lift lobby St George’s Tce end The down button has been pushed into socket | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-11 16:45:00 | Pass | Replaced level 3 down landing button and tested
MSA-DTAG | WA3279167 | Level 31 DMJC & Basement - Unison Client keeps kicking the user out. | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 11:30:00 | Pass | Attended site. Pacom to sync to controllers. Reset and checked all work stations. Relog onto Mirvac work station.Job completed
MSA-DTAG | WA3279380 | custody upper and lower Ceiling Lights not working | Mandurah Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-18 10:15:00 | Pass | Replaced faulty lamps in custody
MSA-DTAG | WA3279420 | Ground floor, Disabled staff toilet -The light isn’t working needs replacement/repair. | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 09:15:00 | Pass | Job complete
MSA-DTAG | WA3279432 | Level 4, Gents toilets (Hay st end ) - toilet lid is broken | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 15:00:00 | Pass | Complete
MSA-DTAG | WA3280225 | Ground floor, toilet behind listings - the light is out | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 11:30:00 | Pass | Job complete
MSA-DTAG | WA3280274 | Level 3, Court 38 - The light in the female toilet in the Magistrates lobby is not working. | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 09:30:00 | Pass | Job complete
MSA-DTWD | WA3278687 | A Block, paving to A Block South area on Royal Street needs repair | East Perth Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 14:30:00 | Pass | Remove pavers due to cut off and remove the roots under pavers - reinstalled the pavers again
MSA-DTWD | WA3278690 | D Block - Paving to D Block West End near A Block needs repair | East Perth Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 3 | CLOSE | 11 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 11:30:00 | Pass | Removed pavers to cut off and remove the roots under pavers and reinstalled
MSA-DTWD | WA3278864 | 6C Bricklaying ground floor kitchen Rat seen in kitchen numerous times. | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 11:30:00 | Pass | Baiting for rodents. Placed baited Beta station to appropriate spots. Follow up in 2 -3 weeks to check / rebait due to high activity.
MSA-DTWD | WA3278875 | Block 8 ground floor 8G3 Rat activity in ducting | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 12:15:00 | Pass | Baited duct to control rodent activity over 8G3 via access trap. A 2 week follow up is recommended to check up on activity.
MSA-DTWD | WA3278893 | Block 8, Grassed area east end- Broken lid on electrical pit | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-18 08:30:00 | Fail | Job complete
MSA-DTWD | WA3278908 | Block 9, Plant Room- Broken belts on Air Handling Unit 1 | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 15:30:00 | Pass | Job completed
MSA-DTWD | WA3278922 | S Block, Main Foyer- Lift not working | Mount Lawley Campus | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 10:05:00 | Pass | Lift1 MLT-Hydraulic :lift out of order with doors closed on ground floor. Found drive tripped with phase missing s/cam. checked all phases all ok reset drive and tested, could not reproduce fault left in service
MSA-DTWD | WA3278936 | Room AT205 Hot water urn not working | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 12:13:00 | Pass | Serviced and fixed hot water urn
MSA-DTWD | WA3278937 | B Block, Room B102 West Wall- Power out to GPOs on West Side of B102 | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 09:00:00 | Pass | Reset tripped rcd. Checked outlets no issue found
MSA-DTWD | WA3279069 | Bike shed door damaged cannot open by vandals over the weekend | West One Services | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 12:45:00 | Pass | work completed and signed off
MSA-DTWD | WA3279109 | Tower block L1 flickering light | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 13:45:00 | Pass | Job complete
MSA-DTWD | WA3279120 | Rat activity in both first and ground floor kitchens | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 13:00:00 | Pass | Cleaned and rebaited existing rodent stations and added baited stations as appropriate. Follow up in 2 - 3 weeks to check / rebait due to high activity.
MSA-DTWD | WA3279131 | Block 7, Rear Canteen- Broken Tap | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-13 17:17:00 | Pass | Instal, new tap
MSA-DTWD | WA3279132 | building 10, ground level, Outside 10G72 - Chilled water dispenser not working | Thornlie Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-06-17 12:00:00 | Fail | Replace leaking fountain that had blown the motor. Old fountain kept tripping power
MSA-DTWD | WA3279255 | tower block L3 flickering light | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-11 15:30:00 | Pass | Job complete
MSA-DTWD | WA3279258 | D block, Level 1, library - Replace/repair 8 off high level light globes | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-06-02 14:16:00 | Fail | Attempted to change faulty globes but even with a 12 foot ladder we could not reach, a one man scissor is required. Returned to site with scissor and replaced faulty globes, repaired conduit and cabling whilst working at a height
MSA-DTWD | WA3279291 | E block car park ground Replace pole light globes that are not operational | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 10:30:00 | Pass | Inspect car park pole lights, take measurements and photos to provide NM tafe a quote to replace top hat of pole lights as they no longer make the same size ballst which fits in the pole.Works to be closed until further notice
MSA-DTWD | WA3279400 | T block, rooms T031 & T032 - heating not working | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 11 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 13:00:00 | Pass | Job completed
MSA-DTWD | WA3279405 | D block, Meat trades area - Hand wash basin is damaged and needs repairs | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-06-10 19:00:00 | Fail | repaired basin, installed knee valve
MSA-DTWD | WA3280104 | No water to half of the building - staff Kitchen and female & Male toilets toilets | Armadale Campus - 145 Jull Street | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 11 May 2020 | 2020-05-12 17:00:00 | 2020-05-12 12:01:00 | Pass | Found isolation valve turned off, turned back on and removed handle. Suspected vandalism.
MSA-DTWD | WA3280174 | B Block, Rear Carpark-Car park Light Pole near plant room has loose cover at base | East Perth Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 11 May 2020 | 2020-05-18 17:00:00 | 2020-05-12 10:00:00 | Pass | Resecured inspection plate onto pole light
MSA-DCA | WA3285477 | Lift 1 - Call buttons fail to remain illuminated after being pressed | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 12 May 2020 | 2020-05-18 17:00:00 | 2020-05-13 12:00:00 | Pass | When responding to the callback dated 13.05.2020, the Schindler Technician found a problem with your equipment. Theintercom/phone power was worn out. Following our attendance, the equipment was left in service.
MSA-DCA | WA3285481 | Lift 2- Call buttons fail to remain illuminated after being pressed | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 12 May 2020 | 2020-05-18 17:00:00 | 2020-05-13 13:23:00 | Pass | Job completed - When responding to the callback dated 13.05.2020, the Schindler Technician found a problem with your equipment. Theintercom/phone power was worn out. Following our attendance, the equipment was left in service
MSA-DCA | WA3286137 | Lift 2 stuck on L1 | State Library of WA-Main Building-Level 1-1.4 - Server Room | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 12 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 14:45:00 | Pass | Not chargeable
MSA-DCA | WA3286456 | Front automatic entry doors are continuously opening & closing unable to lock | King Street Arts Centre-Main Building | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 12 May 2020 | 2020-05-12 19:37:23 | 2020-05-12 17:26:00 | Pass | Found pe sensor wire snagged by door when it closes. Disconnected sensor and remade connections. Disconnected drive brackets to disconnected door. Tightened up bi slide floor guide.Reconnected doors and tested, all ok.
MSA-DCS | WA3283876 | Security system not operating after medical PSU mains fail/battery low error | Pardelup Prison Farm-Administration, Health Centre, Prisoner Reception | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 May 2020 | 2020-05-12 10:28:20 | 2020-05-12 12:19:00 | Fail | Security system / UPS failed after long power as outage, both security system and UPS fully failed restored, checked UPS ok and all security functions ok
MSA-DCS | WA3285369 | Unit 3, Cell D6- Cell door has a split down right hand side | Hakea Prison | SPA-BR | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 12 May 2020 | 2020-05-14 17:00:00 | 2020-07-01 14:00:00 | Fail | Removed locks from old door, transferred locks to new door, installed new door, disposed of old door.
MSA-DCS | WA3285426 | Staff Room, Female Toilet- Cistern constantly leaking | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 May 2020 | 2020-05-14 17:00:00 | 2020-05-12 19:45:00 | Pass | Replaced toilet pan and induct cistern
MSA-DCS | WA3285468 | ODP, Transponder communication failure | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 May 2020 | 2020-05-13 07:41:06 | 2020-05-14 16:34:00 | Fail | Investigated, MDAS transponder fault, tested transponder in ODP, tested communication systems, unable to test further as other contractor had upgraded head end equipment. Referred to other contractor and confirmed fault has been corrected.Tested OKJob Complete
MSA-DCS | WA3285500 | Unit 7, D Wing- Fan not working, rear of oven plate come off, hot plate not working | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 12 May 2020 | 2020-05-14 17:00:00 | 2020-05-22 10:10:00 | Fail | Refitted oven fan guard correctly, oven fan free to spin but not rotating. New fan motor required. Returned 22/5 and fit new fan motor. Test oven ok all functional.
MSA-DCS | WA3285503 | Unit 7, Cell C4- Extractor fan in cell shower not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 09:30:00 | Pass | Checked over exhaust fan found to be running ok, but no airflow from grille,found damper in duct nearly closed,opened up and tested airflow,now has adequate ventilation.
MSA-DCS | WA3285515 | MPU (8) - M12 wall mount in the yard of M12 is rusted | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-07-23 23:00:00 | Fail | Tighten bolts on bracket/wall mounted strike.Measure wall mount strike.Install custom made wall mount strike.
MSA-DCS | WA3285529 | unit 5 house 1/entry low battery report to transponder | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 May 2020 | 2020-05-13 08:15:30 | 2020-05-12 11:00:00 | Pass | Attended site and investigated the fault.Checked MDAS system in control room and cleared all transponder troubles.Checked Transponder 10 in Unit 5 house 1 .Checked wiring and connections on Transponder and battery.Conducted test.All ok at departure.21/5/20 job recalled by site. replaced battery for new. found existing battery collapsed after generator testing
MSA-DCS | WA3285535 | MPU(8), Cell M11- Viewing hatch has been smashed | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-18 16:00:00 | Fail | VIEWING HATCH REPLACED
MSA-DCS | WA3285581 | Unit 5, Cell A14- Cell light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-14 08:00:00 | Pass | Repaired light
MSA-DCS | WA3285583 | Main Boardroom Fluorescent light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-14 09:00:00 | Pass | Repaired boardroom light
MSA-DCS | WA3285620 | Security office- CCTV is offline | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 May 2020 | 2020-05-12 16:55:02 | 2020-05-12 16:30:00 | Pass | Rectified the media converter power connection and fixed the comms failure of indigo ws. Job completed.
MSA-DCS | WA3285643 | Unit 1, Cell A8- large window broken | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 12 May 2020 | 2020-05-13 09:09:36 | 2020-05-13 12:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3285651 | Unit 1, Cell A5- Cell & hatch window is smashed | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-13 14:00:00 | Pass | CELL & OBS WINDOWS RE GLAZED
MSA-DCS | WA3285665 | Unit 1, Cell A5- Cell smashed up bunk side support damaged | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 15:00:00 | Pass | Job cancelled by site
MSA-DCS | WA3285763 | unit 4 cell C 12 door skin requires refixing | Karnet Prison Farm | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2021-01-18 12:45:00 | Fail | NEW DOOR INSTALLED
MSA-DCS | WA3285764 | CCU (11) door lock on cell C3 not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 17:30:00 | Pass | Re install rebuilt lock and adjust escutcheon
MSA-DCS | WA3285817 | Metal Shop - Workshop repair to lights | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 15:30:00 | Pass | Repaired lights in metalshop
MSA-DCS | WA3285848 | L4 lights keep turning off after a period of time-see notes | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | LYNX INTEGRATED SYSTEMS | 1 | CLOSE | 12 May 2020 | 2020-05-13 10:22:42 | 2020-05-12 15:00:00 | Pass | To be closed out cost to date
MSA-DCS | WA3285855 | B Wing Showers Basin Tap leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 13:30:00 | Pass | Shut off mains removed hot and cold taps reseated set and replaced washers o rings and valves
MSA-DCS | WA3285875 | -BFRcontrol unit 10 PDA transponder low battery | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 May 2020 | 2020-05-13 10:31:53 | 2020-05-12 15:30:00 | Pass | Intermittent fault with LOW BATTERY alert alarming and resetting on MDAS PC. Used replacement battery for testing. Battery tested ok. Transponder board tested ok. AC power and Comms ok. Traced fault to lead running from the battery to the transponder. Unable to repair the plug. Removed and replaced lead with site spare. Load tested battery and cleared alarm message on PC. Parts used:Consumables
MSA-DCS | WA3285918 | MPU (8), Cell M11, M12 & M16- Electircal faults with powerpoints | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 13:00:00 | Pass | Repaired damaged cells in MPU Waited access for cells
MSA-DCS | WA3285941 | SHU (9) - Control Room download footage for security in SHU | Casuarina Prison | WSM-GR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-13 14:30:00 | Pass | Down loaded cctv video as requested bysecurity. Following day SecurityManager requested further information regarding cell call system and calling times. All information supplied as requested.
MSA-DCS | WA3285951 | there are some error messages on the CCTV server and the time seems to be out | East Perth | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 May 2020 | 2020-05-13 11:05:52 | 2020-05-12 13:45:00 | Pass | Cleaned up time and error messages.
MSA-DCS | WA3285981 | MPU (8) - Tap in shower has been pulled off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 14:00:00 | Pass | Reinstall shower tap handle and test
MSA-DCS | WA3285993 | Armoury - fluro lights are out and need replacing | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 12 May 2020 | 2020-05-13 11:24:39 | 2020-05-19 09:00:00 | Fail | Repaired lights
MSA-DCS | WA3285994 | Education- GPO broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 09:30:00 | Pass | Investigate and replace broken gpo and mounting block and reterminate damaged cable.
MSA-DCS | WA3286009 | Skills w/s- GPO faulty not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 13:00:00 | Pass | Investigate skills gpo not working. Found fault on circuit. Repaired fault and replaced gpo’s
MSA-DCS | WA3286142 | Driveway camera # 5 is not operating correctly, blurry | Pardelup Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 May 2020 | 2020-05-13 12:22:23 | 2020-05-12 13:00:00 | Pass | Camera #5 on radio tower in front driveway is failing unable to restore i mage to clear picture as i mage is heavily distorted reset both camera and equipment attached with no change, access to camera required (extremely high)SEME have provided a quotation to install new cameras in an alternative location due to access being impractical.No further works under this job - Cameras are still operational
MSA-DCS | WA3286162 | Unit 6, D Wing Cleaning Store- Light switch is faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 14:00:00 | Pass | Replaced damaged switch
MSA-DCS | WA3286189 | Unit 4 Perimeter fence - microphonics multiple alarms | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-08-12 07:00:00 | Fail | Job to be completed under work order WA3495718 SEME number 90229037.
MSA-DCS | WA3286190 | Education, Room 9 courtyard lock sticks | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-28 11:30:00 | Fail | Replaced locks
MSA-DCS | WA3286198 | Amenities building entry door self closer not operating correctly, causing door to slam shut | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-25 14:30:00 | Fail | REPAIRED ENTRY DOOR/ DOOR CLOSER REPLACED
MSA-DCS | WA3286254 | Unit 13 - A wing landing grill motor lock broken | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 14:30:00 | Pass | re install rebuilt lock and adjust strike.
MSA-DCS | WA3286326 | Male Urinal on Lvl 4 is out of order and Male Urinal Lvl 3 has a strong urine smell (possible block) | East Perth-Main Building-Level 4 | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 May 2020 | 2020-05-13 14:00:32 | 2020-05-15 15:00:00 | Fail | Complete
MSA-DCS | WA3286394 | Internal prisoners visits search room door jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 12 May 2020 | 2020-05-13 14:44:40 | 2020-05-12 16:15:00 | Pass | Repaired lock
MSA-DCS | WA3286397 | PTZ 3 - not working | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 May 2020 | 2020-05-12 22:52:30 | 2020-05-13 12:00:00 | Fail | Found PTZ camera 3 offline, unable to ping device, traced issue to network switch failing to communicate after storm, reset and tested fully operational.
MSA-DCS | WA3286442 | orientation centre Vinyl repair to threshold of 2nd door (double) entering orientation | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2021-01-19 13:45:00 | Fail | VINYL FLOOR REPAIRS COMPLETED
MSA-DCS | WA3286467 | unit 8 D4 Waste water leaking from back of pan | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 May 2020 | 2020-05-13 15:44:45 | 2020-05-13 11:30:00 | Pass | Pulled out old toilet replaced Pan rubber then reinstalled toilet
MSA-DCS | WA3286500 | U8 -A/B C/D Dayroom cleaning cupboards - Stop taps leaking and missing handle | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 14:35:00 | Pass | Shut off mains replaced top assembly
MSA-DCS | WA3356461 | Repair electrical fault in perimeter | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 May 2020 | 2020-05-18 17:00:00 | 2020-05-18 12:00:00 | Pass | Pit investigation and walk around as per consultants instructions
MSA-DFES | WA3285833 | Engine room doors are all squeeking | CFRS Vincent | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 12 May 2020 | 2020-05-13 17:00:00 | 2020-06-16 13:45:00 | Fail | Technicians attended the site of Vincent Fire Station Bifold doors A400295780 on 12/05/2020. Following full test and inspection of door components identified fault was some engine bay doors were noisy, in need of lubrication.Lubricated drive shaft to quieten doors down a bit. Shaft loose and needs extra bracings.16/06/2020. Drilled out holes in drive shafts of 6 bi-fold doors and fitted new high tensile bolts to strengthen them. Carried out full test of operation ok.Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3285873 | whole building external doors, swipe cards not working | CFRS Vincent | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 12 May 2020 | 2020-05-13 17:00:00 | 2020-06-12 17:15:00 | Fail | 12/5/20 - Dylan ParslowInvestigated issues with electric locks.All control equipment working correctly.Advised locks onsite are pre-loaded electric strikes, and require more force to open.Advised to wait 2 seconds after swiping card before opening doors.Found stairwell door faulty, requires replacement. BRAF submitted.22/5/20 - Dean SimpsonReplace faulty electric strike on stairwell ground external door.All tested ok.
MSA-DFES | WA3286291 | Bay 2 rear engine room door- support bracket has failed | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 12 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 08:15:00 | Pass | Technician attended the site of Welshpool Fire Station on 12/05/2020identified fault was hinge 4 to left side of door was broken. Required to make temporary repairs and tested ok.Returned on site on 13/05, removed damaged hinge and replaced with new.
MSA-DTAG | WA3285537 | Security gate swipe card not working | Rockingham Justice Complex | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 May 2020 | 2020-05-12 12:13:45 | 2020-05-25 12:45:00 | Fail | Pickup part and travel to site to replace the faulty BREAKGLASS UNIT and CARD READER. Tested it all ok after replacement.
MSA-DTAG | WA3285631 | Buss P Chambers- Light tubes not working in & around Presidents Chambers | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 12 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 08:00:00 | Pass | Replaced faulty lamps in and near presidential chambers
MSA-DTAG | WA3286201 | Bio clean - blood in male staff toilets | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Cleaning (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-13 18:30:00 | Pass | Cost of labour @ $50/hour up to 4 hours including call out
MSA-DTAG | WA3286242 | L29 clipsal panel switches not working properly need to be replaced with hand sensor | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 12 May 2020 | 2020-05-13 17:00:00 | 2020-05-15 11:30:00 | Fail | Installed 2 x new Touchless Exit Buttons on Level 29, tested, all OK.
MSA-DTAG | WA3286286 | ground registry One of the Emergency backup light lights up at random times | Midland Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-12 16:00:00 | Pass | Replaced emergency downlight, replaced 2x LED battens including emergency batten light.
MSA-DTAG | WA3286341 | Door leading into the kitchen off the main waiting area- Door not locking | Rockingham Justice Complex | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-13 11:00:00 | Pass | Attend site,replace faulty digital keypad lever handle lock and retro fit new model for correct operation.
MSA-DTWD | WA3285465 | B Block, Room B102.5 - Barrel Lock is faulty | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 12 May 2020 | 2020-05-18 17:00:00 | 2020-05-12 14:50:00 | Pass | service to lock and replace cylinder components to Room B102.5
MSA-DTWD | WA3285493 | ground workshop 12 hi bay lights in workshops require replacing due to failure, Various locations | Clarkson Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 12 May 2020 | 2020-05-18 17:00:00 | 2020-05-18 15:30:00 | Pass | Rectified faulty globes across all work shops
MSA-DTWD | WA3285504 | ground workshop East side. Replace multiple flouros that are not working-see notes | Clarkson Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-14 15:00:00 | Pass | Replaced various fluros and globes across clarkson campus
MSA-DTWD | WA3285787 | C Block, Remove fallen tree west side of C Block | Balga Campus | GMP-BR | Landscaping & Gardening | General Tree Works (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-22 10:50:00 | Fail | Labour 6 staff @ $100 per hour for 4.5 hours $2,700Marterials: Chipper truck and chipper, cherry picker 4.5 hours @ $200 per hour $900Environmenall: Green waste removal $200Budget $3,400. Actuals rate $3,800. Claim $3,400.
MSA-DTWD | WA3285819 | B Block, External North Side- Gate not latching, frame rusted out | Midland Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-09-04 15:00:00 | Fail | As per sig slips
MSA-DTWD | WA3285868 | U block ground security panel showing low battery, needs replacing | Joondalup McLarty Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 12 May 2020 | 2020-05-13 17:00:00 | 2020-05-12 16:00:00 | Pass | Install, test DGP backup battery DGP 5, DGP 6, Tecom challenger one in U, V & P Block. All ok. Sign in and out key card access
MSA-DTWD | WA3285871 | Block 8, G Floor, Room 8G44/45- Lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-21 13:38:00 | Fail | Attended site and signed in. Replaced further tubes starters and ballasts as required. All lights working. Job complete
MSA-DTWD | WA3285924 | T Block- Air Con is not functioning on level 2 | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 12 May 2020 | 2020-05-13 17:00:00 | 2020-05-13 13:00:00 | Pass | Monitoring reattending tommorowJob now complete. Units on lvl 2 at set temp
MSA-DTWD | WA3285990 | Canteen - HWS not operation properly | Rockingham Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-12 16:12:00 | Pass | Rp lace parts on hws that weren’t working
MSA-DTWD | WA3286018 | Block 3, Room 3B Workshop- Isolate power to Vehicle hoist | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-26 17:00:00 | Fail | Attended site and signed in. Located hoist. Isolated cabling and made safe on roof. Unbolted service pole from roof. Ready to take away. Job complete
MSA-DTWD | WA3286050 | H Block, Cleaners storeman- 4 x bay lights are not working | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-18 09:00:00 | Pass | Repalced faulty huh bay lights with new LED.all working properly.job completed
MSA-DTWD | WA3286103 | B block ground skills area hot water unit keeps tripping rcd, suspect element faliure | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-18 10:30:00 | Fail | COMPLETED
MSA-DTWD | WA3286321 | F Block, Room FT17- hot water system is leaking | Carlisle Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-14 10:30:00 | Pass | Burst/ leaking unit, needs to be replaced
MSA-DTWD | WA3286369 | L3 plant room Boiler N1 on Fault | Perth Campus B2 | GMP-BR | Mechanical Services | Boilers (MS) | Equans Mechanical Services Australia | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 10:00:00 | Pass | MEET BOILERTRONICS ONSITE RUN THROUGH ISSUES. MANUALBOILERS ON. TRIED MULTIPLE.STOP STARTS AND BOILER WOULDN'T TRIP GAS SOLENOIDS GREASED PILOT. CLEANED. WILL MONITOR SETUP BOILER ALARM TRENDING ON BMS. COMPLETE PAPERWORK
MSA-DTWD | WA3286491 | A Block Upstairs east end of block A55 Directors Office has worn carpet | Midland Campus | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 12 May 2020 | 2020-05-19 17:00:00 | 2020-05-20 14:48:00 | Fail | Carried out carpet repairs as requested by site
MSA-DTWD | WA3286556 | Customer Service Centre Blind assembly fallen down | Thornlie Campus | GMP-BR | Furniture | Office Furniture (FU) | NEYLOR | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-15 13:00:00 | Pass | Re-fitted blind
MSA-DTWD | WA3286562 | Block 10 Office 10F6 Faulty door closer to staff office | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-20 09:15:00 | Fail | Attended site and attempted to adjust door closer without success. Door closer has now been replaced
MSA-MRWA | WA3286265 | Courtyard outside of amenities room- Ice Machine making noises & not producing ice | Materials Engineering Branch | GMP-BR | Refrigeration | Ice machine (RE) | Water2water Pty Ltd | 2 | CLOSE | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 13:24:00 | Pass | ATTENDED AND DIAGNOSED ICE MACHINE - NEEDS TO BE REPLACED WAITED FOR APPROVAL AND WE WERE ASKED TO HOLD OFF ON THE ORIGINAL APPROVAL TO REPAIR AS CLIENT WANTED MORE TIME TO CONSIDER - CLIENT ENDED UP WANTING TO REPLACE NOT REPAIR ... CLOSED OUT AFTER BEING ADVISED TO USE NEW WO FOR REPLACEMENT.
MSA-MRWA | WA3286267 | ground Bridge Compound Office Western Entry secure fix top stair nosing it is coming loose-see note | Materials Engineering Branch | GMP-BR | Carpentry | Staircases, Balustrades and Handrails (CA) | MR - Handyperson - PFM | 2 | COMP | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 14:01:00 | Pass | Fixed new screws to the stairs
MSA-MRWA | WA3286270 | Front Entrance - Lifting angles edging on the front entrance ramp near flag poles, please remediate | Materials Engineering Branch | GMP-BR | Paving & Roadworks | Paving (PR) | MR - Handyperson - PFM | 2 | COMP | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 12:30:00 | Pass | Fixed skirting with silicone and mounting screws
MSA-MRWA | WA3286275 | Staff Carpark - Uneven brickwork/ lifting paving near staff carpark please level | Materials Engineering Branch | GMP-BR | Paving & Roadworks | Paving (PR) | MR - Handyperson - PFM | 2 | COMP | 12 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 12:00:00 | Pass | Pulled up pavement cut out root and relayed pavement
MSA-DCA | WA3291647 | Level 4 plant room, AC4 humidifier has a leaking hose. | Art Gallery of WA - James St - Main Building (Block B)-Level 4 - Roof Ventilator Plant | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 13 May 2020 | 2020-05-14 17:00:00 | 2020-05-13 16:30:00 | Pass | Steam leaking from a corroded section of piping in AHU 4. Contractor attended site and replaced the faulty water trap tube on the pressure gauge.
MSA-DCA | WA3298555 | distribution board, reconnect HWS-Please attend Thursday Rick Hill is aware | PICA-Main Building-Ground Floor | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-14 10:00:00 | Pass | Senna + Connor HWU was identified and reconnected 9-10
MSA-DCS | WA3290944 | Boilerhouse- In Line relief valve faulty | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 13 May 2020 | 2020-05-15 17:00:00 | 2020-05-27 20:00:00 | Fail | Carry out repairs to calorifier
MSA-DCS | WA3290951 | Unit 4, B Wing Dayroom- Toaster GPO faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 May 2020 | 2020-05-15 17:00:00 | 2020-05-14 13:30:00 | Pass | Replaced gpo
MSA-DCS | WA3290954 | Laundry, Prisonsers toilet- Cistern cracked & leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 16:06:00 | Pass | Removed panel in wall to get to cistern once removed replaced inlet valve/outlet washer and button mechanism
MSA-DCS | WA3290962 | Turner, B wing- Smashed sash window approx 450x650 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 13 May 2020 | 2020-05-15 17:00:00 | 2020-05-22 12:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3290966 | Gatehouse, Entry Door- Glass sliding entry doors slow to open | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 May 2020 | 2020-05-19 17:00:00 | 2020-05-13 13:00:00 | Pass | Travelled to site, investigated fault on sliding door. Door working correctly however door requires adjusting of speed sensitivity, sliding door is not related to Seme works but rather door technician possibly Dorma. Job complete
MSA-DCS | WA3291030 | Front Gate, Key Control- Key watcher Key 29 not registering | Melaleuca Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 May 2020 | 2020-05-14 07:44:13 | 2020-05-13 11:30:00 | Pass | Travelled to site, investigated fault and reset keywatcher and software on PC. Tested all functions and all tested ok. Instructed security on manual release of key functions on software and advised staff to contact IT department and gain access to keypro software to be able to install on multiple Pcs. If issue Re occurs then recommend replacing with new key slot. Job complete
MSA-DCS | WA3291047 | Unit 4, D Wing, Cell D13- Viiewing hatch door broken | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 May 2020 | 2020-05-19 17:00:00 | 2020-06-08 12:00:00 | Fail | DOUBLE UP - WORK COMPLETED ON WA3343986
MSA-DCS | WA3291049 | MPU(8), Cell M20- Light isnt working properly | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 May 2020 | 2020-05-19 17:00:00 | 2020-05-13 15:00:00 | Pass | Repaired damaged cell light and gpo in m20 MPUWaited access for cell
MSA-DCS | WA3291051 | C Wing Unit 2 Cell C8 main fluro light blown | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 May 2020 | 2020-05-19 17:00:00 | 2020-05-14 11:30:00 | Pass | Repaired faulty lights in unit 2 c8
MSA-DCS | WA3291062 | Bakery - Workshop Berto micer timer not functioning | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-15 16:15:00 | Pass | 15/5/20 - Arrived on site, found contactor block filled with bugs, removed & cleaned out. Reassembled & tested, all components for correct function and all okay.
MSA-DCS | WA3291141 | Investigate faulty PSU’s to Units 13 & 14 | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-06-17 14:48:00 | Fail | Due to the delay in getting the replacement PSU's all Vesda units checked for faults and the below units had charger faults and required new PSU'sU14 B/D WING CELLS 3 & 4 U14 B/D WING CELLS 11 & 12U13 A/C WING CELLS 15 & 16
MSA-DCS | WA3291273 | Control Room, Front Gate- Tamper alarms on duress system | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 May 2020 | 2020-05-14 09:17:41 | 2020-05-15 17:00:00 | Fail | Repair has been conducted under job # WA3295871
MSA-DCS | WA3291284 | Unit 6, B4 - tap dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-13 11:30:00 | Pass | Remove and replace 1/4 turn spindle in basin in Cell
MSA-DCS | WA3291287 | Skills switchboard Main rcd not resetting | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-14 08:30:00 | Pass | Investigate Skills RCD not re-setting, was a faulty unused relay, disconnected
MSA-DCS | WA3291290 | Unit 1, Cell B11- Toilet not filling up all the time | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-13 12:30:00 | Pass | Remove Inlet valve and clean out sand, reinstall and test.
MSA-DCS | WA3291294 | Unit 1, Cell B12- Toilet not filling up all the time | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-13 09:28:00 | Pass | Remove and replace 1 times faulty Inlet valve in cistern
MSA-DCS | WA3291459 | Main control - cell call handset is crackling when the button is pressed and makes the call Intermit | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 May 2020 | 2020-05-14 09:59:46 | 2020-05-13 14:15:00 | Pass | Attended site and investigated the fault.Found that CI-OH handset is faulty and requires replacement.Replaced with new (critical spare from site).Tested.All ok at departure
MSA-DCS | WA3292386 | Unit 4, A Wing, Cell A02- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-14 12:00:00 | Pass | Plunge sink to clear blockage.
MSA-DCS | WA3292454 | Unit 5 - A4 SINK NOT DRAINING CORRECTLY | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-14 13:00:00 | Pass | Plunge sink to clear blockage.
MSA-DCS | WA3292544 | Unit 5, Cell B2 - Window sliding down | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-25 10:00:00 | Fail | BALANCES & FEET RENEWED
MSA-DCS | WA3294951 | Unit 1, B4 - Toilet cistern cracked and leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 09:40:00 | Pass | Pulled apart cistern replacing outlet washer and reinstalled
MSA-DCS | WA3295124 | UNIT 4, C11 - light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-14 14:30:00 | Pass | Replaced switch
MSA-DCS | WA3295336 | External Gardens, SOG’s training shed - Damaged sprinkler near SOG’s training shed | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | Pumps n Pipes | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-15 10:00:00 | Pass | REPLACED 3 FAULTY BROKEN SPRINKLERS
MSA-DCS | WA3295337 | Unit 6 - A & C day room sink leaking water/AC wing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-13 13:30:00 | Pass | Adjust tap seat in kitchen to prevent water leaking into cabinet
MSA-DCS | WA3295622 | External Gardens - Burst pipe next to steps to carpark leading to Driscol Drive | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Pumps n Pipes | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-15 12:00:00 | Pass | BROKEN END CAP, CAP REPLACED
MSA-DCS | WA3295780 | Temporary sally port – CCTV is offline | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 May 2020 | 2020-05-14 12:34:05 | 2020-05-14 09:54:00 | Pass | Contacted site and PFM.Job to be signed off
MSA-DCS | WA3295871 | MDAS - pole 14 and Pole 1 - temper? | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 17:00:00 | Pass | Replaced 2x receiver duress enclosures for new, drilled mounted and sealed, conducted repai re on ex listing receivers and tested i intermittent alarms appear to have cleared. Contacted site upon arrival back in Perth and alarms hgave not returned. No further action required.
MSA-DCS | WA3296021 | Unit 6, Cell N6- Toilet will not flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 10:58:00 | Pass | Removed broken cistern replacing with new one and pipe work
MSA-DCS | WA3296122 | Unit 6, Cell N1 & N7- Master lock intermittently jams and takes several attempts to lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 13 May 2020 | 2020-05-14 12:49:25 | 2020-05-14 15:30:00 | Fail | repairs to lock
MSA-DCS | WA3296461 | Unit 13, Cell C4- light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-14 08:30:00 | Pass | Repaired faulty lights in unit 13 c4
MSA-DCS | WA3296777 | Unit 14 - B4 cold tap in shower faulty/leaking B4 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-13 15:00:00 | Pass | Replace 2 x quarter turn spindles and clean out flow restrictor in basin
MSA-DCS | WA3297850 | ODP Rooms 6, 7, 8 as it is blowing Hot Air and not Cool Air | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-14 15:04:00 | Pass | BMS is still offline but AC system is running
MSA-DCS | WA3298427 | Visits area- network error master state offlline | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 May 2020 | 2020-05-14 13:53:58 | 2020-05-15 15:53:00 | Fail | Investigated fault, suspect computer database issue, loaded site data on laptop and analysed data. Provided phone support to site to diagnose and repair fault. Tested OKJob Complete
MSA-DCS | WA3298571 | Zone control 2, sallyport roller door - Requires service as grinding while opening and shutting | Hakea Prison | GMP-BR- HO | Building | Roller Shutters (BU) | UNIVERSAL DOORS | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-25 10:15:00 | Fail | No approval given
MSA-DCS | WA3298600 | Reception Prisoners disabled toilet Outlet pipe from cistern requires replacement as hole in pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 12:16:00 | Pass | Removed hob wall around flush pipe to gain access to replace broken flush pipe
MSA-DCS | WA3298606 | reception VP door outside handle loose mech is not engaging | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 13 May 2020 | 2020-05-14 15:41:21 | 2020-05-19 14:45:00 | Fail | Job completed - attended site to fix door handle which is loose on VP reception door. Serviced and repaired lock with parts supplied by DOJ
MSA-DCS | WA3298615 | Assessments Dining room external door Plate drops preventing key from entering barrel | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-18 15:00:00 | Pass | ATTENDED site and repair lock as require
MSA-DCS | WA3298623 | Generator shed area - security DGP 5 off-line | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-06-24 16:05:00 | Fail | Repaired comms fault with generator shed DGP.Tested OK.Job CompleteParts:Consumables
MSA-DCS | WA3298626 | kitchen milk freezer fridge no cold air SITE COSTED | Wooroloo Prison Farm | WSM-BR-SITE | Refrigeration | Freezers (RE) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 13 May 2020 | 2020-05-13 20:00:09 | 2020-05-14 12:00:00 | Fail | Condenser fan replaced on milk coolroom.Refrigerant leak repaired on vege coolroom.
MSA-DFES | WA3295893 | Dorm 2- Shower head is broken | CFRS Belmont | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 13 May 2020 | 2020-05-14 17:00:00 | 2020-05-13 15:39:00 | Pass | Replacing the shower and rail in the dorm 2
MSA-DFES | WA3298496 | Bathroom - Soap tray in shower cubicle broken | CFRS Daglish | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-21 15:30:00 | Fail | Broken soap dish in shower. Not screw in type but imbeded into tiling so tiling needs to be chipped away. Need Tiler to resolve issue.
MSA-DFES | WA3298508 | G level- TV antenna blew over in storm, laying on side on roof | DFES Rescue Helicopter Base | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-06-19 15:15:00 | Fail | Need to replace rusted and damage antenna and mount with new
MSA-DTAG | WA3291304 | Level 11, PRB Board rooms - The air conditioning appears to not be working and all three air conditi | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-13 13:00:00 | Pass | Reset bms outstation. All working good.
MSA-DTAG | WA3291305 | L10 First aid box that is attached to corridor wall – fixings are loose | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-14 08:30:00 | Pass | FIRST AID BOX RE SECURED
MSA-DTAG | WA3291597 | Level 10, Front counter -Zip tap in the main staff café not working. Flashing on all lights & not ru | Westralia Square | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-14 12:25:00 | Pass | System in leak fault on arrival. Inlet solenoid faulty and leaking from the Zip JG Fittings Kit + Replaced inlet solenoid . Cleaned brass fittings. Ran further tests, tanks filling, normal operation
MSA-DTAG | WA3291627 | Level 3 – Staff Toilet Staff toilet not flushing - see notes | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-26 16:00:00 | Fail | Complete
MSA-DTAG | WA3298492 | 1903 FIP Reciprocal work order required for ARA Fire to reset fire panel -see notes | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-13 15:00:00 | Pass | Brigade attended site for a detector alarm in basement staff amenities. They disabled device after a staff member burnt toast in staff room.Enable device and returned it to normal.
MSA-DTWD | WA3290939 | Car park area and driveway. Multiple outdoor lights are faulty | Clarkson Campus | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 3 | CLOSE | 13 May 2020 | 2020-05-19 17:00:00 | 2020-06-02 14:14:00 | Fail | Inspected lights and sourced parts. Returned the next day and replaced faulty parts to lights not working. After replacing parts one circuit for the pole lights in front of admin was still tripping out and after various testing throughout the circuit, the cable we found there has a fault from the board to the first light, causing the circuit to trip. We will need to re attend and replace faulty cable and rectify the issue
MSA-DTWD | WA3290968 | T Block, Room T032- Air Con has a fault, room not heating up | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 13 May 2020 | 2020-05-15 17:00:00 | 2020-05-13 13:00:00 | Pass | Job completed 13-5
MSA-DTWD | WA3291104 | ground female toilet Hand basin taps seized and leaking | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-13 13:24:00 | Pass | Install new taps And mini stops
MSA-DTWD | WA3291206 | E block, ground level, loading dock - Repair water leak from ceiling area | Joondalup Kendrew Campus | GMP-BR | Building | Ceiling (BU) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 13:00:00 | Pass | removed split aquatherm pipe and replaced section with copper piping
MSA-DTWD | WA3291396 | H block, Ground level, H06 - Tap in H Block Prep area is dripping. | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Materials (PD) | Techworks Plumbing | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 07:50:00 | Pass | Locate and shut off isolation valve
MSA-DTWD | WA3291591 | BLD 822, Flat A, Bathroom- Faulty cistern | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-05-14 13:00:00 | Pass | Repaired faulty cistern
MSA-DTWD | WA3291852 | G block ground welding bays Lack of Gas pressure in the welding OXYGEN Gas line in the Welding bays | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 13 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 10:30:00 | Pass | Got welding bays working after purge
MSA-DTWD | WA3292878 | Campus - Potential water leak throughout the campus grounds | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 13 May 2020 | 2020-05-18 17:00:00 | 2020-07-30 10:50:00 | Fail | fixed multiple small leaks and monitored
MSA-DTWD | WA3294413 | A block, grounf level, AF20 courtyard side door - Electric keypad not unlocking entrance door lock | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-06-03 10:26:00 | Fail | 15/05/2020, 930-1015Loose wire connection to lock rewired and tested ok.
MSA-DTWD | WA3298151 | Corridor Level 1- Fire Air compressor unit is faulty | Perth Campus B2 | GMP-BR | Equipment | Compressors, Generators (EQ) | Equans Mechanical Services Australia | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-20 12:00:00 | Pass | CARRY OUR WORKS AS PER BRAF. WITNESSED SUCCESSFUL TEST OF NEW FIRE VALVES AND SOLENOIDS.
MSA-DTWD | WA3298484 | Bad smell coming from Safe Room - Possible dead animal | Armadale Campus - 40 Commerce Ave | GMP-BR | Pest Control | General Pest (PC) | High Tech Pest Control | 1 | CLOSE | 13 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 09:00:00 | Pass | Placed 1 deodoriser bag in room, hanging from ceiling.No carcass located.Noticed that Ditrac(R) has been used by Complete which kills rodents veryquickly and increases chance of they dying inside the building and causingunpleasant odour.
MSA-DTWD | WA3298541 | E block ground east end-Evaporative unit leaking water | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 13 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 10:00:00 | Pass | Site to engage plumber for further action after our works
MSA-MRWA | WA3291257 | Basement, Programmed Office- Supply ceilig tiles as discussed | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Ceiling (BU) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 08:00:00 | Pass | Ceiling tiles supplied
MSA-MRWA | WA3297331 | Lvl 6, Lobby- Pull all infill pieces and affix with appropriate adhesive | Don Aitken Centre MRWA Head Office | GMP-BR | Building | Materials (BU) | MR - Handyperson - PFM | 1 | COMP | 13 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 08:00:00 | Pass | Checking and glueing panels that are required
MSA-MRWA | WA3298430 | level 8, kitchenette - Flickering light please replace. | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 13 May 2020 | 2020-05-14 17:00:00 | 2020-05-13 15:25:00 | Pass | Replaced 3 tubes in meeting room
MSA-MRWA | WA3298568 | ground admin building Intermittent trip of New Office PIR 360 degree sensor please remediate | Materials Engineering Branch | GMP-BR | Security | Monitoring (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 13 May 2020 | 2020-05-20 17:00:00 | 2020-05-20 12:45:00 | Pass | 20/5/20 - Dylan ParslowInvestigated issue with office PIR.Tested input, correctly working and currently sealed. No alarms indicated from monitoring since 10/5/20.
MSA-DCA | WA3302300 | ground level, Quarantine Lab - high pressure on gauge outsidequarantine lab in HBRC. | Collection and Research Centre Welshpool-Harry Butler Centre-Ground Floor | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 14 May 2020 | 2020-05-15 17:00:00 | 2020-05-14 16:30:00 | Pass | Attended site 14-5-20 1500. Quarantine laboratory zone pressure too high with in the laboratory creating a loud whistling noise. Applied tests and checks to find AHU7 and sequential extract fans operative for the vacant laboratory ? Deactivated enabled status. Pressure to have normalised with no loud whistling present. Left site 14-5-20 1630
MSA-DCA | WA3302326 | Retrospective work order donot attend-Fault on FIP, orange fault light, zone unknown | Shipwreck Galleries-Administration Building -Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 14 May 2020 | 2020-05-14 17:00:00 | 2020-05-14 13:00:00 | Pass | Tech attended and reset panel. Cause unknown.
MSA-DCS | WA3301340 | Unit 1, Cell D10- Window wont stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 May 2020 | 2020-05-20 17:00:00 | 2020-05-27 10:30:00 | Fail | REPAIRED CELL WINDOW
MSA-DCS | WA3301343 | Unit 13, B & D Wing- Hot water unit in kitchen digital screen broken. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 14 May 2020 | 2020-05-20 17:00:00 | 2020-05-22 11:00:00 | Fail | Replaced screen Fascia Assy/Electronic Timer to Rheem 25 L BWU URN
MSA-DCS | WA3301345 | CCU(11), Cell D7- Door is stiff to turn | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 14 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 14:30:00 | Pass | Reinstalled rebuilt lock
MSA-DCS | WA3301352 | Entry Building, Air lock doors opening at the same time | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 May 2020 | 2020-05-14 11:08:58 | 2020-05-14 10:00:00 | Pass | Attended site and found interlocking group had been disabled due to utilising key override, located workstation and re enabled interlocking groups through programming. All programmed and tested doors, all tested working ok. Job complete
MSA-DCS | WA3301354 | Unit 1, B & D Wing- Cell B5- Obs light have blown | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 May 2020 | 2020-05-18 17:00:00 | 2020-05-26 12:00:00 | Fail | attended unit, found prisoner had the flu. Returned once prisoner was cleared. Repaired faulty lights in B5
MSA-DCS | WA3301360 | Gym, Office- Vinyl floor lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 May 2020 | 2020-05-18 17:00:00 | 2020-07-02 14:15:00 | Fail | damaged vinyl removed/ replaced
MSA-DCS | WA3301509 | reception shade sail damaged outside sallyport | Hakea Prison | GMP-BR- HO | Building | Awnings (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-07-01 12:03:00 | Fail | braf email and approved to replace and make shade sails.PRISON THEN CANCELLED THE JOB.INVOICE IS FOR THE MATERIALS AND THE MANUFACTURE OF THE SHADE SAIL.
MSA-DCS | WA3301553 | Visits Centre- 3x globes are blown | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-18 15:00:00 | Pass | Repaired lights visits
MSA-DCS | WA3301558 | Unit 1, Cell B6- GPO in cell is damaged | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-14 10:00:00 | Pass | Replaced gpo
MSA-DCS | WA3301567 | reception DO desk Duct cover missing and damaged | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-06-05 11:30:00 | Fail | Repaired duct gpos
MSA-DCS | WA3301639 | main kitchen Ice machine not working | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Main Kitchen | GMP-BR- HO | Refrigeration | Ice machine (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-27 14:58:00 | Fail | Replaced the filter cartridge and solenoid valve.
MSA-DCS | WA3301659 | Unit 2, D13 - Bed light broken/wires exposed | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-14 12:30:00 | Pass | Repaired damaged cell light in unit 2 d13
MSA-DCS | WA3301729 | Electrical cabinet 3 - Sterile Zone has ant infestation | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 May 2020 | 2020-05-15 09:49:14 | 2020-05-14 13:30:00 | Pass | Collected parts and travelled to site. Replaced EC3 power supply with new powerbox power supply due to any infestation. All replaced and programmed ok. Programmed mains fail alarm to control room workstation utilising spare input on controller. All tested and working ok. Job complete
MSA-DCS | WA3301753 | MPU (8), M15 - toilet blocked and wont flush away | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-14 15:30:00 | Pass | Plunge toilet to clear blockage. Pull apart cistern and clean blocked Inlet valve. Reassemble and test.
MSA-DCS | WA3301802 | Unit 2, Cell C13- Key has broken off in prisoners lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 14 May 2020 | 2020-05-14 14:17:39 | 2020-05-14 12:15:00 | Pass | removed broken key and test lock function.
MSA-DCS | WA3301904 | Control room, Duress alarms - montior system has dropped out,saying out of range | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 May 2020 | 2020-05-14 19:06:49 | 2020-05-28 21:22:00 | Fail | Replaced monitor with Dahua 27inch.Connected speakers through inbuilt speakers.Monitor to be ordered and sent to WKRP to replace
MSA-DCS | WA3301911 | CCU, Cell 5- Toilet pan is leaking at the base | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 May 2020 | 2020-05-15 11:11:09 | 2020-06-08 11:00:00 | Fail | Attended site,Locate pan leaking internally and requiring replacement as will be broken during removal. Return to site,Removed failed pan with jack hammer,Supply and install new Lea pan by cementing. Tested works on completion
MSA-DCS | WA3301985 | Bakery W/S DOOR TO BE REPLACED TO THE DRY STORES AREA-see notes | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-09-14 13:00:00 | Fail | INSTALLED NEW STAINLESS STEEL DOOR
MSA-DCS | WA3302004 | Unit 13, A16 - basin taps leaking/ low shower pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-15 13:00:00 | Pass | Replace 1/4 turn spindle on basin. Check shower pressure, all ok.
MSA-DCS | WA3302022 | Unit 3, A13 - toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-15 12:00:00 | Pass | Turn water supply back on to the toilet cistern in plumbing duct and test.
MSA-DCS | WA3302066 | Unit 3 control room Toilet leaking at base | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 13:31:00 | Pass | Cut and modify waste pipe to replace pan collar
MSA-DCS | WA3302078 | Unit 3 B11 Toilet cracked and leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 14 May 2020 | 2020-05-15 12:18:39 | 2020-05-14 16:10:00 | Pass | Removed old broken toilet replaced with new
MSA-DCS | WA3302119 | Alarm system has stopped sending communications to security monitoring(The alarms are still working) | Riverbank-Riverbank Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 10:30:00 | Pass | Attended site and replaced 2 x 12vdc 7ah batteries. Restored power and tested alarm. All tested ok. Job complete Informed N.Dwyer and returned site keys.
MSA-DCS | WA3302166 | Unit 1, A8 - Veiwing window smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 14 May 2020 | 2020-05-15 12:59:09 | 2020-05-15 09:45:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3302175 | Unit 1 A2 veiwing window smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 14 May 2020 | 2020-05-15 13:00:18 | 2020-05-15 11:45:00 | Pass | OBS PANEL REGLAZED
MSA-DCS | WA3302231 | Unit 2, lower inside landing low water pressure | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 13:00:00 | Pass | COMPLETED
MSA-DCS | WA3302236 | Unit 1, hut toilet block floor drain blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 13:30:00 | Pass | COMPLETED
MSA-DCS | WA3302240 | Shared facilty - Leaking PVC water pipe | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 11:30:00 | Pass | COMPLETED
MSA-DCS | WA3302247 | Unit 13, Cell C9 - Cell light is faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-14 13:30:00 | Pass | Repaired faulty lights in unit 13 c9
MSA-DCS | WA3302252 | Unit 14, A & C Lobby- lights are faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 15:00:00 | Pass | Repaired multiple faulty lights in lobbies and outdoor patio.
MSA-DCS | WA3302384 | Duress system inaccuracy and no monitoring signal | Rockingham | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-06-11 12:05:00 | Fail | Completed as required.
MSA-DCS | WA3302401 | Duress mapping and zone list inaccurate | Rockingham Justice Complex | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-06-17 16:00:00 | Fail | Install 8 configure new permaconn unit. Reconfigured inputs to report contact ID codes and updated zone listing to monitoring company 02533 Account Number. Updated maps for PACOM. Created commissioning sheet for acc on Pacom & Gallagher. Completed zone locations on map to provide to SecureX.
MSA-DCS | WA3302430 | Unit 9 D11 Stop tap dripping running into cell and corridor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 14 May 2020 | 2020-05-15 15:28:53 | 2020-05-15 08:30:00 | Pass | Turned off water replaced tap washer/valve/oring
MSA-DCS | WA3302446 | medical centre, Sluice room - hot water tap continously on | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-15 14:45:00 | Pass | Turned off water reseated and washerd taps
MSA-DCS | WA3302450 | Unit 7, G wing shower - shower continuously running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-26 16:35:00 | Fail | Rewasherd taps new valves oring and seated set
MSA-DCS | WA3302499 | Unit 1, A2 - GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 13:00:00 | Pass | Replaced gpo
MSA-DFES | WA3302156 | Level 1 , Female toilet - Light has blown | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 14 May 2020 | 2020-05-15 17:00:00 | 2020-05-14 15:30:00 | Pass | Complete
MSA-DTAG | WA3302352 | 1987, Staff Car Park- Bike rack in underground car park, dyna bolts are loose | Supreme Court | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-14 17:00:00 | Pass | BIKE RACK RE FIXED
MSA-DTAG | WA3302434 | Ground floor, Family Voilence and Custody center - light fittings in these spaces are coming loose | Joondalup Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 14 May 2020 | 2020-05-15 17:00:00 | 2020-05-15 10:00:00 | Pass | Resecured light fittings in custody and family violence and replaced blown lamps
MSA-DTAG | WA3302486 | Duress alarms not correctly displaying on custody control PACOM | Rockingham Justice Complex | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-15 12:30:00 | Pass | Put system on test. Tested duress but PC audio not alarming and no notification. Refined the speakers and tested audio, all is ok now. Computer not communicating to Server correctly for alarms. Rebooted PC and tested operation. alarms and audio now working.
MSA-DTAG | WA3302488 | 2 x foyer cameras 1 x secured entry gate camera not working | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 12:14:00 | Pass | Reset 2 cameras, back online. 3rd camera had lens issue. Rectified with parts.
MSA-DTAG | WA3302493 | 7x faulty lighting Across Court registry and custody areas- see noes for locations | Joondalup Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 14 May 2020 | 2020-05-15 17:00:00 | 2020-05-15 09:30:00 | Pass | Replaced all faulty lamp throughout court
MSA-DTAG | WA3302496 | Ground level, court 2, Magistrtes entry door to court, not closing properly | Joondalup Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-21 09:30:00 | Fail | ADJUST DOOR CLOSER & SEALS
MSA-DTAG | WA3302502 | Gravel area – south west corner (near sallyport) - There is exposed mesh embedded in the ground | Supreme Court | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 14 May 2020 | 2020-05-15 17:00:00 | 2020-08-27 14:00:00 | Fail | WIRE MESH REMOVED- GRAVEL REPLACED
MSA-DTWD | WA3301485 | Water cooler at rear of Electro technology. Water is brown when tap is opened initially | Clarkson Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 2 | CLOSE | 14 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 11:30:00 | Pass | INVESTIGATED BROWN WATER COMING FROM BUBBLER - STICK HAS BEEN PUSHED INTO THE MOUTH PIECE OF ONE OF THE BUBBLERS - REMOVED, CLEANED FLUSHED UNIT TESTED. A404213025 WORKSHOP LOCKER AREA 1
MSA-DTWD | WA3301592 | V Block, Western auto entrance door Auto door not locking; | Rockingham Campus | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-14 15:45:00 | Pass | =Inspected door operation, =Found yellow COM wire broken away from terminal block, replaced and tested, okay, =Replaced 2 x batteries,
MSA-DTWD | WA3301656 | auto W/S G block air con leaking onto walkwy causing trip hazard | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 10:00:00 | Pass | Attended the site and signed in. Found the ceiling cassette in the auto class room leaking water onto the walkway from the condensor. This happens on heating only , removed the leaking plugs and sealed. Test ran all ok.
MSA-DTWD | WA3301671 | A block plant room Boiler tripping out every day, high temp fault | East Perth Campus | GMP-BR | Mechanical Services | Boilers (MS) | Precise Air Group | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-08-17 11:00:00 | Fail | Picked up required materials.isolated sysem and removed faulty dp switch,installed new dp switch and pipe work. Tested for leaks and left dp switch ready for bms tech to wire up.
MSA-DTWD | WA3301710 | B Block, G Floor, Corridor- Lights not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-06-03 13:00:00 | Fail | Found faulty corridor light. Isolated power and replaced with new led downlight. Tested all ok. Job complete.
MSA-DTWD | WA3301820 | Block 6 ground Brick paved area rear of Carpentry and Joinery Brick paving collapsed | Thornlie Campus | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-06-14 12:52:00 | Fail | Supply and install temp fence panels from 14/5/20 - 14/6/20
MSA-DTWD | WA3301834 | T block heating boilers are in a fault stage and need to be checked | Murdoch Campus | GMP-BR | Mechanical Services | Boilers (MS) | Equans Mechanical Services Australia | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-20 09:30:00 | Fail | Samples taken and inspection of boilers carried out
MSA-DTWD | WA3301868 | L Block around to P block, N/W External ring road- Floodlights not working | Midland Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-06-16 13:30:00 | Fail | Job complete need new lights
MSA-DTWD | WA3301874 | External, car park on South side of H Block- Flood lights (car park pole types) not working | Midland Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-06-16 11:15:00 | Fail | Job complete, need new lights
MSA-DTWD | WA3301883 | E block,North East roof- A/C water valve is faulty | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 16:00:00 | Pass | Replaced faulty 20mm RPZD and pipework to suit
MSA-DTWD | WA3302347 | D block D5-Right side auto wall tap keeps coming on-see notes | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-29 10:00:00 | Fail | Job complete on 29-5 but promap was down couldn’t upload
MSA-DTWD | WA3302407 | G block Administration, room G17 - Staff rom under sink HWS faulty | Rockingham Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-18 16:30:00 | Pass | Replace Steibel Replace valve and non return valve Install pressure limiting device
MSA-DTWD | WA3302412 | E block, Bistro Male toilet - cold tap not working on handwash basin | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-21 11:00:00 | Fail | Serviced hot and cold taps on both hand wash basins in the male toilets.
MSA-DTWD | WA3302471 | G block Entry, card door not reader | Leederville Campus | GMP-BR | Security | Security Management System (SE) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 14 May 2020 | 2020-05-15 17:00:00 | 2020-05-15 15:00:00 | Pass | Complete
MSA-DTWD | WA3302476 | A block, level 2, card reader not working | East Perth Campus | GMP-BR | Security | Security Management System (SE) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 14 May 2020 | 2020-05-15 17:00:00 | 2020-05-18 12:00:00 | Fail | Complete
MSA-DTWD | WA3302506 | B Block/Wing, Room B104- Access Control System issues - see notes below | Leederville Campus | GMP-BR | Security | Security Management System (SE) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-25 13:30:00 | Fail | Complete
MSA-DTWD | WA3302510 | B block, BG25 Mezzanine Level - Electric HWU Leaking | Carlisle Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 14 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 17:24:00 | Fail | Replaced leaking safe tray, installed separate tundish for relief lines. Installed new thermostatic mixing valve, insulated pipework and set temperature to 42°
MSA-MRWA | WA3301920 | Level 1, Kitchen - please replace fluro light/starter | Traffic Operations Centre | GMP-BR | Electrical | Lighting, Internal (EL) | MR - Handyperson - PFM | 1 | COMP | 14 May 2020 | 2020-05-15 17:00:00 | 2020-05-15 10:55:00 | Pass | *PROMAP WOULD NOT UPDATE ON MY PHONE UNABLE TO LOG JOB INSIDE TIMEFRAME**
MSA-MRWA | WA3302438 | Metrology Lab lighting to emergency exit stairwell not working please remediate-see notes | Materials Engineering Branch | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 14 May 2020 | 2020-05-21 17:00:00 | 2020-05-26 16:30:00 | Fail | Installed new led emergency light
MSA-DCA | WA3306740 | external doors 23 and 24 on upper balcony faulty door closer | State Theatre Centre (Heath Ledger Theatre)-Main Building-External Area-Courtyard - Entry and External Corridor | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 15 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 15:20:00 | Pass | Inspected door and found that the transom closer has failed and requires replacing. Please quote for 1x hold open RTS85 en4 and side load arm. 2x men required also. Braf being raised
MSA-DCA | WA3306756 | G Floor, Workshop- High chloride levels in RO unit | Shipwreck Galleries-Administration Building -Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-22 16:30:00 | Pass | Please refer to work logs. Job to be closed quotation submitted to PFM DCA for approval of applicable works as highlighted via Auswater.
MSA-DCA | WA3311110 | Lift Number 5 is out of service.-See notes | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 15 May 2020 | 2020-05-18 17:00:00 | 2020-05-18 13:00:00 | Pass | Not chargeable
MSA-DCA | WA3311599 | Water dripping from pipes, possible tap issue | King Street Arts Centre-Main Building-Level 1-Female Toilets - Back of Stair Foyer | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 14:45:00 | Pass | Replaced badly corroded basin set.Struggled to unscrew old basin set due to corrosion.Inspected room downstairs for future water connection
MSA-DCS | WA3306643 | Rational oven is not working SITE COSTED | Karnet Prison Farm | WSM-BR-SITE | Building | Materials (BU) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 15 May 2020 | 2020-05-19 17:00:00 | 2020-05-15 17:20:00 | Pass | 15/05/20 - Called as requested to the oven showing error 34.4 Checked the oven operation and the bus cable all good. Checked the top ignition unit again all ok. If fault occurs again then a new ignition unit will be required or main control board.
MSA-DCS | WA3306698 | Eradicate rabbit infestation | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 15 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 12:40:00 | Pass | Carried out fumigation for rabbits to all active warrens around the demountable, stores and car park. Added quick phos tablets to each active warren and back filled soil to seal the entry. High levels of rabbit activity/droppings throughout the site, should be vigilant for any obvious warrens that would need fumigating over the course of time.
MSA-DCS | WA3306711 | External Grounds, Front Gate & Visits Building- Remove rabbit Infestation | Melaleuca Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 15 May 2020 | 2020-05-21 17:00:00 | 2020-05-21 10:00:00 | Pass | 1st visit to lay bait. see photos. Warning signs displayed. Returning on 26/5/20 to rebait after rainfall & collect carcasses.returned 3/6/20, rebiat collect carcas
MSA-DCS | WA3306720 | Unit 5, B Wing, Cell B4- Medication hatch is not closing properly | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 15 May 2020 | 2020-05-21 17:00:00 | 2020-05-21 11:00:00 | Pass | Adjusted hatch & replaced hatch barrel
MSA-DCS | WA3306723 | Unit 5, B Wing, Cell B11- Window not opening or closing correctly, spring mechanism broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 May 2020 | 2020-05-21 17:00:00 | 2020-05-25 11:30:00 | Fail | new balances & feet fitted
MSA-DCS | WA3306730 | Unit 6, B & D, Cell D09- toilet constantly leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 May 2020 | 2020-05-21 17:00:00 | 2020-05-15 08:00:00 | Pass | Remove and replace faulty Inlet valve in cistern.
MSA-DCS | WA3306735 | Unit 5, Cell D8- Drain in cell not draining correctly, foul smell & filling up with water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 May 2020 | 2020-05-21 17:00:00 | 2020-05-15 09:00:00 | Pass | Moflo drain, rinse drain and plunge to unblock drain.
MSA-DCS | WA3306842 | orchid pump cutting out no flow | Wooroloo Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-15 13:00:00 | Pass | Orchid pump cutting out no flow. Check pump & controls. Test pipework on Chlorine injector. Purge gas from pump housing. Prime & run pump. Check flow & amps. All water line correct.
MSA-DCS | WA3306846 | education kitchen power cutting out | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 13:00:00 | Pass | Reset power to kitchen and educated staff
MSA-DCS | WA3306890 | unit 1 Control room external handle of control room appears to be loosening. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-27 12:00:00 | Fail | RE-SECURED CONTROL ROOM DOOR HANDLE
MSA-DCS | WA3306893 | Gate House - Front Entrance east sallyport door faulty closing at different times | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 15 May 2020 | 2020-05-16 10:07:09 | 2020-05-16 10:05:00 | Pass | Saturday 16/05/20Attend site. Inspect doors.No fault found.No additional information available.
MSA-DCS | WA3307060 | Bakery - Prover requires attention due to no Humidity. | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 15 May 2020 | 2020-05-16 10:37:04 | 2020-06-04 15:46:00 | Fail | 15/05/20 - Arrived at site, liaise with kitchen crew, identify faulty prover, isolate, remove panels, fault find, diagnose, found 2 wet elements to be faulty and 1 solid state relay to be faulty and require replacement.18/05/20 - Returned to site, liaised with front desk, walk to kitchen, identified prover, isolated, removed panels, diagnosed, removed faulty parts, install 2 new wet elements and 1 solid state relay, reassemble all components and test all components for correct function okay.04/06/20 - Delivered parts to site
MSA-DCS | WA3307075 | Unit 2, Cell C1- Shower leaking water through tiles at bottom of the wall | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-25 10:30:00 | Fail | Attended site and carried out inspection. Re-attended site and re-grouted shower recess.
MSA-DCS | WA3307113 | Unit 2, D15 - Sink spout broken, sprays water on the floor. | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-20 13:18:00 | Pass | Removed broken air raider and replaced with new
MSA-DCS | WA3307217 | unit 2 D15 Shower Tiles Broken and Coming off the Floor | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 15 May 2020 | 2020-05-16 11:04:23 | 2020-10-28 11:57:00 | Fail | REPLACED FLOOR TILES AND RE GROUTED - RE MOVED MOLDY SILICON
MSA-DCS | WA3307355 | Unit 1 - A & C A/c Dayroom lights not working as required | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-18 08:30:00 | Pass | Repairs to day room lights in unit 1
MSA-DCS | WA3307383 | unit 1 B8 GPO broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-15 15:00:00 | Pass | Replaced broken gpo
MSA-DCS | WA3307387 | CCU (11), Cell D3- Water leaking from sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-15 14:30:00 | Pass | Remove and replace 2 x quarter turn spindles in plumbing duct. (Was held up by staff for half an hour)
MSA-DCS | WA3307400 | Unit 13, A Wing, Cell A02- shower drain is blockked, no pressure in hand basin | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-18 14:30:00 | Pass | Remove grate, remove hair, moflo, rinse, plunge, reinstall grate and test. Adjust pressure in plumbing duct to Basin.
MSA-DCS | WA3307418 | Unit 1, Cell B13- Shower floor tiles missing & broken | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2021-02-24 14:18:00 | Fail | INSPECTIONS ONLY - PRISON ADVISED TO CLOSE OFF JOB COST TO DATE
MSA-DCS | WA3307623 | all of prison cell call system has gone down | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 May 2020 | 2020-05-15 15:56:27 | 2020-05-15 14:30:00 | Pass | Attended site checked and found cell call not working in Control. Checked locally in Units found cell calls working ok. Located the problem to be the faulty handset in control. Replaced faulty handset with the spare part in equipment room and tested it ok. CI-OH X 1 - Seme Stock Used
MSA-DCS | WA3307710 | Unit 2 Cell C-3 & C-D Wing Kitchen Broken Lights x 4 Total | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-21 10:30:00 | Fail | Investigate and repair lights in Cell C3 C and D Kitchen
MSA-DCS | WA3308897 | Whole Building- Spiders and crockroaches throughout building | Midland | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-20 17:45:00 | Fail | internal treatment for spiders & American & german Cockroaches. Improving external doors to prevent entry of American cockroaches is recommended
MSA-DCS | WA3309000 | Unit 2, Cell A3- Basin leaking, pipe under basin split | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-22 09:48:00 | Fail | Replaced broken pillar tap
MSA-DCS | WA3309166 | Programs room 2 - light fitting not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 12:00:00 | Pass | Investigate and Repair external lights at Programs Room
MSA-DCS | WA3309276 | Gardens lettuce shed - Broken GPO's | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-22 10:00:00 | Pass | Replace broken GPOs
MSA-DCS | WA3309330 | Front Gate, S/O Desk- GPO not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-25 11:00:00 | Fail | Repaired GPO
MSA-DCS | WA3309335 | Spine walkway, Outside wall of reception- Hose tap has been pulled out of the wall | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-20 14:10:00 | Pass | Repaired broken tap in wall
MSA-DCS | WA3309601 | SOG base front entry doo not auto door not closing automaticly | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 15 May 2020 | 2020-05-16 13:17:13 | 2020-05-15 16:30:00 | Pass | job completed - attended site adjust door closer - SOG front door
MSA-DCS | WA3309615 | SOG base conference room 1 fluro light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-18 12:30:00 | Pass | Repaired light
MSA-DCS | WA3311120 | Gate House - Crypt-We have an issue with our Building Management System (BMS).-see notes | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 15 May 2020 | 2020-05-16 14:18:59 | 2020-06-17 12:13:00 | Fail | Issues with the bms has been rectified.
MSA-DCS | WA3313836 | Unit 1, Control- Fire alarm sensor is activating | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 May 2020 | 2020-05-16 14:50:35 | 2020-05-15 17:33:00 | Pass | Attended site to investigate unit 1 fire alarm.Replaced detector for new & reset Ok.
MSA-DCS | WA3317982 | Prisoner Education Co-ordinator 3 room - fly screen is unable to be secured as it has a faulty lock | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 11:30:00 | Pass | Replaced broken security screen door lock on Educators Co -ordinators office door Room 3
MSA-DCS | WA3317986 | Gate house - Monitor 17 no pictures available | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 May 2020 | 2020-05-16 16:58:47 | 2020-05-16 10:15:00 | Pass | Contacted John and attendance only required in the morning. Arrived on site and quad monitor not showing cameras. Rebooted PC and setup software. Quad screen now displaying cameras.
MSA-DFES | WA3306742 | Server Room - Water condenser issue on cooling unit | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 15 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 11:00:00 | Pass | Attend site. Access server room. Found crac units not in fault but red light on unit. This is to notify of an event that previously happed but did not effect operation. Clear notifications and check operation of unit, working ok.SERVICE
MSA-DFES | WA3307125 | All Levels, Walk around building- replace lights that are not working | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-09-10 08:45:00 | Fail | Arrived onsite and signed in. Removed faulty light fittings and replaced with new. Informed staff of work completed and signed out.
MSA-DFES | WA3315052 | North end bathroom – firefighters dorm-Shower is draining poorly and back flows into sink | Kensington (old) | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-21 09:04:00 | Fail | Clear blocked drains
MSA-DFES | WA3335187 | RETROSPECTIVE - Security Alarm Monitoring Service - BYPASS ONSITE FROM THE 2 ROLLER DOORS | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 15 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 11:55:00 | Pass | BYPASS ONSITE FROM THE 2 ROLLER DOORS - PLEASE CHECK WHO IS ONSITESECURX ONSITE TESTING THE ALARM. STAFF ONSITE AS WELL. TEST WAS BEING DONE. MONITORING ADVISED
MSA-DTAG | WA3306683 | Hallway that runs from Court 1 to 3, gound floor - lights are out | Joondalup Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 15 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 14:30:00 | Pass | Replaced faulty lights and tested working
MSA-DTAG | WA3306729 | The acoustic panel in Court 4 is separating from the rear wall | Joondalup Courthouse | GMP-BR-HO | Building | Internal Screens (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 May 2020 | 2020-05-21 17:00:00 | 2020-09-04 09:17:00 | Fail | ACOUSTIC PANEL REPAIRED
MSA-DTAG | WA3317638 | Outside eaves of pre-trial conference room - Eaves are collapsing | Mandurah Courthouse | GMP-BR-HO | Roofing | Tiled Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-21 10:45:00 | Fail | EAVES REPAIRED
MSA-DTWD | WA3306710 | S Block, Room S106- Pin lock to door is not working | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 15 May 2020 | 2020-05-21 17:00:00 | 2020-05-19 10:19:00 | Pass | replace faulty mechanical push button lock to room 106
MSA-DTWD | WA3306855 | A block AG01-A AC1 Aircon Unit showing Fan status fault. Not heating. | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-15 12:30:00 | Pass | Was Already on site attending another job , found air-conditioning system number one had tripped the evaporator fan over load. Checked the power supply all ok , all wiring is tight, contactor over load all ok. Reset and ran up , amp draws with in motors tolerance, motor not over heating, voltage all good through the contactor and over load. Temperature in class rooms heated up and the air-conditioning system cycled several times. No cause apparent must of been a problem with the mains supply.
MSA-DTWD | WA3306861 | Fire Cabinet, Located outside Fire pump shed (near Murdoch Uni- Graffiti to be removed | Mandurah Campus (formerly Peel) | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-22 10:00:00 | Pass | REMOVAL OF GRAFFITI FROM FIRE CABINET LOCATED OUTSIDE FIRE PUMP SHED
MSA-DTWD | WA3307032 | T Block, Lvl 3- Hot water unit, circulating pump is in fault. | Murdoch Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 15 May 2020 | 2020-05-20 17:00:00 | 2020-05-29 12:00:00 | Fail | Replaced pump and made sure working correctly
MSA-DTWD | WA3307330 | W Block, Lvl 3- Male & Female Toilets hot water not heating at all | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-28 14:44:00 | Fail | Fixed issues around hot water for the whole block
MSA-DTWD | WA3308287 | L5 plant room damaged drive belts to T/E fan | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-20 10:00:00 | Pass | PICK UP REPLACEMENT BELTS. ISOLATE TEF REPLACE BELTS ON TEF 14 A AND B, CLEANED, TESTED ALL OK.
MSA-DTWD | WA3308331 | Chiller compound, - cooling water release value broken, losing lots of water and unable to turn off | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 0 | CLOSE | 15 May 2020 | 2020-05-15 16:24:44 | 2020-05-15 15:00:00 | Pass | Accessed site and plant equiptment. Chiller pumps isolated and also chillers from operation.Found faulty safety relief valve to chilled water line.Isolated via controll valves water throttle and butterfly valve. Removed faulty valve from circuit and replaced with replacement valve. New like for like to arrange. Pumps returned to service and chillers also . Room temps reducing as desired. Waterflow check Valve holding.
MSA-DTWD | WA3309158 | L1 Aberdeen Main entrance Remove Grafitti | Perth Campus B1 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 15 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 10:50:00 | Pass | REMOVAL OF GRAFFITI FROM ENTRANCE L1
MSA-MRWA | WA3307215 | Level 1, Kitchen - Faulty light, tombstones are broken | Traffic Operations Centre | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 15 May 2020 | 2020-05-18 17:00:00 | 2020-05-15 15:30:00 | Pass | Complete Attended site and found faulty kitchen lights, found the light fittings to b damaged beyond repairs, replaced with new lights and tested all in working order, notified staff and signed out
MSA-MRWA | WA3312426 | Building Access – Sliding side door not operating correctly.-see notes | Heavy Vehicle Services | GMP-BR | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 15 May 2020 | 2020-05-15 18:36:46 | 2020-05-15 16:48:00 | Pass | Arrived on site and site contact was not contactable another site member showed me the door and could not fault operation at time of test
MSA-DCS | WA3318937 | Zone 14 fence line alarm is not activating | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 May 2020 | 2020-05-16 11:05:01 | 2020-05-16 11:00:00 | Pass | Checked cable for damage and replaced a few cable ties. Used Senstar programmer to check settings and sensitivity. Tested ok back to he gatehouse.
MSA-DCS | WA3318955 | locksmith interior back door wont close | Hakea Prison-Main Gatehouse | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 16 May 2020 | 2020-05-16 12:23:19 | 2020-05-16 10:15:00 | Pass | Job completed - Attended site after hours Saturday 16/05/2020. Removed strike and tested - no fault found. Reinstalled in workingorder. Appears to be power issue. Advised to have SEME attend to test switch in control room
MSA-DCS | WA3318971 | locksmith interior back door wont close | Hakea Prison-Main Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 May 2020 | 2020-05-16 13:56:20 | 2020-05-16 11:00:00 | Pass | Back door into prison (by gatehouse) not operating. Attended site and staff advised locksmith repaired lock and for us to check operation. Tested door operation and door unlocking & locking correctly. Status lights also working indicating status of door. No fault found.
MSA-DCS | WA3318985 | Cell call in cell D2 is not operating in the self care unit | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 May 2020 | 2020-05-16 14:47:16 | 2020-05-16 14:30:00 | Pass | Selfcare D2 intercom not working. Checked cell call pc and all nodes online. Waited for escort to selfcare. Tested cell call D2 and no calling. swapped D2 & D3 around on controller. Tested operation and intercom ok. Swapped ports back and tested operation, all is in working order now.
MSA-DCS | WA3318989 | SITE COST Urguhart unit EHWS no hot water coming | Banksia Hill Detention Centre | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 16 May 2020 | 2020-05-16 14:58:14 | 2020-05-16 13:27:00 | Pass | Adjusted water temperature to the whole wing.
MSA-DCS | WA3323677 | Zone 8 Temper Alarm Perimeter Deactivated on system. | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 May 2020 | 2020-05-18 01:35:04 | 2020-05-18 10:00:00 | Fail | Tested End of Line resistor on zone 8 and zone 3 fence controller. All tested ok. Reset controllers and retested. All had tested ok. Job complete
MSA-DCS | WA3333130 | 8 Camera on the perimeter fence line is not recording. | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 May 2020 | 2020-05-17 11:48:19 | 2020-05-20 07:48:00 | Fail | Job to be completed with costs to date.
MSA-DCS | WA3333137 | Dishwasher in the main kitchen is broken. | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 17 May 2020 | 2020-05-18 09:06:09 | 2020-05-17 12:20:00 | Pass | 16/05/20 - Called as requested on the weekend to the dishwasher not working correctly, burning smell and smoke coming from the electrics. Found the wiring to the wash element burnt off so made good, tested all ok. Note. Hot water pressure very poor therefore not rinsing correctly and taking a long time to fill. A pressure pump external of the machines is required.
MSA-DCS | WA3333145 | Banksia Hill Detention Centre -Omni tracks and inner fence in S 16 constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 May 2020 | 2020-05-17 14:15:53 | 2020-05-18 11:00:00 | Fail | install new splice kit & rectified loose cable zone 16. used 2 x splice kits & 100 cable ties (seme stock)
MSA-DCS | WA3333203 | Broome RS- in gatehouse cell call system coming out with network error. | Broome Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 May 2020 | 2020-05-20 17:00:00 | 2020-05-18 17:00:00 | Pass | Restored network fault on gatehouse officer station.
MSA-DCS | WA3333212 | surveillance monitor in control room not working | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 May 2020 | 2020-05-22 17:00:00 | 2020-05-18 12:00:00 | Pass | Monitor in control room i indicating no signal input, traced issue to crypt delivery signal. Tested now fully operational, confirmed with control officers correct image displayed. All ok
MSA-DFES | WA3333233 | Sewage blockage, bring auger/worm | CFRS Joondalup | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 0 | CLOSE | 17 May 2020 | 2020-05-17 23:27:34 | 2020-05-17 21:00:00 | Pass | Cleared Blockage using drain machine.
MSA-DCS | WA3333238 | Zone 4 fence alarm can't be reset or stopped/ going off continuously. | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 May 2020 | 2020-05-18 09:07:21 | 2020-05-18 09:00:00 | Pass | Travelled to site, investigated zone 8 and all had been working ok. Tested End of Line (EOL) resistor and all tested ok. Reset controller and all tested ok. Job complete
MSA-DCS | WA3333321 | Boiler House - Boilers at the industries are not firing up. | Hakea Prison-Kitchen and Laundry | GMP-BR- HO | Building | Materials (BU) | Boilertronics | 0 | CLOSE | 18 May 2020 | 2020-05-18 10:55:57 | 2020-05-18 10:00:00 | Pass | Travelled to site and signed in. Escort to boiler house and de isolated boilers and started up. Let boilers build uppressure and released steam to plant. Signed out and left site
MSA-DCS | WA3333362 | U2 a/b wing, water leak - Seems to be coming from Cell A17 down the walls into the Kitchen/dayroom | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 May 2020 | 2020-05-19 07:29:00 | 2020-06-08 13:30:00 | Fail | Attended site,Investigate water leaking into kitchen,Locate pan in unit 17 leaking water and causing water ingress into kitchen.Pan and seals will require replacement. Return to site,Removed failed pan with jack hammer,Supply and install new Lea pan by cementing. Tested works on completion
MSA-DCS | WA3333368 | SITE COST Unit 1 Bwing - Toilet is leaking water from the main pipe. | Bandyup Prison | WSM-BR-SITE | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 18 May 2020 | 2020-05-18 11:33:08 | 2020-05-18 13:01:00 | Fail | Attended site,Locate multiple issues causing water to leak in the duct and within unit B26, completed the following to rectify. Used drain machine to clear an unknown blockage to the sewer line from the duct inspection opening. Used feropre to repair the split sewer line and leaking pan adapter.Supplied and installed a new 40mm flush pipe rubber.Tested works on completion
MSA-DCS | WA3333393 | gatehouse - perimiter equiptment cabinet GPO faulty | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 May 2020 | 2020-05-22 17:00:00 | 2020-05-19 10:00:00 | Pass | Replaced damaged power supply
MSA-DCS | WA3333449 | Monitor room - PTZ camera 36 not responding to alarms or joy stick | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 May 2020 | 2020-05-19 08:07:10 | 2020-05-18 10:15:00 | Pass | Attended site checked and found PTZ camera 35&36 not responding to joystick and alarm. Located the problem to be Indigovision workstation 1 problem. Restart Indigovision Control Center in workstation and tested all ok.
MSA-DCS | WA3333454 | Unit 2, Cells D1,D2 & D3- power keeps switching off | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 10:00:00 | Pass | Replaced damaged GPOs and switches in cells
MSA-DCS | WA3333463 | Unit 3, Control Room carpet is piece needs re-sticking down | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-09-29 11:30:00 | Fail | DOUBLE UP - THIS WORK WAS COMPLETED ON WA3203808
MSA-DCS | WA3333476 | Prisoner Day Room- Urn is leaking on the underside on left hand corner | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-19 10:52:00 | Pass | Secured loose fittings all seems okay
MSA-DCS | WA3333481 | Unit 2, B1 - Blocked sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 15:04:00 | Pass | Unblocked basin and shower
MSA-DCS | WA3333485 | Unit 3, D Wing- Cleaning Cupboard water pipes really noisy | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-18 09:00:00 | Pass | Replace 1 times quarter turn spindle in cleaners store on showers.
MSA-DCS | WA3333489 | Day stay - key stuck in lock | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 18 May 2020 | 2020-05-18 12:33:09 | 2020-05-18 11:30:00 | Pass | Repaired Lock on sliding glass door fitted new lock tailpiece and packing plates
MSA-DCS | WA3333490 | SHU (9), Cell B2 sink taps not turning off, broken split spins | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 12:30:00 | Pass | Replace missing split pin in plumbing duct
MSA-DCS | WA3333493 | Unit 2, B7 - Blocked sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 15:37:00 | Pass | Unblocked shower and basin
MSA-DCS | WA3333497 | Unit 4, Cell A7- Window frame & sliders broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-29 16:00:00 | Fail | replace,reglaze window. repair framework. replace parts
MSA-DCS | WA3333498 | Unit 2, A8 - Blocked sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 May 2020 | 2020-05-19 08:37:54 | 2020-05-18 15:35:00 | Pass | Cleared blocked shower and basin in A8
MSA-DCS | WA3333506 | Unit 4, Cell C13- Lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 13:00:00 | Pass | Repaired faulty lights
MSA-DCS | WA3333517 | Kitchen, security cameras have lost signal | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-19 11:39:00 | Pass | Security cameras indicating lost signal in kitchen area, confirmed area is under warranty period and requires follow up by third party contractor via Broad construction.
MSA-DCS | WA3333522 | SOG Base- Power point is not working & needs to be removed | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 May 2020 | 2020-05-19 08:51:25 | 2020-05-18 12:00:00 | Pass | Removed gpo
MSA-DCS | WA3333527 | Unit 4, Cell 13- Window stays broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-22 14:15:00 | Fail | RENEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3333531 | Unit 13, Cell B11- Viewing hatch has come off & need refixing to door | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-03 13:00:00 | Fail | HATCH RE FIXED TO DOOR
MSA-DCS | WA3333535 | Unit 14, B & D Wing- Air lock door handle has come loose | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-28 09:15:00 | Fail | AIR LOCK DOOR HANDLE MISSING - JOB NEEDS TO BE RE-ISSUED TO A LOCKSMITH.
MSA-DCS | WA3333542 | Unit 13, C Wing, Cell C11- viewing hatch bottom part of the frame is missing | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-03 12:45:00 | Fail | HATCH REFIXED TO DOOR
MSA-DCS | WA3333543 | unit 1, tearoom - Staff room air-con leaking water | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-18 10:30:00 | Pass | Checked over aircond found condensate drain pump blocked,isolated and cleaned out,turned back on and tested all running ok at present.
MSA-DCS | WA3333547 | Unit 5, Cell B8- Toilet cistern continually running water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 11:00:00 | Pass | Remove and replace one faulty Inlet valve and test
MSA-DCS | WA3333550 | Unit 14, Cell C12 - toilet leaking at base. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-09 11:00:00 | Fail | Removed damaged pan. Installed new pan, tested and removed rubbish.
MSA-DCS | WA3333551 | Administration - A/C check Heating appaears to be U/S down the HR corridor | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-18 12:00:00 | Pass | Checked over aircond found tripped out,reset and tested all running ok at present, checked heater banks to make sure ok,
MSA-DCS | WA3333554 | Unit 4, Cell C8- Leaking sink tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 10:00:00 | Pass | Remove and replace 1 times quarter turn spindle on basin in Cell
MSA-DCS | WA3333562 | Unit 3, Cell A7- Sink in blocked resulting in an overflow from the drain under the sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-18 09:10:00 | Pass | Plunge both Basin and floor waste to clear blockage.
MSA-DCS | WA3333564 | SHU (9) - The Whole Unit Cell call system has network fault | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 14:00:00 | Pass | Cell call system indicating multiple errors, cleared all error s except for construction zone, checked individual cell intercom ok. No further action is required.
MSA-DCS | WA3333578 | Unit 1 B12 GPO faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 10:00:00 | Pass | Replaced gpo
MSA-DCS | WA3333585 | Admin Foyer Toilet, sink - Tap not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-19 13:00:00 | Pass | Located isolation valve turned off water replaced mini stop with new one and turned water back on cleaning filter
MSA-DCS | WA3333592 | Zone 13, Camera 2 is not working | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 May 2020 | 2020-05-18 13:19:43 | 2020-06-05 15:15:00 | Fail | Collected parts and travel to site, replaced zone 13 camera 2 fixed camera with new Indigo BX IP camera, all cabling install and programming complete. 30 metres of cat6 underground and 6 core underground cable used. Tested camera recording and all recording ok. Job complete. EWP used
MSA-DCS | WA3333594 | Unit 3, B Wing Shower window metal bit on the left side needs fixing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 13:00:00 | Pass | SPIRAL BALANCES RENEWED
MSA-DCS | WA3333609 | Unit 5, Cell B8- Cell window sliders are not working | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 12:15:00 | Pass | new balances & feet fitted
MSA-DCS | WA3333617 | Unit 5, Cell B5- Window stays damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 10:45:00 | Pass | RENEWED SPIRAL BALANCES & FEET
MSA-DCS | WA3333620 | Unit 2 C6 GPO faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 11:00:00 | Pass | Replaced gpo
MSA-DCS | WA3333631 | Gascoyne kitchen sink Hot tap continually leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-19 14:00:00 | Pass | turbed off water removed tap Reseated tap set turned water back on
MSA-DCS | WA3333634 | Boiler House - The Whole Unit-main compressor power not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-18 12:00:00 | Pass | Investigated faulty compressor in Boiler House, re-installed phases. Reset and test
MSA-DCS | WA3333646 | kitchen above sink urn is not producing hot water and nozzel is not working | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 18 May 2020 | 2020-05-19 09:50:37 | 2020-05-18 12:00:00 | Pass | diagnosed and replaced rheem tap assembly + adaptor tested checked on A40184108F
MSA-DCS | WA3333652 | Unit 14, Cell D12- Bedisde light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-21 09:00:00 | Pass | Repaired all lights in cell d12 unit 14
MSA-DCS | WA3333667 | SOP, Cell A9- toilet not filling up after flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-18 13:30:00 | Pass | Remove pipework, clean out corrosion build up, reinstall and test.
MSA-DCS | WA3333890 | Turner, A01 - toilet is split and leaking water on the floor | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-27 12:30:00 | Fail | Repaired leaking tpilet
MSA-DCS | WA3333913 | Kitchen, rational oven error with cleaning cycle | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 13:00:00 | Pass | LHS Rational Oven Cleaning cycle error. Check oven, check errors in history. Flush boiler, run clean jet mode, All working correctly. Report to staff.
MSA-DCS | WA3334663 | Unit 14, C wing C05 - water leaking through shower screen, on to mattress (screen not sealed) | Casuarina Prison | GMP-BR- HO | Glazing | Glass wall (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-28 11:15:00 | Fail | SHOWER SCREEN REPAIRED
MSA-DCS | WA3335048 | Boilerhouse - Boilers to be switched Off | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 18 May 2020 | 2020-05-19 11:35:40 | 2020-05-18 16:15:00 | Pass | Travelled to site and signed in.Isolated boilers at the main switch and also the feed water valves.Completed blowdowns on boilers and gauge glass mounts.Isolated inlet steam valve on header.
MSA-DCS | WA3335175 | Unit 7, S Wing Showers- Showers leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 12:52:00 | Pass | Couldn’t turn off isolation valves for hot as it needs new valve or isolate valve for cold as could not find the one to turn off that wing the others I found were seized so need to be changed also
MSA-DCS | WA3335179 | Unit 7, Cell E21- Tap continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 13:55:00 | Pass | Replaced broken Pilar tap
MSA-DCS | WA3335308 | Unit 1, B12 - toilet constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-19 09:30:00 | Pass | Remove Inlet valve, clean out calcium deposits, reinstall and test.
MSA-DCS | WA3335313 | Vegetable Preparation - emergency light globe in office needs replaceing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-19 08:30:00 | Pass | Repaired faulty lights in Vege prep
MSA-DCS | WA3335315 | unit 4, D2 - toilet flush button not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-20 09:30:00 | Pass | Remove push button, clean out paint build up, reinstall and test.
MSA-DCS | WA3335319 | unit 4, B & D wing - showers require attention | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-19 13:30:00 | Pass | Inspect the showers no plumbing issues were found. Tiles are missing from around the floor waste. Report back to maintenance.
MSA-DCS | WA3335325 | Unit 4, A & C wing - sky light is cracked and require replacing/repairs | Casuarina Prison | GMP-GR | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-12-17 14:00:00 | Fail | 4X SKYLIGHTS REPLACED
MSA-DCS | WA3335352 | Vegtable Prep- potato rumbler that you installed | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-19 08:30:00 | Pass | Repaired potato rumbler in Vege prep
MSA-DCS | WA3335354 | Unit 1, Lunch Room- light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-23 10:30:00 | Fail | Checked damaged lights in unit 1. Sourced suitable lights. Picked up replacements and installed and tested
MSA-DCS | WA3335360 | Unit 14, D14 -Main cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-21 10:30:00 | Pass | Repaired faulty lights in unit 14 d14
MSA-DCS | WA3335372 | Compound boom gate faulty sensor issue | Pardelup Prison Farm | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-27 16:30:00 | Fail | Replaced control board
MSA-DCS | WA3335376 | Investigate SMS backup power hold time | East Perth | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-24 16:35:00 | Pass | Replaced old batteries and powered up and down server
MSA-DCS | WA3335380 | Key control camera mounting unsecure and vision impacted by fluorescent lighting | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-06-22 14:49:00 | Fail | Sourced parts, attended site, installed and cabled new camera, configured camera and servers, confirmed correct operation and recording.Tested OK.Job Complete
MSA-DCS | WA3335385 | Unit 4, Cell H31 & H32- No hot water | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-21 13:50:00 | Pass | COMPLETED
MSA-DCS | WA3335393 | Cris Care, H7 - Lower LHS window loose due to window seal damage | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 18 May 2020 | 2020-05-19 13:57:05 | 2020-05-19 11:45:00 | Pass | RESET GLASS- FRAME SECURED
MSA-DCS | WA3335399 | Unit 1, D-5 - Blocked sink & shower | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 May 2020 | 2020-05-19 14:04:36 | 2020-05-19 08:50:00 | Pass | Unblcoked drain in d5
MSA-DCS | WA3335406 | Unit 1, C3 - Sink spout Broken, water squirting onto the floor | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 16:18:00 | Pass | Removed and replaced air raider
MSA-DCS | WA3335417 | Unit 1, D-5 - Broke shower floor tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2021-02-24 14:21:00 | Fail | INSPECTIONS ONLY - PRISON ADVISED TO CLOSE OFF JOB COST TO DATE
MSA-DCS | WA3335433 | Uni 3, front entrance, garden tap copper feed pipe burst | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-19 08:30:00 | Pass | Isolate water, remove and repair tap, de-isolate and test.
MSA-DCS | WA3335514 | Unit 1, Cell A14- Blocked toilet | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 May 2020 | 2020-05-19 15:38:05 | 2020-05-19 15:41:00 | Fail | Attended site,Used drain machine to remove a large amount of tree roots from the sewer line. Tree roots entering at 2-3m away from stack I.O.Tested works on completion
MSA-DCS | WA3335544 | U10 A wing grille locking mechanism becoming more difficult to open | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-06-10 13:15:00 | Fail | replaced lock.
MSA-DCS | WA3335545 | CCTV monitors 2 have gone blank | Midland (North East Metro) | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 May 2020 | 2020-05-19 16:30:46 | 2020-05-19 10:00:00 | Pass | Rectified and repaired psu hdmi extender, job completed.
MSA-DCS | WA3335552 | unit 10 A3 Cell call speaker is faint | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-20 15:04:00 | Pass | Rectified and fixed distorted audio, tested working. Job completed.
MSA-DCS | WA3335569 | Gym,Recreation and Educational Centres are offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 20:11:00 | Pass | ups battery levels are over 30mins on load after minutes without power.Upgraded firmware on network card
MSA-DCS | WA3335570 | Control Room - PDS and DCP is not working - going offline. | West Kimberley Regional Prison-External Area | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 May 2020 | 2020-05-19 07:10:28 | 2020-05-18 23:44:00 | Pass | Site contacted technican, advised all systems are offline.Technicians attended site and restored MDAS using back-up file.Gallagher system showing ok but will not load.Checked through system logs.Found timesync on the server is out by an hour.Reprogrammed NTP time sync and logged back into Gallagher from control.Performed systems check and perimeter check.Back online
MSA-DCS | WA3338047 | Retrospective - Control Gate, no control to open prison doors. computer is down | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 May 2020 | 2020-05-19 02:00:00 | 2020-05-18 19:30:00 | Pass | Contacted site and found Gallagher door control PC turned off possibly due to power outage. Re powered Gallagher PC and reloaded door controls. All powered on and tested ok . Job complete
MSA-DFES | WA3333574 | Bathroom - Pressure test on the shower as possible leak in wall | CFRS Ellen Brook | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 11:20:00 | Pass | Conducted several pressure tests and detected leak. Advised PFM further investigation required.
MSA-DFES | WA3333736 | Ground Floor, South Wall of Building/Secure Carpark - Graffiti on outside of wall south of building. | DFES Cockburn Emergency Services Complex | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 09:30:00 | Pass | REMOVAL OF GRAFFITI FROM OUTSIDE BUILDING WALL NEAR UNDERCROFT
MSA-DFES | WA3335332 | Repair cracks and pot holes in rear drill yard of station | CFRS Maddington | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-07-13 08:45:00 | Fail | BRAF has been submitted and we are now waiting for approval to proceed
MSA-DFES | WA3335345 | Kitchen - Zip boil, BilliQudra is not working - intermittent flashing faults | CFRS Daglish | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 18 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 09:00:00 | Pass | Replaced PCB board . All working fine. Billi Quadra Unit A400510144
MSA-DFES | WA3335396 | Hose Room Door- Door handle has fallen completey off | CFRS Vincent | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 12:30:00 | Pass | Supply and install new handle screws. Resecure door handle. While on site found that a few swipe card readers were not working (electronic strikes) - advised site and Steve Cassie of this.
MSA-DFES | WA3335427 | White ants in floorboards | Armadale Regional Office | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 18 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 13:55:00 | Pass | Installed AG to active workings in floor boards.Follow up required in 2 weeks to assess and rebait.
MSA-DFES | WA3335446 | rear access wooden door paint is peeling off and requires repainting to make good | DFES Regional Office - Joondalup | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-27 13:30:00 | Fail | Painting of door
MSA-DFES | WA3335508 | Dorm 4 - Air con unit displaying fault / check code 5 and unable to function. | CFRS Kiara | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-26 11:30:00 | Fail | Replaced pcb. Unit runs great
MSA-DFES | WA3335510 | L1 Various areas have blown light bulbs-please see notes | CFRS Kiara | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-30 10:15:00 | Fail | Locate faulty light in the kitchen. Replaced faulty downlight and driver with new.
MSA-DFES | WA3335512 | External Air con unit on south wall, main isolation switch broken off. | CFRS Kiara | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 14:00:00 | Pass | See work notes replaced isolator
MSA-DFES | WA3335513 | Rear Courtyard - Rubbish Bin Alcove P trap that links the washing machine outlet to drain is broken | CFRS Kiara | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 08:30:00 | Pass | Repairing the washing machine outlet pipe.
MSA-DTAG | WA3333513 | Level 2, Sheriff’s Office - The light in the small storeroom in the basement is not working. | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 18 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 09:30:00 | Pass | Inspected fault to fittings in store room and found damaged cable - re-ran new cable and Resecured lighting
MSA-DTAG | WA3333598 | Basement, Custody - Security don’t have any of their systems functioning. No CCTV, no duress alarms | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 18 May 2020 | 2020-05-18 13:22:58 | 2020-05-22 17:00:00 | Fail | Job completed - Work Station, created new log in for Indigo & Gallagher assecurity advised they could not remember their passwords. Confirmed all back to normal
MSA-DTAG | WA3333610 | Level 5, Sherriffs office - There is a light flickering in the back of the office. | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-19 11:00:00 | Pass | Job complete
MSA-DTAG | WA3335250 | level 1, pump room - Sprinkler pump circuit to be re-connected | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 18 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 08:15:00 | Pass | Job complete
MSA-DTAG | WA3335254 | L5 public seated area Wallpaper is peeling away from waiting area wall - opposite Court 56 | Central Law Courts | GMP-BR-HO | Building | Internal Walls (BU) | PPM Project Painting & Maintenance | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-21 13:00:00 | Pass | Repair and paint damaged wall
MSA-DTAG | WA3335395 | Lvl 1, Public Faux marble wall paint is peeling, cornice is also showing signs of deterioration | Supreme Court | GMP-BR-HO | Painting | Internal (PA) | COLGAN INDUSTRIES PTY LTD | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-06-03 12:00:00 | Fail | Repaint Upper Corridor on Level 1 at Supreme Court
MSA-DTWD | WA3333383 | Level 1, N129 - Reinstall boards in Facilities Office | Perth Campus B1 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 18 May 2020 | 2020-05-22 17:00:00 | 2020-05-18 15:30:00 | Pass | Arrived on site meet with contact shown job and proceeded. Complete hanging whiteboards cleaned up and left site.
MSA-DTWD | WA3333470 | Lvl 1, Room A146- water leaking from hand basin & trough waste | Leederville Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 14:30:00 | Pass | Complete
MSA-DTWD | WA3333472 | E block, ground floor, E606 - Damaged GPO with exposed wiring | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 18 May 2020 | 2020-05-19 17:00:00 | 2020-05-18 12:00:00 | Pass | Resecured gpo to duct in E606. Job complete
MSA-DTWD | WA3333681 | D block,Celeste kitchen- Prep area/East damaged mixer tap and under sink pipe repairs reqd | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-25 09:49:00 | Fail | COMPLETED
MSA-DTWD | WA3333707 | B block, ground floor, corridor - Circuit RED 1 faulty. Board located in corridor | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 18 May 2020 | 2020-05-19 17:00:00 | 2020-05-18 16:00:00 | Pass | Fault finding rcbo tripping on R1.Fault determined to be damaged rcbo.Replaced with new rcbo and ensure circuit in working operation.
MSA-DTWD | WA3333751 | Basketball court - Alarm system showing battery fault | Rockingham Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-21 09:23:00 | Pass | 18/05/2020, 1350-1430Replaced backup battery for Basketball court Ness alarm. Tested alarm as well, it is a local alarm.
MSA-DTWD | WA3333757 | Basketball court - Shed roller door lock faulty | Rockingham Campus | GMP-BR | Building | Doors (BU) | UNIVERSAL DOORS | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-06-26 12:15:00 | Fail | Job completed - ATTENDED SITE, SUPPLY & INSTALLED ONE (1) NEW CENTRE LOCK WITH KEYS, CHECKED OPERATION, ALL OK
MSA-DTWD | WA3335010 | E block EG15-Auto Sliding Door not closing. -see notes | Carlisle Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-18 14:16:00 | Pass | Found internal sensor self actuating causing door to stay open, checked sensor and cable, adjusted angle and sensitivity and reset sensor, tested all ok
MSA-DTWD | WA3335259 | T Block, room T026 - not heating up from the air conditioning | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 18 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 12:00:00 | Pass | Cleared blockage in fcu
MSA-DTWD | WA3335358 | P Block, Roof (single storey, S/E corner- Rusted gutter | Midland Campus | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-06-24 14:45:00 | Fail | Inspected rusted gutter on P block, will have to quote a BRAF and return with materials.Removed 5m length of squareline gutter and replaced with new. Installed new gutter clips. Removed metal downpipe and replaced with PVC, removed waste .
MSA-DTWD | WA3335361 | Wooded Boat Works- Large wooden sliding door hard to open | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-06-15 11:30:00 | Fail | Supply & Install flat bar to wooden boat works roller door track to repair guides. Job complete
MSA-DTWD | WA3335497 | Lvl 1 & 2, No heating to all vav's | Perth Campus B4 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 18 May 2020 | 2020-05-25 17:00:00 | 2020-05-21 12:00:00 | Pass | ATTENDED SITE WITH CHRIS SPADAK. GAINED ACCESS TO BUILDING4 AND LOCATED VAV BOXES. CARRIED OUT TESTING ON DUCT HEATER BANKS. CONTROL CONTACTS FOUND TO BE FAULTY. BRAF BEING CREATED BY CHRIS S FOR WORKS. 2 TECHS REQUIRED DUE TO EQUIPMENT LOCATION AND CELLING HEIGHT. WORK AREA LEFT TIDY. ASSISTED CHRIS VAN REPLACING THE HEATER RELAYS
MSA-MRWA | WA3335227 | Basement Foyer EWIS Battery charging fault, please investigate | Don Aitken Centre MRWA Head Office | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 18 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 09:00:00 | Pass | Attended site found charger fault and system on batteries led fault on EWIS panel, investigated and found that EWIS PSU needs to replaced.Advised site on departure.BRAF submitted - no response. Please supply new work order if proceeding.
MSA-DCA | WA3337849 | Level basement and 4 Fire panel devices in fault | Art Gallery of WA - James St - Main Building (Block B) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 15:30:00 | Pass | Attended site for the following faultslevel 1 reference vesda in conventional fault, found vesda isolated by others causing fault at fip. Liased with site Deisolated and left in normal operation.L4 concourse loop 4 sensor 32 in maintance fault located detector at high level and replaced with extension pole. Reset fip and left in normal operation
MSA-DCA | WA3337980 | Multiple mechancical services alarms after power interruption | Art Gallery of WA - James St - Centenary Gallery Ground Floor - Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 13:30:00 | Pass | Multiple alarms active on site due to power maintenance the night before. Water tray alarm active in L1 Collections. Inspected and located faulty sensor in store 1. Isolated faulty sensor and reset panel. Carried out manual reset of all mech plant on L4 and Centenary. Monitored alarms during reset period.All alarms cleared.Jobs found during investigation raised with Programmed Closed job.
MSA-DCA | WA3338011 | Investigate fault on AC 9 humidifier | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 15:30:00 | Pass | Humidifier in over current fault. Reset fault and monitored operation. Water fill did not stop at fill level. Cylinder leaked from seals. Isolated unit. Removed cylinder and cleaned tank and water sensor. Re installed. Humidifier breaker had tripped. Checked terminals and reset. Operated unit in manual 100% humidification. Monitored water fill, fill stopped at mark. Monitored heater banks, during next open inspection will re assess replacement of elements, corrosion on fins.While on site, AMT requested an inspection of the Air Dryer as Fire systems had low pressure alarms in basement. Found no flow through dryer chamber. Isolated and bypassed until assessment can be made.No further alarms or issues reported for Humidifier AC 9.Closed job.
MSA-DCA | WA3338093 | Lift doors are shuddering when they close and taking a very long time for the doors to close. | Maritime Museum Victoria Quay-Main Building-Ground Floor-Hoist Room - Within Loading Dock | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 13:30:00 | Pass | Job completed -Upon arrival at site, the technician performed the following:GUIDE RAILS - GUIDE SHOES-ROLLER - COMPONENT DAMAGED
MSA-DCA | WA3338232 | RO plant water running down drain | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-06-02 10:00:00 | Fail | Carried out investigation into water leaking in Plant Room. Checked all cycles of controller and monitored flow. Waste chamber always leaking water during any stage. Contractor to attend for repairs.Arranging induction registration for contractor to access site
MSA-DCA | WA3338406 | Centenary Gallery, RO booster pump is leaking | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 17:30:00 | Pass | RO Booster Pump in gnd plant room, Centenary Gallery, has hairline crack in base of housing. Retrieved details, awaiting quotation from manufacturer to replace. Due to Humidifiers 1-4, 6-8 no isolation of RO water is possible.Closed job. Quotation to replace the pump will be submitted.
MSA-DCA | WA4112930 | RETROSPECTIVE WORK ORDER-Lift - Automated fault alarm after power failure-Ref WA3337984 | Art Gallery of WA - James St | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | COMP | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 17:30:00 | Pass | COMPLETED
MSA-DCS | WA3336714 | Entry door to the Unit 1 office doesn’t lock – appears to be faulty. | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 19 May 2020 | 2020-05-20 07:01:11 | 2020-05-19 10:30:00 | Pass | Replaced Broken lock on Security Screen Door adjusted main door lock and locking strike
MSA-DCS | WA3336720 | Scan ground beneath flag poles for any services | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 May 2020 | 2020-05-25 17:00:00 | 2020-05-21 09:15:00 | Pass | Helped scan area for future digging locationing services
MSA-DCS | WA3336734 | Boilerhouse- Boiler 2 not starting up | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 19 May 2020 | 2020-05-20 07:17:38 | 2020-05-19 16:00:00 | Pass | Travel to site sign inStart up 3 boilers and complete safety checks then bring onlineTravel to site sign inIsolate boilers at main switch close main steam stop at header shut feedwater valves complete blowing down of all 3boilers and blowdown gauge glass mounts
MSA-DCS | WA3336738 | C Wing Showers- Fluro light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 May 2020 | 2020-05-21 17:00:00 | 2020-05-19 15:00:00 | Pass | Repaired light
MSA-DCS | WA3336741 | Unit 3, Cell C2- Toilet cistern leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 May 2020 | 2020-05-21 17:00:00 | 2020-05-21 09:20:00 | Pass | Re sealed orings under screws on cistern to stop leak.
MSA-DCS | WA3336750 | Recreation, TC Room- Door Lock fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 19 May 2020 | 2020-05-21 17:00:00 | 2020-05-21 08:45:00 | Pass | Job complete- Adjust striker and hinges to TC room door recreation hall
MSA-DCS | WA3336762 | Kitchen- Sea container freezer not working | Karnet Prison Farm | WSM-BR-SITE | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 May 2020 | 2020-05-20 07:35:37 | 2020-05-22 17:00:00 | Fail | essential ref found compressor tripped , test and found compressor needs replacing . replace compressor and commission.
MSA-DCS | WA3337793 | Kitchen - Cool Room 3 constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 19 May 2020 | 2020-05-20 08:08:45 | 2020-05-19 13:00:00 | Pass | System is at set point and running
MSA-DCS | WA3337802 | Canteen - light switch in toilet broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 11:30:00 | Pass | Replaced damaged switch in Canteen
MSA-DCS | WA3337807 | Gate House- cell call system recording wrong time in recent call area | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-19 11:30:00 | Pass | Attended site and investigated cell call fault. Found Tecera PC time out by 5 minutes. Re adjusted time server and restarted server. All restarted and tested ok. Tested cell calls and all tested ok. Job complete
MSA-DCS | WA3337812 | Karakin, B Wing- Smashed window approx 1400x600 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-22 09:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3337858 | L4 lights keep turning off after a period of time-see notes | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | LYNX INTEGRATED SYSTEMS | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-06-10 10:00:00 | Fail | Job completed - pre programmed 2x new touchscreens
MSA-DCS | WA3337882 | Boilerhouse- Leak from steam pipes below roof | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-06-10 10:30:00 | Fail | Carry out repairs and re-lag pipework using scissor lift to gain access.
MSA-DCS | WA3337924 | Rusted door frame to yard door from main hall | Nyandi Training Academy | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-10-09 11:20:00 | Fail | DOOR FRAME REPLACED
MSA-DCS | WA3337957 | Unit 2, C Wing- Grill Lock Jamming when unlocking | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 May 2020 | 2020-05-20 09:41:57 | 2020-05-19 13:45:00 | Pass | No completion notes
MSA-DCS | WA3337972 | Repair SOG ring road as per information provided to Sam Groenveld | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-07-31 16:30:00 | Fail | 31/07/20Completed works carried out:Area 1) rear of ring road, near panels 11 and 10:3m x 1.5m across road at soakwellCut / Lift entire area / Reset road base / Emulsion / Lay 30mmArea 2) rear LHS corner of ring road, near panel 8:2.5m x 2m potholed areaCut / Lift entire area / Reset road base / Emulsion / Lay 30mmArea 3) LHS of ring road, near panel 7:1.5m x 700mm tree root damageCut / Lift entire area / Remove small tee root / Reset road base / Emulsion / Lay 30mmArea 4) main drive near 1st car park, at crossing 1:Corner blow out3m x 3m Cut / Lift entire area / Reset road base / Emulsion / Lay 30mmNew mountable kerb 5m
MSA-DCS | WA3338060 | Outcare- Reset family visitor centre kitchen light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 10:00:00 | Pass | Repaired lights in Outcare kitchen
MSA-DCS | WA3338092 | moniter camera 35 not responding to alarm or joy stick | Boronia Pre-release-External Area-Ground Floor | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 May 2020 | 2020-05-20 11:13:22 | 2020-05-21 15:33:00 | Fail | System operating correctly
MSA-DCS | WA3338115 | Unit 6 garden- Tap needs repair | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-19 12:30:00 | Pass | Isolate water service, drain down pipe work, weld pipe work to seal leak. De-isolate and test.
MSA-DCS | WA3338127 | Kitchen, Prisoner Day Room- Billi water cooler the bubbler has water flowing constantly | Casuarina Prison | WSM-BR-SITE | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-22 09:45:00 | Pass | Replaced bubbler assy
MSA-DCS | WA3338175 | PO's Site Cabin- Power keeps tripping | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-19 13:30:00 | Pass | Repaired lights
MSA-DCS | WA3338189 | Eastern Gym faulty 4 maintenance locks on doors with MKR locks | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-07-20 13:00:00 | Fail | JOB COMPLETED - Supplied & fitted door hardware as quoted.
MSA-DCS | WA3338200 | Unit 1 - B Wing-Broken external window and viewing hatch window in Cell B03 | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 19 May 2020 | 2020-05-20 12:11:10 | 2020-05-19 19:45:00 | Pass | windows reglazed
MSA-DCS | WA3338201 | Pre release Unit - main entrance of Unit 4 electronic door access button is not working | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 12:24:00 | Pass | Re terminated POE
MSA-DCS | WA3338297 | Boilerhouse- Boiler 2 not starting | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-25 12:30:00 | Fail | 20/05/2020Attend site 7:30 am - Start up boilers/ Return to site 2 pm to shut boilers down.21/5/2020Attend site 7:30 am - Start up boilers/ Return to site 1:45 pm to shut boilers down.22/5/2020Attend site 07:00 am - Start up boilers/ Return to site 2:45 pm to shut boilers down.25/05/2020Attend site 11:00 am - Boiler 2 & 3 not filling, found air lock in feed water pumps bleed all three pumps and fill boilers, reset lo water alarms and fired boilers.
MSA-DCS | WA3338334 | Unit 2, A & B Wing Kitchen- Broken light | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 08:00:00 | Pass | Investigate and repair light in Unit 2 A and B Kitchen
MSA-DCS | WA3338336 | Front Gate- Air Lock Door Intermittently Not Latching | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 May 2020 | 2020-05-20 13:28:56 | 2020-05-19 15:00:00 | Pass | Attended and investigated, the door is bouncing from the door frame and not locking from time to time. found worn out rubber stoper from door frame. Advice SO on site and maintenance that they require another contractor to fixed the door frame.Not our scope of work.
MSA-DCS | WA3338416 | Unit 14 EC14 power supply faulty | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 11:00:00 | Pass | Replaced faulty 24vac power supply
MSA-DCS | WA3338417 | DDU office complex entrance way and centre of grass paving needs re-leveling | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Paving (PR) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-09-01 14:30:00 | Fail | new concrete pad laid and center paved seating area removed
MSA-DCS | WA3338496 | kitchen remove damaged RCD to rotel oven | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-06-04 13:30:00 | Fail | Disconnected broken oven
MSA-DCS | WA3338507 | Front gate Prison Side Air Lock Door Rubber Seal Stopping Door From Latching | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 May 2020 | 2020-05-20 14:45:58 | 2020-05-20 16:00:00 | Fail | job completed - inspected doors user error, doors are fine
MSA-DCS | WA3338560 | SOG Training wing air con is too hot | Hakea Prison | GMP-BR- HO | Air Conditioning | Ducted Split System (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-20 16:00:00 | Pass | Unit operating correctly. Fault due to user error.
MSA-DCS | WA3338566 | Unit 4 B wing Day room GPO faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 15:00:00 | Pass | Replaced gpo
MSA-DCS | WA3338569 | Main visits area - Vinyl is bubbling in different spots and require repair | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-09-09 14:45:00 | Fail | rubber flooring repaired
MSA-DCS | WA3338570 | unit 3 S/O light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 10:00:00 | Pass | Replaced lights
MSA-DCS | WA3338573 | unit 9 C9 Tap leaking under sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-22 14:58:00 | Pass | Replaced trap washer
MSA-DCS | WA3338580 | Unit 4 Camera 9 dirty camera lens | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 12:27:00 | Pass | Cleaned all PTZ cameras unit J + L
MSA-DCS | WA3338601 | Scanning of the underground service locations to ready for isolation valve works | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 14:40:00 | Pass | Scanned for underground services
MSA-DFES | WA3336704 | Pipe underground near the HWS has burst , water is going every where. I | CFRS Joondalup | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 0 | CLOSE | 19 May 2020 | 2020-05-19 10:50:09 | 2020-05-19 09:45:00 | Pass | 19/05/2020Arrived on site to repair burst pipe underneath brick paving near hot water system in the corner of the building dug up and found 25MM was burst and the 20 MM was burst as well used to 25MM couplings and 1 m of pipe for the cold side used to couplings on the 20 MM hot side tested and working correctly drained out the sand out of the lines and brick paved up.
MSA-DFES | WA3337900 | Sink in the SODP Dining room is blocked, water drains away very slowly | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 15:45:00 | Pass | Investigated blocked drains and found the pump pit to be full after lifting the lid, I found the pump to be isolated. Turned pump on and watched it pump down. Flush all toilets and sinks. All working correctly.
MSA-DFES | WA3337904 | BAT Building, control panel button has been pressed on control board & is stuck down | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-06-05 14:00:00 | Fail | Complete Located BAT room and found damaged switch, isolated power and changed over switch mount
MSA-DFES | WA3337907 | Driveway near Heritage Shed not working -see notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-07-17 16:00:00 | Fail | Replaced faulty light head on crapark pole lights. Tested and all in working order returned scissor lift
MSA-DFES | WA3337911 | Ladies Toilet (opposite Reception)- Lock on external door is slipping | FESA RHQ - Forrestfield | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-21 10:25:00 | Pass | Attend site to repair strike and service lock.
MSA-DFES | WA3337915 | Broken sprinkler near the First Aid Post of the Heritage Shed. | FESA RHQ - Forrestfield | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 17:00:00 | Pass | Call out & repair sprinkler
MSA-DFES | WA3337920 | Car Parks A & B – paving has sunk near curbing creating a trip hazard. | FESA RHQ - Forrestfield | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-06-10 13:45:00 | Fail | BRAF has been submitted for approval 11/6 works are now completed and the paving is level
MSA-DFES | WA3337923 | Pathway,near eAcademy Office- Several pavers are being raised due to tree roots | FESA RHQ - Forrestfield | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 15:30:00 | Pass | Pavers taken up, roots removed causing issue and pavers re-laid
MSA-DFES | WA3337928 | Change Room 1- Hand wash basin leaking near the base | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 11:24:00 | Pass | Repairing the leak under the basin
MSA-DFES | WA3338034 | Boundry fence - Roe Highway - barbed wire has been cut | FESA RHQ - Forrestfield | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-20 09:00:00 | Pass | Works are now completed - Wire sections have been replaced
MSA-DFES | WA3338041 | Engine room Charge cord retaining wire has come off socket. Needs re-swaging. See notes | CFRS Kiara | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-21 16:00:00 | Pass | COMPLETED
MSA-DFES | WA3338549 | Bushfire Risk Management Area water damge to wall cavity & carpet below window-see notes | DFES Regional Office - Belmont | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-06-04 13:15:00 | Fail | Run stormwater drain and connect downpipe
MSA-DFES | WA3338554 | Bushfire Risk Management Area Water damage in floor to ceiling and cupboard-see notes | DFES Regional Office - Belmont | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-06-25 14:30:00 | Fail | Sourced leak - think the pointing on bricks may be letting the water in - measured up for a flashing. Returned with materials - install parapet flashing to divert water from problematic area
MSA-DFES | WA3338609 | area 2 electric fence goes into alarm when armed | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-21 12:15:00 | Fail | Complete
MSA-DFES | WA3338639 | Front glass sliding door is not responding - unsure if security programming or door itself | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 19 May 2020 | 2020-05-19 21:53:44 | 2020-07-16 14:30:00 | Fail | Technician attended the site of Cockburn Emergency Services Centre main entry automatic door on 19/05/2020. Noted door not remaining locked. Inspected with Sontec and found access system operating ok. However there was an issue with the mode inputs not selecting correct door modes. Required to alter wiring and Sontec altered access to suit as temporary measure to enable door locking and day mode. Required new logic unit and mode, sensor connection board.16/07/2020. Removed existing faulty controller replaced it with a new controller set up access all ok.29/07/2020. Replaced faulty existing Rubek controller with an Assa abloy MUK upgrade SL 500-2 setup access system test all ok as approved Option 2.Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3338643 | Front glass sliding door is not responding - unsure if security programming or door itself | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 0 | CLOSE | 19 May 2020 | 2020-05-19 22:00:02 | 2020-05-20 02:00:00 | Fail | 19/5/20 - Dean Simpson, Dylan ParslowAfter hours call out.Investigated issues with front auto door.Found day/night cable loose in the door head. Tested cable all ok.Instructed to stay onsite and wait for door contractor.Door contractor rewired door hardware.Reprogrammed door functions to GMS temporarily to test door.All tested ok from our end.
MSA-DTAG | WA3337991 | Basement,Carpark- Door handle leading to Judges lift has become detached | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 14:00:00 | Pass | RE ATTACHED DOOR HANDLE
MSA-DTAG | WA3338121 | Multiple L9 is out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 13:30:00 | Pass | Not chargeable
MSA-DTAG | WA3338167 | Staff toilet Female toilet pan is leaking/right hand cubicle toilet in corridor adjacent to Court 1 | Supreme Court-Supreme Court Building-Ground Floor | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 12:00:00 | Pass | Replaced leaking flexi and inlet vakve
MSA-DTAG | WA3338469 | kitchen located in public area light bulb needs replacing | Rockingham Justice Complex | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-20 09:50:00 | Pass | Replaced blown lamps in kitchen and faulty light fittings and tested working
MSA-DTAG | WA3338535 | Limestone wall seperates walkway and grass area removed-see notes | Joondalup Courthouse | GMP-BR-HO | Building | External Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-07-22 15:00:00 | Fail | LIMESTONE WALL HAS BEEN REPOINTED
MSA-DTAG | WA3338563 | L3 court 32 Screws on the chairs in the dock need tightening | Central Law Courts | GMP-BR-HO | Furniture | Office Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-21 08:45:00 | Pass | bolts tightened
MSA-DTAG | WA3338603 | ground disable toilet not flushing | Mandurah Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-21 15:00:00 | Fail | Complete
MSA-DTWD | WA3336731 | A Block- Exit light buzzing near offices A126 entry door east End | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 19 May 2020 | 2020-05-19 17:00:00 | 2020-05-19 10:18:00 | Pass | Inspected apprentice noise coming from exit signs . All seems fine. Job completed
MSA-DTWD | WA3337995 | Graffiti on external wall | Armadale Campus - 40 Commerce Ave | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 15:00:00 | Pass | REMOVAL OF GRAFFITI FROM EXTERNAL WALLS
MSA-DTWD | WA3338007 | Air con blowing cold air-See notes | Armadale Campus - 145 Jull Street | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-06-03 09:30:00 | Fail | Found heater bank fuses removed and stage 2 comp sump heater failed. Refitted fuses and replaced heater.
MSA-DTWD | WA3338020 | Block 3 - Dyno cold well leaking | Thornlie Campus | GMP-BR | Building | Foundations (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 09:15:00 | Pass | Cost to date only as works are not proceeding
MSA-DTWD | WA3338055 | house 803 Power line is sparking . The one that goes from line to the house | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 15:30:00 | Pass | Repaired cabling
MSA-DTWD | WA3338120 | B Block, Room B104- Issues with CCTV software | Leederville Campus | GMP-BR | Security | CCTV Surveillance (SE) | Securex Security Systems & Services | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-21 15:00:00 | Pass | Installed IVMS-4200 software on other facilities computersReset passwords for NVRs for Block C, D and G.
MSA-DTWD | WA3338134 | Block 9, Library - Damaged carpet needs repairing | Thornlie Campus | GMP-BR | Flooring | Carpet (FL) | Creative Flooring Pty Ltd | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-30 13:00:00 | Fail | job completed- repaired damaged joins
MSA-DTWD | WA3338136 | Block 8, Main Entry - Damaged carpet needs repairing south entry | Thornlie Campus | GMP-BR | Flooring | Carpet (FL) | Creative Flooring Pty Ltd | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-30 15:00:00 | Fail | job completed- installed new matting
MSA-DTWD | WA3338161 | D block D24 Staircase - 2x Faulty light fittings | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-07-07 14:07:00 | Fail | BRAF was declined, invoice cost to date
MSA-DTWD | WA3338169 | A Block, Server Room- Refix GPO | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-06-12 13:30:00 | Fail | Relocated gpo in server room.job completed
MSA-DTWD | WA3338173 | E block E49 - Split system air con not working | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-28 15:35:00 | Fail | INVESTIGATED AND FOUND THAT THE 4 WAY VALVE WAS STUCK ON COOLING. BRAF SUBMITTED TO REPLACE. COMPLETED REQUIRED PAPERWORK AND SIGNED OUT.ARRIVED ON SITE SIGN IN ASSISTING LUKE RICHMOND WITHSPLIT ON ROOFTRAVELLED TO COLLECT PARTSM TRAVELLED TO SITE AND SIGNEDIN. CARRIED OUT WORKS AS PER BRAF. COMPLETED REQUIRED PAPERWORK AND SIGNED OUT.
MSA-DTWD | WA3338213 | Block C C006 The heater in C006 is not coming on, | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | Precise Air Group | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-20 15:00:00 | Pass | Accessed site and room c006. Found a/c not even coming on fan only.Isolated unit and removed panels.Found power ok.Evap mtr contactor overload tripped.Inspected evap area. Found belt alignment out due to wear and tear and bracketry of mtr mount.Installed new belt. Test ran to find amps high on breaker.Adjusted variable speed pulley to correct fan speed and replaced faulty buzzing contactor to 4amp, rewired to suit.Found upon heat test temp set too high. Located stat in r/a. Adjusted to suit.Temps and airflow as desired
MSA-DTWD | WA3338215 | L Block Ladies toilet light doesn't work. | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 08:30:00 | Pass | Repalced faulty electronic ballast and lamp to light L block ladies toilets. Job completed
MSA-DTWD | WA3338221 | A block L2 A276 A/C not working. | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-06-12 14:00:00 | Fail | Picked up required parts,attended site, isolated and tagged out system,set up barricades and ladder inside room a276.removed and replaced all faulty parts including two indoor pc boards,fan motor,capacitor,stepper motor and sensor board.cleaned up work area and tested system.left system operational
MSA-DTWD | WA3338243 | E Block- Door lock faulty getting stuck | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Locksmith (SE) | GRONBEK SECURITY | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 10:30:00 | Pass | Supplied & installed new cylinder
MSA-DTWD | WA3338274 | L block Security lights not working in carpark 1 | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 19 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 11:00:00 | Pass | Repalced multiple lamps ,starters and ballasts to security lights L block. Tested all working properly job completed.
MSA-DTWD | WA3338275 | A Block, Cafe - Display fridge not cooling | East Perth Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-19 16:30:00 | Pass | Attended site found display fridge in cafe area to be short of gas,pressure tested system, pin hole leak to be coming from indoor evaporator coil. Evacuated system and gased accordingly tested system and found to be reaching temperature.left system all operational.request to change out evaporator coil if issue persists
MSA-DTWD | WA3338379 | F block F20 male toilet faulty cistern | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 16:07:00 | Pass | Replaced broken cistern
MSA-DTWD | WA3338412 | Boilers in fault please check heating boilers and adjust a/c set points | West One Services | GMP-BR | Mechanical Services | Boilers (MS) | Precise Air Group | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 16:00:00 | Pass | Arrived on site, invesgigsted boiler, found was on fault,reset and started working with no issues, suspect a blipin computer, once boiler was working monitored it cycledtemp of 73 degrees, all working well , adjusted temps to24 cooling 22 heating and see if eveyone finds this ok ,if not adjust to suit
MSA-DTWD | WA3338485 | S block L1 S110 CCTV Computer has alarm fault on it | Mount Lawley Campus | GMP-BR | Security | CCTV Surveillance (SE) | Securex Security Systems & Services | 1 | CLOSE | 19 May 2020 | 2020-05-20 17:00:00 | 2020-05-28 08:13:00 | Fail | 19/05/2020, 1515-1530Cctv had unacknowlege alarm . Reset alarm all back normal
MSA-DTWD | WA3338602 | B block B2220 – Damaged wall mounted urn in kitchenette | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 19 May 2020 | 2020-05-26 17:00:00 | 2020-05-21 16:10:00 | Pass | Replaced urn
MSA-DCA | WA3339360 | FIP - fire log has activated, fire brigade arrived and advised of low pressure for sprinkler | State Library of WA-Main Building-Ground Floor-GF12 - Security Office - Control Room | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 20 May 2020 | 2020-05-20 11:58:49 | 2020-05-20 15:30:00 | Fail | low air pressure alarm. Aircompressor required reset after investigation (client reset)Mechanical Fire had to attend site to fill system with air pressureobserved until fulldeisolated FIP - system normal on leaving siteOn arrival low air pressure alarm was present.Pre-action system had 0kpa air pressure, investigated issue and found inline air Heater to be the issue.Client repaired issue with in-line heater, providing air pressure.Mech fire attended to assist with re-pressurising the installation end of the deluge pre-action.Observed the system re-pressurisation. reset alarm, de-isolated FIPAll systems normal (note: beam detectors isolated due to works)
MSA-DCS | WA3339255 | One of the PE beams in zone 12 is constantly alarming. | Roebourne Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 May 2020 | 2020-05-20 14:25:52 | 2020-06-24 11:00:00 | Fail | Job complete
MSA-DCS | WA3339288 | waste Water treatment plant - plant wont start | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 1 | CLOSE | 20 May 2020 | 2020-05-21 07:12:50 | 2020-05-27 11:20:00 | Fail | See SR WO7974 attached
MSA-DCS | WA3339309 | Yeeda, CUE - yard - Led lighting not | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 May 2020 | 2020-05-22 17:00:00 | 2020-05-28 11:00:00 | Fail | Repaired light
MSA-DCS | WA3339319 | Yeeda, CUE obs 2 - Scratched camera | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 May 2020 | 2020-05-22 17:00:00 | 2020-05-28 10:05:00 | Fail | Replaced laminate for new and tested image good.
MSA-DCS | WA3339326 | Yeeda, CUE obs 4 - Exhaust fan fault light is on | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 20 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 15:14:00 | Pass | Complete
MSA-DCS | WA3339336 | Control - camera 288 is not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 May 2020 | 2020-05-21 07:44:28 | 2020-05-22 09:45:00 | Fail | Rectified and fixed the video fault, camera back to normal. Job completed.
MSA-DCS | WA3339340 | MPU (8), M16 & M20 have broken yard windows and M20 also has broken vewing hatch window | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 20 May 2020 | 2020-05-21 07:41:18 | 2020-05-20 19:00:00 | Pass | ALL WINDOWS RE GLAZED
MSA-DCS | WA3339343 | Unit 13, B10 - blocked toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 May 2020 | 2020-05-26 17:00:00 | 2020-05-20 11:30:00 | Pass | Plunge toilet to clear blockage, test several times.
MSA-DCS | WA3339349 | INF, B wing, B6 - observation light globe needs repair/replacing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 May 2020 | 2020-05-26 17:00:00 | 2020-05-21 15:00:00 | Pass | Repaired faulty lights in infirmary b6
MSA-DCS | WA3339369 | skills external security flood light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 May 2020 | 2020-05-26 17:00:00 | 2020-05-21 15:00:00 | Pass | Investigate and repair skills workshop external floodlight
MSA-DCS | WA3339398 | Security office - Key watcher will not produce consistent reports or reports from the dates listed | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | BJ SYSTEMS | 1 | CLOSE | 20 May 2020 | 2020-05-21 08:13:02 | 2020-05-22 13:30:00 | Fail | Dion Maher (22/05/2020) - Work NoteCheck and run reports. Confirmed events missing. Copied DB and backups off for further investigation BJ Systems (17/06/2020) - NoteContacted site for return visit. Site no longer requires BJ Systems attendance as KeyWatcher upgrade contract has been awarded to another contractor
MSA-DCS | WA3339406 | Unit 5, Staff Lunch Room- Light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-21 10:30:00 | Pass | Repaired light
MSA-DCS | WA3339419 | Unit 5, Medical Room- Light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-26 12:00:00 | Fail | Replaced light
MSA-DCS | WA3339421 | Laundry- Sheet Machine sight glass leaking steam and water | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-06-16 06:53:00 | Fail | Supply & Install new 20mm sight glass and nipple
MSA-DCS | WA3339426 | Reception- A/C not working | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 10:30:00 | Pass | Found no fault on arrival and unit running on heating. Tested in all modes and checked components. All ok. Unit is a multihead system with 2 indoors and both must be on the same setting. All operational at time of departure
MSA-DCS | WA3339523 | Control room - Call cell system not working - gatehouse network error | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 May 2020 | 2020-05-20 13:12:49 | 2020-05-20 16:00:00 | Fail | Provided site with technical phone support, sourced parts (spare officer station console), attended site, found network faults and calls not coming to gatehouse from units and Site Management software not starting on server. Corrected software fault on server, checked all nodes, found several nodes offline and intermittent calls from unit 16 jamming system.Corrected issue and tested OKJob CompleteNo parts used.
MSA-DCS | WA3339554 | Gate control external perimeter log faulty | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-06-10 09:00:00 | Fail | Fault rectified before I arrived on site. Staff were going to cancel the job but did not. Used time to alter CCTV presets as requested.
MSA-DCS | WA3339557 | gate control PTZ 1,3,4 and 9 cameras faulty lagging and dropping out | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-29 14:49:00 | Fail | Investigated multiple cameras lagging. Repaired network and workstation faults. Recommend workstation upgrade and network review.Tested OKJob Complete
MSA-DCS | WA3339562 | ICF admin computer is not talking to monitors | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-27 14:38:00 | Fail | Investigated computer fault in Security, traced fault to corrupt software operating system. Moved computer to gatehouse, downloaded all software required from internet, reinstalled all software, configured, reinstalled, customised as per Security Manager.Tested OK.Job Complete
MSA-DCS | WA3339583 | Unit 1, Pod 7- PA speaker not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 17:00:00 | Pass | Replaced faulty PA speaker
MSA-DCS | WA3339589 | Officers house 1- power faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 18:00:00 | Fail | Replaced faulty outlet and cable
MSA-DCS | WA3339590 | abattoir - electric hoist not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 May 2020 | 2020-05-21 09:39:43 | 2020-05-20 15:30:00 | Pass | Investigate abattoir hoist, Found damaged cable - repaired cable.
MSA-DCS | WA3339881 | Control room - 2x personal duress alarms not working 62 & 184 | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 May 2020 | 2020-05-21 10:22:58 | 2020-06-17 16:15:00 | Fail | Spoke to Security Officer NARANG who believed that transmitter 184 had also now been repaired. Located the officers with keys/alarms 62 and 184. Both tested ok.Transmitter left onsite as spares
MSA-DCS | WA3339896 | Visits, Non Contact area- intercom in non contact 7 not working (to quiet) | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-22 11:15:00 | Pass | Attended and test the intercom with officer, working ok. Job completed.
MSA-DCS | WA3339901 | CCu (11) Dayroom & main corridor- Several Fluros are not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-21 13:30:00 | Pass | Repaired multiple faulty lights in CCU corridors and dayrooms
MSA-DCS | WA3339902 | Unit 14, Cell A5 - clogged shower drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-20 14:30:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3339906 | Unit 14, A wing, Cell A9 - clogged shower drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-20 10:40:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3339907 | Unit 13, B Wing, Cell B1- Main light is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 08:30:00 | Pass | Repaired faulty lights in unit 13 b wing
MSA-DCS | WA3339917 | CCU (11), Cell C5- Obs hatch handle is damaged | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-06-11 14:15:00 | Fail | DOOR HATCH REPAIRED
MSA-DCS | WA3339954 | Cameras 34,35 & 38- no visual | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 May 2020 | 2020-05-20 15:02:21 | 2020-05-27 10:45:00 | Fail | Installed the new UPS and connect all the security systems from OBS 6, job completed.
MSA-DCS | WA3339955 | External mircowaves 12 & 13- no activation | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 May 2020 | 2020-05-20 15:05:50 | 2020-05-20 14:30:00 | Pass | Rectified and fixed the faulty power and test the zones, job completed.
MSA-DCS | WA3339957 | unit 3, D9 - tv antenna faulty/socket broken | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 09:30:00 | Pass | Attended site. Replaced connector & crimp in Unit 3, D9. Tested signal, OK.Job complete
MSA-DCS | WA3339962 | Unit 4, D Wing, EM13- landing light faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-20 15:00:00 | Pass | Replaced faulty emergency light in unit 4 D wing
MSA-DCS | WA3340016 | Education center kitchen auto boil not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-21 10:15:00 | Pass | replaced Rheem Level Sensor to Rheem BWU in Education Centre - Technician advised site that due to age of this unit these repairs may be enough to keep the unit working for long and advised that whilst the unit was working on departure it may be worth looking at replacing this asset we are quoting for a replacement also.
MSA-DCS | WA3340035 | Video link, Panic room door - Panic room door is emergency locked | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 May 2020 | 2020-05-21 11:40:49 | 2020-05-20 16:33:19 | Pass | Job completed - onsite and repair video link panic room door
MSA-DCS | WA3340041 | Unit 7, H wing - plug broken needs repair/replace | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-21 09:00:00 | Pass | Replaced broken plug
MSA-DCS | WA3340043 | unit 1 cell A8 vinyl flooring damaged | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 20 May 2020 | 2020-05-21 11:48:57 | 2020-05-20 17:15:00 | Pass | VINYL REPAIRED
MSA-DCS | WA3340052 | Visits centre 4 Downlight bulbs blown | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-26 14:00:00 | Fail | Replaced lights
MSA-DCS | WA3340065 | Unit 14, A Wing, Cell A11- shower drain clogged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-21 08:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test. Plunge basin.
MSA-DCS | WA3340077 | SOG comand centre is going off for no reason fault | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 20 May 2020 | 2020-05-20 16:06:54 | 2020-05-20 16:30:00 | Fail | job completed - Checked log file reported event. Rectified Main Armoury REX alarm that has been activated Door forcedaround reported event. Controller 3 DIP switch 2 is not configured yet. That is the controller in PFM stores
MSA-DCS | WA3340083 | Unit 14 - A Wing Basin and shower clogged Cell A10 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-20 15:30:00 | Pass | Remove and replace damaged aerator in basin, unblock shower head.
MSA-DCS | WA3340187 | New video link bolt hold electric latch wont reset | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 May 2020 | 2020-05-21 13:28:43 | 2020-05-20 17:30:00 | Pass | Trace the fault on emergency button that failed to activate the custodial lock, rectified and fixed. Job completed.
MSA-DCS | WA3340228 | Unit 3 B11 window sliding hatch needs repaired damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-06-11 13:00:00 | Fail | SLIDING HATCH REPAIRED
MSA-DCS | WA3340250 | Unit 1, B Wing. Cell B3- Tap has come away from the basin | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-21 09:00:00 | Pass | Tighten up basin spout under basin in cell.
MSA-DCS | WA3340263 | Unit 1, A8 - toilet service hatch damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 May 2020 | 2020-05-21 14:33:43 | 2020-05-21 11:18:00 | Pass | Panel heated straight inspection hat reinstalled with new security screws
MSA-DCS | WA3340308 | Maintenance workshop- Controller offline | Boronia Pre-release-AS20 - Industries Vocational Skills Development-Ground Floor-Workshop Area | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-21 14:30:00 | Pass | Collected parts, attended site and found controller not communicating , tested fiber with light source and all tested ok. Replaced with new 6000 controller and all programmed and working ok.Replaced old fiber modem with new S714 fiber modem set. All replaced and tested building alarms, all working ok. 1 x 6000 controller and 1x S714 fiber modems used. Seme stock usedJob complete
MSA-DCS | WA3340327 | entry building air lock doors both door open at the same time | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 May 2020 | 2020-05-21 15:54:13 | 2020-05-21 09:00:00 | Pass | Third party required for repair.
MSA-DCS | WA3340336 | Unit 9 C5 Retapping of screws required to hinge as screw broken off | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-06-10 12:00:00 | Fail | Replaced hinges
MSA-DCS | WA3340363 | perimiter camera 46 not working at all-SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-21 20:23:00 | Pass | Replaced S732DVT RST2 from site stock Camera has PTZ function
MSA-DCS | WA3340365 | control room keyboard and mouse fail - SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-21 20:20:00 | Pass | Keyboard and mouse intermittently working on DCP and PDS.Sourced 5x wireless keyboard and mouse combos from local supplier.Replaced PDS,DCP,FREEZE FRAME, UVSS and MDAS.Cable management of control room
MSA-DFES | WA3339810 | Applied training - Light not working in Unisex Toilet/Shower #3 & Exhaust fan is still turning on | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 15:15:00 | Pass | COMPLETED
MSA-DFES | WA3339841 | Main Administration, reception - Door leading to Parade Ground is not shutting properly | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-20 14:00:00 | Pass | Works are now completed and the door mechanism is functioning correctly - See photos attached
MSA-DFES | WA3340134 | ground floor lift lobby sliding door egress button not working | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 20 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 17:30:00 | Pass | 20/5/20 - Dylan Parslow2 door controller not responding on egress activation.Power cycled and tested, fault rectified.20/5/20 - Dylan ParslowReturn visit after fault returned.Replaced 2 door controller, and checked all door functions.Door operating correctly.
MSA-DFES | WA3340314 | Damien Pumphrey’s Office- Door is faulty & will not close properly & is a bit loose | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 12:00:00 | Pass | Works are now completed, door removed and re-aligned - Please see photos attached
MSA-DTAG | WA3339358 | FIP - Technician required to attend & assist Australian HVAC Friday 22 May 2020 from 07.45am | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-22 09:00:00 | Pass | Meet consultant on site to talk about ongoing issues with fire system and mech services. Quotes will be sent through to fix issues. Panel returned to full function
MSA-DTAG | WA3339363 | FIP - Technicians required to attend & assist Lucid Consultants on Friday 22 May 2020 from 07.45am | Joondalup Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-22 12:00:00 | Pass | Attend site.Meet with consultant and fire technicians. Go over issues with current operation of the fire panel. Assist consultant with location and access to plantrooms. Confirm fire relays still energized on active fire alarm. Consultant to review and report recommendation.Carry out further checks on fire system operation throughout building
MSA-DTAG | WA3339432 | Ground, Links office - 16 Degrees in one section of the building | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-28 16:30:00 | Fail | Mark Kember (20/05/2020)Attend site. Access cold office at rear of building. Found staff member complaints about being too cold. Check Airconditioning serving this office, found to have 3 outlets. Access ceiling space and found location of outlets. Found one outlet situated directly above staff member and blowing straight down. Obtain commissioning data on airflow and found to be correct. Access balancing damper for outlet and completely shut. Found air to stop dropping straight down. To maintain correct airflow in room without causing discomfort to staff i recommend relocating this outlet to a different position in the office.Mark Kember (27/05/2020)Pick up gear required for works. Attend site, access rear office. Cover all computers on desks. Remove ceiling tiles from ceiling to access outlet. Disconnect duct fron outlet. Remove outlet from ceiling. Run duct toward other side of room. Install new section of duct to extend to new location. Fit outlet in new position. Connect duct
MSA-DTAG | WA3339436 | Ground - Multiple lights flickering | Perth Children's Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-22 08:45:00 | Pass | Job complete
MSA-DTAG | WA3339453 | Basement, car park - Digital lock on door leading to lift 2 is jamming | Supreme Court | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 20 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 10:16:00 | Pass | Attended site, lockwood 530dx failed and latch gets jammed.Stripped lock, tightened components and lubricated mechanisms.Reassembled, all working.Date on site: 20/05/2020Time onsite: 09:45am - 10:15am
MSA-DTWD | WA3339441 | Student lunch room- Tap is leaking | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-20 11:57:00 | Pass | Installed new tap sign slip emailed
MSA-DTWD | WA3339801 | Level 3, Staff Lunch room- Door lock is faulty | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-20 15:10:00 | Pass | service lock to level 36 staff lunch room
MSA-DTWD | WA3339844 | Lvl 2, B249 Corridor- Vinyl below water fountain is damaged | Perth Campus B1 | GMP-BR | Flooring | Vinyl (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 15:30:00 | Pass | Works are now completed and vinyl patch is installed
MSA-DTWD | WA3339856 | A block, ground level, AF18 - 3 phase power circut tripping out | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 10:15:00 | Pass | Attended site and signed in. Located main switchboard and found RWB9 tripping. Investigated to what area and what circuit powers. Found to be the air con isolator outside. Air con trips when turned on. Opened aircon unit to find and controls okay and clean. Opened isolator to find full of water. Replaced isolator. Tested air con works okay. Replace light switch in library. Tested all okay. Job complete
MSA-DTWD | WA3339864 | K Block, K20 (Common/Games room)- Broken window pane | Midland Campus | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-25 07:25:00 | Pass | Attended site, reglazed fixed panel in common room in5.38 clear laminated safety glass1 - 800 x 770
MSA-DTWD | WA3339993 | H block ground H04 outside North East corner Safety shower needs attention-see notes | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-06-04 13:11:00 | Fail | Replaced safety valve
MSA-DTWD | WA3340070 | Lunch Room- Glass sliding door unable to lock | Perth Campus B2 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-20 15:50:00 | Pass | repair and adjustment to sliding glass door lock
MSA-DTWD | WA3340129 | External Remove graffiti from signage on Connolly drive | Clarkson Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 1 | CLOSE | 20 May 2020 | 2020-05-21 17:00:00 | 2020-05-20 14:20:00 | Pass | REMOVAL OF GRAFFITI FROM EXTERNAL SIGNAGE ON CONNOLLY DRIVE
MSA-DTWD | WA3340237 | Block 6 ground Rear Carpentry and JoineryDamaged leach drain | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 20 May 2020 | 2020-05-21 17:00:00 | 2020-06-08 14:34:00 | Fail | Bricks and sand back in place
MSA-DTWD | WA3340257 | A block, level 1, A106 - Gas Chip fryer wont start in cafe | East Perth Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 20 May 2020 | 2020-05-21 17:00:00 | 2020-05-21 12:00:00 | Pass | Complete
MSA-DTWD | WA3340258 | Leaking taps in wet area | Armadale Campus - 40 Commerce Ave | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 20 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 15:40:00 | Pass | Various plumbing work in wet areas armadale
MSA-DTWD | WA3340274 | B Block, Room BG25- Suspended 15A WP Outlet. Switch is broken | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 12:30:00 | Pass | Repalced faulty outlets in B block as shown by site. Job completed
MSA-DTWD | WA3340301 | Buzzing noise coming from security light -see notes | Armadale Campus - 145 Jull Street | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 20 May 2020 | 2020-05-21 17:00:00 | 2020-06-03 09:00:00 | Fail | Replaced faulty time Located too many blown lamps on security lights
MSA-DTWD | WA3340310 | D Block, D37 Meat Trade – Damaged flexi hose to basin | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-21 16:05:00 | Pass | CAp cold line Insert tee in hot line and connect soap dispenser
MSA-MRWA | WA3340125 | level 7, Hallway near RM 7.45 - Switchmech in 4 gang face failed near room 745 | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 20 May 2020 | 2020-05-25 17:00:00 | 2020-05-26 13:22:00 | Fail | Attended site and replaced 4 faulty light switches. Checked and tested all now working.
MSA-DCA | WA3341097 | Chiller Plant Room- Chiller 2 re-occuring fault | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-P.05 - Plant Room | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-09-14 16:30:00 | Fail | Please refer to work logs and attached applicable contractor service reports.
MSA-DCA | WA3341251 | Roof leak above AC 9 | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 21 May 2020 | 2020-05-22 17:00:00 | 2020-05-22 14:30:00 | Pass | Water leaking above AC 9. Investigated. Water dripping from lagging on HW line. Removed all lagging from HW line following wet insulation. Located air bleed valves leaking. Isolated and removed. Supplied and installed two new air auto bleed valves on HW lines. Reinstalled insulation and lagging on HW lines.
MSA-DCA | WA3341352 | Door 23 is catching unable to automatically lock due to closing issues | State Theatre Centre (Heath Ledger Theatre)-Main Building-External Area-Courtyard - Entry and External Corridor | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 21 May 2020 | 2020-05-22 17:00:00 | 2020-05-22 09:35:00 | Pass | Carried out temp repair, will return to replace 2x RTS85Returned 22/5 Removed 2x doors from opening and replaced 2x side load drive arms as necessary, rehung and aligned doors.
MSA-DCA | WA3341356 | Seating- Wooden timber has spilt and needs repair on outdoor furnishing | Sunset Hospital Heritage Precinct-Building H-Catholic Church-Ground Floor | GMP-BR | Furniture | Outdoor Furniture (FU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 10:45:00 | Pass | Works are now completed and the battens secured
MSA-DCS | WA3340574 | unit 1, D wing, D5, personal lock - repair as not able to use the master key on it to unlock it, | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 21 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 11:00:00 | Pass | Replace hinges, lock & barrel
MSA-DCS | WA3340580 | Unit 4 - Lock sticking, the lock on the main entrance door to unit 4 is really hard to open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 21 May 2020 | 2020-05-25 17:00:00 | 2020-08-07 14:30:00 | Fail | Service lock, lock beyond repair, require new lock.Replace 4L42 lock, mounting tabs and fixings.
MSA-DCS | WA3340592 | WWTP relays not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 12:00:00 | Pass | Source parts , replace relays
MSA-DCS | WA3340593 | Chapel - Security flood light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 May 2020 | 2020-05-27 17:00:00 | 2020-05-22 08:30:00 | Pass | Investigate and repair Chapel flood light
MSA-DCS | WA3340601 | unit 2, top landing - end toilet keeps blocking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 14:00:00 | Pass | COMPLETED
MSA-DCS | WA3340631 | education 1, wood work tea prep room - kitchen cupboards,shelvs & drawers are unable to be used | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 21 May 2020 | 2020-05-25 17:00:00 | 2020-09-21 11:21:00 | Fail | BRAF EMAILED 01/09 - STILL NO APPROVALCLOSING OF JOB - COST TO DATEI SUGGEST YOU MAY WANT TO RE-ISSUE JOB AS A LVM...???
MSA-DCS | WA3340635 | ISU, C wing - x2 external lights not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 May 2020 | 2020-05-27 17:00:00 | 2020-05-28 13:00:00 | Fail | Repaired lights
MSA-DCS | WA3340670 | Prisoner clothing store/Urine room - Exterior building light not working | Boronia Pre-release-AK19 - Library, Education Personal Development | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 09:30:00 | Pass | Replace PE Cell
MSA-DCS | WA3340719 | Internal mircophonics 19 & 20 no activation | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 May 2020 | 2020-05-21 12:48:29 | 2020-06-03 18:00:00 | Fail | Replaced damaged mx cable Z19, calibrate and test. Job completed.
MSA-DCS | WA3340772 | Entry air lock - both doors are opening at the same time, closer to | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 21 May 2020 | 2020-05-22 09:14:29 | 2020-06-09 11:00:00 | Fail | Attend site with DOJ Locksmith to discuss requirements. Removed lock and checked wiring and reed switches. SEME required to install reed switch
MSA-DCS | WA3340775 | unit 5 bedroom 4.1 - BOS0 duress system no response | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 May 2020 | 2020-05-22 09:17:38 | 2020-05-21 11:15:00 | Pass | Unit 5 bedroom 4 receiver indicating missing error, found missing i information in programme, deleted point and reprogrammed and entered location on map, point cleared and communicated correctly when testing point in area. No further action required.
MSA-DCS | WA3340829 | Main Building, external, rear of main Kitchen - Fire hose needs repair (photo to follow in email) | Nyandi Training Academy | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-21 12:40:00 | Pass | FHR is being used for training and is being over stretched.
MSA-DCS | WA3340842 | Kkins shed emergency shower light broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 09:30:00 | Pass | Replace light
MSA-DCS | WA3340973 | Abattoir- electrical cable in slaughter floor is faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 10:00:00 | Pass | Investigate and repair cable in Abattoir
MSA-DCS | WA3340978 | Unit 14, A & C- Shower drain has a blockage | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-22 08:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3341037 | Kitchen, Veg Prep area - Hot water tap not turning off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 May 2020 | 2020-05-22 11:50:04 | 2020-05-21 13:25:00 | Pass | Turned off water to kitchen to replace top assembly and reseated tap
MSA-DCS | WA3341046 | Reception, laundry - dryer GPO broken | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 May 2020 | 2020-05-22 11:56:23 | 2020-05-21 15:06:00 | Pass | Replaced faulty gpo
MSA-DCS | WA3341082 | Unit 1, Cell B2- Toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 May 2020 | 2020-05-22 12:08:33 | 2020-05-21 15:30:00 | Pass | Blocked cell turned into blocked drains cleared hole line outside all unblocked
MSA-DCS | WA3341085 | Front Gate, Above Control- roof sheeting pulling away | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-07-31 14:30:00 | Fail | ROOF SHEETING REPAIRED/MADE NOT TO PULL AWAY
MSA-DCS | WA3341089 | Offical Visits, Prisoners toilet not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 May 2020 | 2020-05-22 12:12:57 | 2020-05-22 07:45:00 | Pass | Unblocked toilet and changed plugs on solinoid
MSA-DCS | WA3341127 | monitor room - investigate blind stop issue with camera 37 | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 May 2020 | 2020-05-22 12:37:06 | 2020-07-09 13:34:00 | Fail | Mounting bracket replaced via cherry picker and p readers set for zone activations, good image.
MSA-DCS | WA3341141 | Control room - Camera system crashed | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 May 2020 | 2020-05-22 12:48:46 | 2020-06-24 22:32:00 | Fail | Replaced hard drive with Seme stock,Configured new hard drive and tested Stratus server.
MSA-DCS | WA3341146 | skills w/s rcd to drill press faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 13:00:00 | Pass | Found damaged cable, repaired
MSA-DCS | WA3341152 | construction w/s power keeps tripping rcd | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 13:30:00 | Pass | Investigate and repair power circuit tripping
MSA-DCS | WA3341183 | Level 3 Kitchen lights flashing on tap - similar fault only fixed 2 weeks ago. | East Perth | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-22 15:30:00 | Pass | Complete
MSA-DCS | WA3341193 | #10 Unit 5.6 – Power Low. Medium High Priority - Error message In Entry pod. | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 May 2020 | 2020-05-22 13:17:09 | 2020-05-22 10:15:00 | Pass | Attended site and replaced new 12vdc 7ah battery in unit 5 house 6. Reset controller and retested house 6 alarms. Also checked and tested duress system and alarms for correct operation due to generator tests. All had reset,replaced and tested ok. Job complete
MSA-DCS | WA3341209 | Kitchen- Power has been cut that feeds fridge | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 21 May 2020 | 2020-05-21 17:33:21 | 2020-05-25 14:30:00 | Fail | Replaced damaged cool room supply
MSA-DCS | WA3341220 | Dairy water pipe leaking near storage tank | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-22 12:00:00 | Pass | COMPLETED
MSA-DCS | WA3341223 | Education 2, Class 3 - smashed door window approx 1050x650 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Door Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 14:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3341234 | Lvl 1- Toilet will not flush, button may be broken | East Perth | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-22 16:00:00 | Pass | Complete
MSA-DCS | WA3341263 | Family visits – Gallagher PC not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-06-24 22:35:00 | Fail | Installed new workstation and programmed Gallagher and Indigo.2x 27inch monitors from seme stock 2x wireless keyboard and mouse combo from seme stock 1x workstation from seme stock 2x HDMI to DP from seme stock
MSA-DCS | WA3341316 | Unit 4 office- hot urn tap faulty | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 21 May 2020 | 2020-05-22 15:07:40 | 2020-05-22 09:45:00 | Pass | Changed zip tap as required
MSA-DCS | WA3342845 | Level 3 Kitchen lights flashing on tap - similar fault only fixed 2 weeks ago. | East Perth | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 11:17:00 | Pass | Unit all working on arrivalChecked everything could not find a reason for the lights flashing pressure tested fittings, inspected hot and cold tanks, ok inspected all water lines, ok compressor very noisy but working.Compressor is noisy on start upUnit is 10 years old may require replacement - if compressor is failing
MSA-DFES | WA3341169 | Hot water is coming through the cold taps in various areas and also hot water in the toilet room 11 | CFRS Malaga | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 21 May 2020 | 2020-05-22 17:00:00 | 2020-06-02 15:30:00 | Fail | Return to site supplier gave the wrong size will return with proper fitting
MSA-DTAG | WA3340951 | Lvl 11, Registry- CCTV monitors on wall are showing no imagines for Lvl 10 | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 09:30:00 | Pass | Reset monitors to view Smart Wall on Level 11.
MSA-DTAG | WA3341136 | level 4, staff toilets (locked) - Male Staff toilet blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-22 16:30:00 | Pass | Complete
MSA-DTWD | WA3340652 | Fire panel. Battery is faulty | Clarkson Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 15:00:00 | Pass | Attended site to rectify fire panel fault/battery fault. Issue found to be detector faulty. Replaced detector and base
MSA-DTWD | WA3340676 | E block, South side, Loading dock area- Damaged ceiling 2 pieces like for like & paint to match | Joondalup Kendrew Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-06-09 10:15:00 | Fail | Remove old screwsMark ceiling joists locationMeasure cut sheet and mark fixing linesNotch sheet for sensor cableFit sheet and fix offFit sensorFill where screws had pulled throughPaint sheetClean up
MSA-DTWD | WA3340705 | A Block, Level 3 Opp A304 inner door Gas strut broken | East Perth Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 12:30:00 | Pass | Attend siteSign in get keysLooked for internal door opp A304Rang Steve MeyerConfirmed male toilet doorsDoors are slammingGet toolsClose access to toiletsAdjust and tweak door closing and latching speedsTest doors working and not slamming shutRefit covers pack up
MSA-DTWD | WA3340792 | Workshop - 2x padlocks are seized | Jandakot Campus - Hangar | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 08:15:00 | Pass | repairs to lock
MSA-DTWD | WA3340836 | A Block, AF20 courtyard side- 5x wooden window frames are damaged | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-06-08 14:30:00 | Fail | Works are now completed and please see the photos attached
MSA-DTWD | WA3340844 | Centre Block, C401 staffroom main entry- Door does not self latch | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-22 11:15:00 | Pass | Adjustment to strike and reposition door closer arm to allow door to latch freely. Also replaced faulty square back projection lock
MSA-DTWD | WA3340942 | E Block, E617 (male toilets)- Blocket toilet (3rd cubicle from door) | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 13:06:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3340986 | K Block, K02 Canteen kitchen)- Positive pilot light cannot be maintained (oven will not light) | Midland Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-28 12:00:00 | Fail | Works complete 12:00pm 28/5/2020 job # s42868
MSA-DTWD | WA3341025 | Block 8, Aboriginal Services classroom- Multiple lights out in track lighting | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-07-06 08:46:00 | Fail | Attended site and signed in. Located aboriginal classroom. Isolated track lighting and removed as required. Made safe cabling. Spoke with staff on site about holes and said not to worry about them. Job complete
MSA-DTWD | WA3341156 | A BLOCK, GRND, AF20 - Door handle on keypad lock faulty | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Locksmith (SE) | GRONBEK SECURITY | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 16:15:00 | Pass | Replaced Borg Digital Lock due to wear and tear.
MSA-DTWD | WA3341178 | Clasroom F- 5, Daiken reverse cycle A/C, indoor unit, swing vane mechanism grinding | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-06-12 13:00:00 | Fail | LOCATED ROOM F5 AND FOUND THAT DIRECTIONAL FAN LOUVRE MOTOR WAS GRINDING. CLASS IN ROOM AT PRESENT AND WAS TOLD THATTHE CLASS WAS EXITING AROUND 1200. REMOVED SPLIT FASCIA AND REMOVED PCB BOX. REMOVED MOTOR ASSEMBLY AND REMOVED FAULTY MOTOR AND INSTALLED NEW LOUVRE MOTOR. REMOVED OTHER MOTOR ASSEMBLY AND INSTALLED NEW LOUVRE MOTOR. REASSEMBLED UNIT AND TESTED OPERATION. LOUVRE MOTORS ARE NO LONGER GRINDING.
MSA-DTWD | WA3341181 | P block, P012 - aircon, The indoor fan in this unit is very noisy | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-07-10 15:40:00 | Fail | Picked up parts, accessed site ,isolated a.c. in p012 stripped head unit replaced motor & blower.rewired motor. Rebuilt head unit, reinstated power & tested ok
MSA-DTWD | WA3341206 | B Block, BG25.A- Leaking taps in wash bays | Carlisle Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 15:00:00 | Pass | Serviced leaking taps
MSA-DTWD | WA3341298 | Lvl 2 - Toilet tower, Ladies cubicle door lock broken | West One Services | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 15:30:00 | Pass | Attend siteGet access keyClose toilet down inspect lock indicator not working correctlyLeft site to get replacement partsReturned to siteClose accessRemove old lock and replaceClean upReturn keysSign out
MSA-DTWD | WA3341301 | F Block, Lights not working rear left area of Library | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-06-09 14:30:00 | Fail | Restored power to lights and replaced faulty lamps. All working properly job completed
MSA-DTWD | WA3341304 | Building 8, ground floor, rooms 8G45/46 - Leaf litter entering through ceiling slats | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 21 May 2020 | 2020-05-22 17:00:00 | 2020-05-30 10:00:00 | Fail | Works are now completed and ceiling is cleaned
MSA-DTWD | WA3341305 | Exterior North Block- Repair camera exterior North Block unable to view driveway | Balga Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 3 | CLOSE | 21 May 2020 | 2020-05-28 17:00:00 | 2020-06-03 10:12:00 | Fail | 02/06/2020, 230-245Checked footage of all north facing cameras.All carparks and driveway visible
MSA-DTWD | WA3341308 | Lvl 4 office, Tower Block- Venetion Blind broken | West One Services | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 1 | CLOSE | 21 May 2020 | 2020-05-22 17:00:00 | 2020-05-22 13:30:00 | Pass | Repairs to blinds
MSA-DTWD | WA3341312 | L Block workshop- Fan not working on top of the flamable liquid cupboard | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-06-02 13:30:00 | Fail | Turned on isolator on roof and tested the motor. All works ok. Job complete.
MSA-DTWD | WA3341323 | L Block- Broken light switch in the stonemasons | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 21 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 09:24:00 | Pass | Repalced firstly light switch and mounting block to L block .job completed
MSA-MRWA | WA3340808 | Administration entry, Front doors – not opening automatically, Alarm went off please remediate | Jandakot Depot | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 21 May 2020 | 2020-05-22 17:00:00 | 2020-05-21 11:00:00 | Pass | Found door working on arrival, reported by client that door was not opening when walking up from either side but could hear door clicking, checked over sensors, control boards and wiring and tested all ok, reset operator. Door is on time lock via security access and may have had intermittent fault and not unlocked door at correct time
MSA-DCA | WA3341887 | Tap by roller doors requires replacing and re-fixing to wall. | State Library of WA-Main Building-Ground Floor-GF15 - Van Dock | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 07:55:00 | Pass | Replaced leaking tap and adjusted pipework to suit
MSA-DCS | WA3341549 | Unit 13, front entrance - The page button for the front entrance intercom isnt audible at control | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 May 2020 | 2020-05-26 17:00:00 | 2020-05-22 13:15:00 | Pass | Replaced the master intercom with new, job completed.
MSA-DCS | WA3341575 | Jeelia, C1 - faulty light switch | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 May 2020 | 2020-05-26 17:00:00 | 2020-05-29 10:23:00 | Fail | Tested lights switches in c1
MSA-DCS | WA3341605 | unit 2 - top landing hand basin taps faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-28 17:00:00 | 2020-05-22 13:00:00 | Pass | COMPLETED
MSA-DCS | WA3341640 | Unit 3, Lunch room - Dripping tap, officers kitchen sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-28 17:00:00 | 2020-05-22 09:00:00 | Pass | Remove and replace 2x jumper valves in tap set.
MSA-DCS | WA3341641 | Unit 14, A wing, cell A13 - shower drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-28 17:00:00 | 2020-05-22 10:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.
MSA-DCS | WA3341644 | Unit 4, A11 - Water is leaking from copper pipe from wall to sink in cell. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-22 11:00:00 | Pass | Tighten up basin spout under basin in cell.
MSA-DCS | WA3341667 | unit 1, D10 - main light is flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-26 13:30:00 | Pass | Repaired in unit 1 d10
MSA-DCS | WA3341695 | Level 4, Deak W4.33 - light is flashing | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 09:30:00 | Pass | Replaced failed lamps and starters.
MSA-DCS | WA3341705 | Front Gate, key watcher- Key 44 wont release | Melaleuca Prison | GMP-BR- HO | Security | Keys & Access (SE) | AAA Ability Locksmiths | 1 | CLOSE | 22 May 2020 | 2020-05-23 08:31:03 | 2020-05-25 12:20:00 | Fail | Job completed - removed jammed key from key watcher
MSA-DCS | WA3341740 | Unit 7, E wing, dayroom - kitchen waste cracked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-22 11:50:00 | Pass | Removed old broken pipe work redid with new
MSA-DCS | WA3341750 | Reception - Inner auto door slow to open, Doors not commencing to open prior to people reaching door | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Main Reception Area | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-25 08:30:00 | Pass | Adjusted sensor and door opening time. test operation, all okay.
MSA-DCS | WA3341759 | Emergency Generator - ‘Set on Auto’ indicator panel light- lamp holder disintegrating | Boronia Pre-release | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-12 11:00:00 | Fail | Panel indicator lights replaced
MSA-DCS | WA3341781 | Unit 3, Cell B5- Toilet button missing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-30 12:00:00 | Fail | Removed old flush button. Installed new flush button assembly and tested. Parts ordered and collected offsite.
MSA-DCS | WA3341912 | Unit 4, Back Yard- Repair leak on main domestic inlet pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-19 09:00:00 | Fail | 10/6/20- Prepwork. Marked out and cut concrete.16/6/20- Issolated water. Removed concrete. Dug hole and exposed pipe. Tracked pipework to source of leak (2m away). Dug new hole and exposed pipework. Barricaded area off and turned water back on.17/6/20- Reexposed pipework. Isolated water. Repaired pipe. Tested. Backfilled all holes. Barricaded concrete hole, until dry day.9/6/20- Reinstated concrete and cleaned up area.
MSA-DCS | WA3341939 | Interview room 2, one light out and one flickering | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 10:15:00 | Pass | Replaced globes in light
MSA-DCS | WA3341999 | Murchison, B Wing- Oven not getting to temperature | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 10:00:00 | Pass | Repaired oven.
MSA-DCS | WA3342077 | Unit 2, B12 - prisoner lock tongue is jammed in | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-25 09:45:00 | Pass | Job completed - Replaced faulty mortice lock in Unit 2, B12 and realigned door level
MSA-DCS | WA3342081 | Unit 9, Cell A15- Sink needs refixing to wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 May 2020 | 2020-05-23 11:38:38 | 2020-05-22 16:00:00 | Pass | Removed and reinstalled basin
MSA-DCS | WA3342123 | SITE COST Perimeter Fence, zone 16 - alarm not flashing red fault | Melaleuca Prison | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 May 2020 | 2020-05-22 15:44:50 | 2020-05-22 15:00:00 | Pass | Travelled to site and investigated fault. Walk tested zone 16 and contacted control, found no activation from melaleuca control, reset perimeter workstation and re-armed zone. Checked all programming and functions. Walk tested zone 16 again and had technician monitoring software from comms room. All tested and working ok. Job complete
MSA-DCS | WA3342142 | Healthcare, staff area & CCU - door lock wont slam shut | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 22 May 2020 | 2020-05-23 11:54:15 | 2020-05-22 12:45:00 | Pass | Job completed - repair lock
MSA-DCS | WA3342218 | Unit 2, A & C Wing- Emergency Lights not working | Melaleuca Prison | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-06-05 10:30:00 | Fail | Investigate night lights not working. Found faulty contactor. Source replacement parts. Repair fault.
MSA-DCS | WA3342262 | ISU, D Wing- Cameras not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 May 2020 | 2020-05-23 12:10:28 | 2020-05-25 11:33:00 | Fail | Replaced 2 x lenses in ISU D wing cells D8 and D9 images are now good. N ok further action required.
MSA-DCS | WA3342380 | Unit 3 Control Panel cannot access all lights | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-07-20 12:00:00 | Fail | This job completed on job no WA3400260 - Replaced failed power supply
MSA-DCS | WA3342419 | Boilerhouse- 125mm Copper Pipe under chlorinator tank leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 May 2020 | 2020-05-23 12:27:57 | 2020-05-22 17:10:00 | Pass | Inspected leak in boiler room, had to pass job onto boilertronics
MSA-DCS | WA3342429 | Unit 4, H1 - external cell call faint, hard to hear | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-17 14:52:00 | Fail | Sourced parts 16/6/2020Removed faulty CI-CC, used existing face plate and replaced all components and tested, loud and clear two way communication
MSA-DCS | WA3342440 | Unit 1 - P/A faulty | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 12:42:00 | Pass | Replaced both Mics with redback mic from Site stock.Seme to replace site stock with CG-OH
MSA-DCS | WA3342444 | CCU, holding Cells - cell doors dropped jamming on frames | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-25 10:45:00 | Pass | Job completed - on site and adjust door CCU holding cell as required
MSA-DCS | WA3342460 | Kitchen - freezer broken light | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 10:00:00 | Pass | Replaced 4x LED lights
MSA-DCS | WA3342463 | Kitchen - rear door entry area broken light | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 12:00:00 | Pass | Replaced light with emergency led fitting
MSA-DCS | WA3342492 | Kitchen Baine Marie lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 15:00:00 | Pass | Repair lights
MSA-DCS | WA3342548 | Gym, retic main line is broken ,near path | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-06-08 14:00:00 | Fail | UTLISIED EXCAVATOR TO DIG OUT BREAK, REPAIRED PIPE AND FILLED IN.
MSA-DCS | WA3342589 | stores - Toilet and drain blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-25 13:15:00 | Pass | unblocked toilet
MSA-DCS | WA3342608 | Dairy- water leaking out of ground behind coolroom shed | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-29 13:30:00 | Pass | Job to be completed by others
MSA-DCS | WA3342666 | kitchen - Gas oven is damaged & requires removing & capping | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-02 08:45:00 | Fail | It was the flat grill not oven as stated.Disconnect Flat grill as instructed.
MSA-DCS | WA3342686 | Gatehouse, Entry Door- Glass sliding entry doors slow to open | Banksia Hill Detention Centre | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 13:00:00 | Pass | Attended site to investigate why door was not opening properly. Client explained that issue onlyseemed to happen in the afternoon, door was working fine whilst i was on site. I have reset doorand changed some settings on both the internal and external sensors, as door is working fine andi could see no clear or obvious faults i have asked client to monitor the door to see if issue returns.It sounds like the door may have been going into a safety mode for some reason but i was unableto figure out why, I think possibly the wind as we have had bad weather recently.
MSA-DCS | WA3342691 | Unit 4, D Wing shower block, sink - Hot water tap and S bend leaking on sink in D Wing shower block | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-25 11:00:00 | Pass | Tighten up spout and associated pipework. Realign tapware.
MSA-DCS | WA3342695 | Unit 5, D wing - 1 shower only getting hot | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-22 14:06:00 | Pass | Replace 5 split Pins in quarter turn spindles to showers in cleaning closet and test.
MSA-DCS | WA3342708 | Unit 3 cell 62 door lock cannot be locked. | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-25 14:10:00 | Pass | Replaced faulty Cell lock on Cell 62 Unit 3
MSA-DCS | WA3342718 | Staff Toilet outside unit 2- Toilet on right side leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-23 12:05:00 | Pass | pulled apart cistern and Installed new outlet washer
MSA-DCS | WA3342729 | Unit 4, B Wing- PA Speaker at end of wing constantly buzzing | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-25 11:00:00 | Pass | Rectified and adjust the amplifier due to unwanted sound coming out from speaker. Job completed
MSA-DCS | WA3342732 | Unit 1, Cell B10- toilet is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 May 2020 | 2020-05-23 14:34:30 | 2020-05-23 08:00:00 | Pass | Removed paper Unblocked toilet
MSA-DCS | WA3342754 | Bakery Workshop- Prover humidity currently 95 percent | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-04 12:00:00 | Fail | 22/05/2020Called as requested to the prover not working correctly. Found the solid stat relays faulty and require new. Also checked the mixer for the timer not working but found it was on the wrong setting made good all ok.04/06/2020Arrived at site with parts, remove old faulty parts, supply and replace, install, reassemble all components and test for correct function okay.
MSA-DCS | WA3342759 | Unit 6 Cell 16 stainless toilet is not working, not flushing, no water | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 May 2020 | 2020-05-23 14:53:08 | 2020-05-23 09:33:00 | Pass | Attended site after hours,Reconnected flush mechanism to cistern as required to restore function. Tested works on completion
MSA-DCS | WA3342769 | Stores - barrel of the lock on the above doors has become loose | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-25 13:10:00 | Pass | Replaced barrel in Stores lock
MSA-DCS | WA3342770 | Perimeter omnitrax - battery faults | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-17 14:51:00 | Fail | Sourced batteroes 16/6/2020Travelled to site 17/6/2020Replaced 3x 6v batteries and 1m fig 8 cable
MSA-DCS | WA3342772 | UPS fail in houses | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-24 18:00:00 | Pass | Upgraded the firmware on all 43 UPS across the site .
MSA-DCS | WA3342775 | Flyscreen door on Lecture room 2 is missing the lock, needs to be MKSO | Wooroloo Prison Farm-Education Program Centre | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-25 12:40:00 | Pass | Replaced Missing Lock on Security Screen Door Lecture room 2 / Education
MSA-DCS | WA3342776 | EC4 - microwave power supply fail | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-25 20:48:00 | Pass | RFI failed, replaced with Powerbox 13.8vdc from site stock.Programmed mains fail alarm and tested
MSA-DCS | WA3342778 | Perimeter main gate read switch failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-24 22:43:00 | Fail | Replaced 2x heavy duty reed switches from seme stock
MSA-DCS | WA3342781 | Gate, x-ray machine not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 12:43:00 | Pass | Reset X-ray machine. Monitor had failed replaced with site stock.Seme to replace site stock with 27"monitor with HDMI lead
MSA-DCS | WA3342787 | Unit 7, Cell E24- Toilet main flushing rod broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 May 2020 | 2020-05-23 15:13:18 | 2020-05-23 09:05:00 | Pass | Replaced washer valve and o ring
MSA-DCS | WA3342793 | Officers toilet,Staff toilet adjacent to canteen east- Toilet is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 May 2020 | 2020-05-23 15:16:10 | 2020-05-23 10:08:00 | Pass | Removed paper and unblocked toilet
MSA-DCS | WA3342794 | Orientation, Prisoner toilet adjacent to cog skills blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 May 2020 | 2020-05-23 15:18:24 | 2020-05-23 11:10:00 | Pass | Removed paper and unblocked toilet
MSA-DCS | WA3342814 | Control room - PTZ 5 is out of focus | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 22 May 2020 | 2020-05-23 15:42:29 | 2020-05-22 17:30:00 | Pass | Job completed - all working ok for a short while then picture went purple and then restored. Camera needsreplacing.
MSA-DCS | WA3342852 | Unit 3 - D Wing - Sliding door grill stuck open - electronic failure | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 May 2020 | 2020-05-22 21:06:50 | 2020-05-22 20:00:00 | Pass | Check and test the gallagher systems, working ok its mechanical issue and not our scope of work.
MSA-DFES | WA3341920 | Station officer ensuite - Blocked toilet | CFRS Claremont | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 22 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 12:15:00 | Pass | Investigate blocked toilet at Claremont Firestation in ensuite roomplunge blocked toilet multiple times to clear blockage, flush and paper test once clearedPack up and clean up worksite
MSA-DFES | WA3342041 | Admin Building, Superintendent office- Air Con is faulty, see further notes below | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 22 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 14:00:00 | Pass | Attend site. Investigate AC 15 not working. Check fault codes and found to be A1 indoor printed circuit board abnormalities. Found unit to have stopped after power failure the previous day. Access roof and power cycle unit. Found unit to reset and turn back on. Run unit on heating and cooling, unit now woring as normal. Fault caused by power issues in building.
MSA-DFES | WA3342043 | Admin Building, Secretary office- Air Con is faulty, see further notes below | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 22 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 14:00:00 | Pass | Attend site. Investigate AC 16 not working. Check fault codes and found to be A1 indoor printed circuit board abnormalities. Found unit to have stopped after power failure the previous day. Access roof and power cycle unit. Found unit to reset and turn back on. Run unit on heating and cooling, unit now woring as normal. Fault caused by power issues in building.
MSA-DFES | WA3342710 | Generator - to check fuel load | DFES Regional Office - Belmont | GMP-BR | Mechanical Services | Pumps (MS) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 22 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 10:30:00 | Pass | Check generator fuel level and adjust temps and schedule
MSA-DFES | WA3342798 | Applied Training Ground- Water valve, bottom dam has a minor leak | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-29 09:00:00 | Pass | repair leak on water isolation valve near bottom dam .re packed stuffing box on 25 valve for safety shower
MSA-DTAG | WA3341725 | staff kitchen 204 - no pwer on right side wall | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 22 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 07:45:00 | Pass | Cooler/boilling unit tripping circuit in kitchen(204)
MSA-DTAG | WA3341728 | Lift 1 is not responding – stuck on level 3 | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 22 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 10:21:00 | Pass | job completed - Door drive malfunction Lost parameters Copied From other lift and put back into service If it happens again recommendreplacing door drive Lift running
MSA-DTAG | WA3341800 | Lvl 2, Sheriff’s Office- Air flow problem throughout the whole floor area | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-06-17 09:00:00 | Fail | Actuators replaced & Air survey completed.
MSA-DTAG | WA3342705 | Level 6, Lift Lobby- PRB - There is a light flickering in the lift lobby that needs attending to. | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-25 13:33:00 | Pass | Repalced faulty fluros and starters to lift level 6 lobby. Parts supplied by site. Job completed
MSA-DTAG | WA3342739 | Ground floor, staff meals area - Skirting has detached from wall in main staff kitchen | Central Law Courts | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-23 11:00:00 | Pass | skirting re attached
MSA-DTAG | WA3342811 | Bio Clean Cell 4 | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Cleaning (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 0 | CLOSE | 22 May 2020 | 2020-05-22 19:43:49 | 2020-05-22 18:00:00 | Pass | Job carried out as per work order
MSA-DTWD | WA3341643 | North Block, Room N117- Cockroach infestation | Mount Lawley Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 3 | CLOSE | 22 May 2020 | 2020-05-28 17:00:00 | 2020-05-26 12:00:00 | Pass | Applied gel to doorways, windows and cupboards. Sprayed bottom cupboard.
MSA-DTWD | WA3341713 | Building 6, ground floor, VBB projrct store - Remove damaged lights and make safe | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-25 01:00:00 | Pass | Attended site and removed damaged light and made safe. Was going to install new lights but roof still leaking. Site advised to close off work order and will return with new work order once roof is being repaired.
MSA-DTWD | WA3341715 | F10 male toilet, RH cubicle -- Behind wall toilet cistern broken | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 16:55:00 | Pass | Replace broken toilet cistern with dual flush
MSA-DTWD | WA3341741 | Lvl 4, Room 406- Door break glass is damaged | Perth Campus B2 | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-25 11:00:00 | Pass | Cut in size 100x100 2mm thick glass but door release is damaged and needs to be replaced. advised to close job.
MSA-DTWD | WA3341749 | B Block, Metal fab W/shop- Blocked floor drain from wash troughs | Rockingham Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 16:02:00 | Pass | Badly blocked drain required extensive work with machine to unblock
MSA-DTWD | WA3341773 | Stainless flexi hose on Tank Quick-Fill Valve has a couple of holes in it so is spraying water out. | Carlisle Campus | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Firesafe Service & Maintenance Pty Ltd | 1 | CLOSE | 22 May 2020 | 2020-05-25 17:00:00 | 2020-05-22 14:00:00 | Pass | DescriptionRECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro TAFE - Carlisle Campus, Bank Street, Carlisle WASite contact: Glen PearsonWork Order Number: WA3341773Call out Date: 22/05/2020Target finish: 25/05/2020Original information: Stainless flexi hose on Tank Quick-Fill Valve has a couple of holes in it so is spraying water out.F block, Fire Pump Compound (external)Please attend today as worried leaks may get worse over the weekendAttended siteDate:22/05/20Start Time:1200Finish Time: 1400Techs on Site: 1Works Carried Out:-Isolated valve-Removed leaking braided hose- Replaced with new oneMaterials and Equipment Used:1 braided hose water connector 600 mm longSystem Status on Departure: NormalRecommendations or Comments: -Possible cause over a period of time the hot sun heats the braided hose perishingthe inner hose.The above mentioned works have been carried out as arranged and the system was left operational and in goodworki
MSA-DTWD | WA3341908 | Block 6- Painting & Decorating wet area- Multiple lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-07-13 10:30:00 | Fail | Attended site and signed in. Installed 4 x lights over mesh floor to existing circuit. Tested all okay. Job complete
MSA-DTWD | WA3341946 | D Block Fitting w/shop -Faulty door lock Room D23; | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 10:00:00 | Pass | repairs to lock
MSA-DTWD | WA3342680 | Room B11 Electrical - Faulty double batten light fitting, replace with LED please | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 12:00:00 | Pass | Attended site and signed in. Located B11. Found faulty light. Removed and replaced with new LED batten. Upon isolating in switchboard found door handle jammed and not unlocking. Removed mechanism and reinstalled correctly. Tested all okay. Job complete
MSA-DTWD | WA3342697 | Lvl 3, Room A356- Lights blown | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 May 2020 | 2020-05-29 17:00:00 | 2020-05-26 11:17:00 | Pass | Repalced multiple lamps to area as requested by site. Job complete d
MSA-DTWD | WA3342847 | Block 8 Plant room 1 Rat activity on the roof | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 22 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 11:00:00 | Pass | Renewed bait to existing stations in plant room areas and garden beds surrounding block 8. Added baited stations to roof area of block 8, to be added to list of existing units and rebaited at scheduled services. Recommend a follow up to check activity and renew baits as needed in 2 - 3 weeks due to evidence of big population / high activity,
MSA-DCS | WA3342894 | Casuarina Prison main unit 3 D wing grills are not working | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 23 May 2020 | 2020-05-23 12:41:59 | 2020-05-23 10:55:00 | Pass | Inspect Unit 3 D wing grill. Loose. Neutral cable in terminal block. Re-terminate. Test operation, all okay.
MSA-DCS | WA3342897 | SITE COST Unit -1 Control room -Cameras are frozen | Melaleuca Prison | WSM-BR-SITE | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 May 2020 | 2020-05-23 12:58:36 | 2020-12-01 16:17:00 | Fail | Installed new workstation as per quote.Tested OKJob Complete
MSA-DCS | WA3342904 | Unit1 wing1 cell 6 cell call B red light is On unable to communicate from the cell to control room | Roebourne Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 May 2020 | 2020-05-23 17:59:49 | 2020-06-24 12:30:00 | Fail | Job complete
MSA-DCS | WA3342909 | SITE COST Video interview room 1 camera is not working | Broome Regional Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 May 2020 | 2020-05-23 18:24:21 | 2020-07-17 08:45:00 | Fail | Removed roof sheets to access camera cable run.Found lizard has been living in roof and evidence of cable damage.5 cameras in close proximity, installed 5x 20m cat6 cable from seme stock. Left spare cable in roof space above cameras. Installed Indigo BX420 and programmed.Removed redundant cables.
MSA-DCS | WA3342958 | Hakea B woman's prison - sally port metal door not locking | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 23 May 2020 | 2020-05-23 17:20:52 | 2020-05-25 11:15:00 | Fail | Attended site after hours 23/05/2020. Key found to be faulty - no other keys available to test/operate lock. Return visit required.On site 25/05/2020. Inspected and serviced lock on gate to sallyport.
MSA-DCS | WA3342967 | unit14 Fire alarm keeps going off | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 0 | CLOSE | 23 May 2020 | 2020-05-23 17:43:53 | 2020-05-23 16:00:00 | Pass | 23/05/20 GACausarina prison unit 14Wing b/d cells 15&16 vesda in alarm and fault and unable to reset. Investigated and found alarms cleared from vesda after resetting as smokehad dissipated, inmates smoking in cells have caused the alarm. Minor high airflow on pipe 3 foundRaw flow okay and pipe continuous, cleared fault and left vesda and fip at unit 14 in normal operation.
MSA-DCS | WA3343000 | PDA is offline M desk in prison ward | West Kimberley Regional Prison-External Area | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 May 2020 | 2020-05-24 01:24:27 | 2020-05-23 18:30:00 | Pass | Removed faulty UPS from the EDUCATION BLOCK. Installed new brackets to accommodate the new UPS. Swapped over network card to new UPS. Load tested ok. Site stock APC UPS
MSA-DCS | WA3343385 | PTZ1 camera - Vision is puple/pinky. It's not clear. | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | Sapio Pty Ltd | 1 | CLOSE | 24 May 2020 | 2020-05-25 09:57:37 | 2020-05-24 11:50:00 | Pass | Job completed - found camera OK on arrival
MSA-DCS | WA3343431 | Hakea-Melaleuca Prison- in U 2- fire alarm is contunioously beeping- no fire in it | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 May 2020 | 2020-05-25 13:48:39 | 2020-05-24 15:48:00 | Pass | 24/05/20GAMelaleuca prisonAttended site due to fire alarm in unit 12 and unable to reset. Checked fip at unit 12 found vesda a/c wing 13&14 in alarm/ fault. Reset alarmand cleared normal. Cleaned out all sampling points to clear airflow fault and left normal. Sampling points had been blocked.
MSA-DCS | WA3343437 | Unit 14- Fire panel fault. | Casuarina Prison-Prisoner Accommodation Unit 14 | GMP-BR- HO | Fire Protection Services | Fire Protection - Fire Brigade (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 24 May 2020 | 2020-05-24 18:47:11 | 2020-05-24 17:46:00 | Pass | 24/5/20 GACasuarina prison unit 14Attended site vesda wing b/d 3&4 and 9&10 in minor low airflow faults cleared blocked sampling points on both vesdas to clear both faults.Left system normal.Inmates smoking in cells will continue to set off Vesda systems
MSA-DCS | WA3343443 | Hakea-Melaleuca Prison - Inner gate infront of the Sallyport is stuck half open. | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 0 | CLOSE | 24 May 2020 | 2020-05-24 19:51:34 | 2020-05-24 17:15:00 | Pass | Sunday 24/05/20Recalibrate limit switches and controller
MSA-DCS | WA3359025 | ** Retrospective work order **Fire alarm activated | Riverbank | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 24 May 2020 | 2020-05-24 18:00:00 | 2020-05-24 17:25:00 | Pass | 24/05/20&25/05/20Riverbank prison GAAttended site due to fault on code red call through from grant. Went to Burswood programmes office to pick up keys and then attended site.Fault on fip due to main fail fault as power outage to area. Advised grant I will return tommorow to check that power was reinstated and faultcleared.25/05/20Reattended site and found power had reinstated and fault cleared. Cleared code red and left normal
MSA-DFES | WA3348846 | RETROSPECTIVE WORK ORDER DO NOT ATTEND-NO PERSONS FOUND ONSITE | VFRS Mandurah | GMP-BR | Security | Guards (SE) | Securex Security Systems & Services | 1 | CLOSE | 24 May 2020 | 2020-05-25 17:00:00 | 2020-05-24 10:53:00 | Pass | BYPASS ON ZN 24 MRS APP BAY 2 FRONT DOOREXTERNAL CHECK CARRIED OUT. ALL APPEARS SECURE. NO OFFENCE DETECTED. NO PERSONS FOUND ONSITE. EXTREMELY WINDY ONSITE. MONITORING ADVISED - BEN
MSA-DCA | WA3344408 | All BMS remote connection is offline for all buildings at the site. | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Collection area 12 - General Collection Room within Vault | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-28 14:00:00 | Fail | Re-attended site 28-5-20 1230 with Schneider. Carried out applicable tests and checks to BMS control system, applicable automation server and modem. Checked operation of remote connection and applicable fault monitoring (ok). Checked BMS control strategy and operation of CRC mechanical services equipment (ok). Works completed. Left site 28-5-20 1400
MSA-DCA | WA3344429 | L1 Terrestrial Vertebrates Laboratory Temp and RH sensor failure-see notes | Collection and Research Centre Welshpool-Harry Butler Centre | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-28 16:30:00 | Fail | Please refer to work logs.
MSA-DCA | WA3344597 | one of the large glass facia windows has a large crack, held together with tape | Perth Concert Hall-External Area-Ground Floor | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-06-19 11:56:00 | Fail | ATTENDED SITE TO MEASURE & ASSESSSECURED 2 CRACKED PANELS WITH SECURITY FILMRETURNED LATER DATE WITH 5 MEN TO REGLAZE 2 PANELS10MM CLEAR TOUGHENED SAFETY GLASS1-2438 X 18251-2438 X 1820POLISHED EDGES AND 2 SIDE CUT OUTS IN EACH PANEL7 TUBES OF SILICONE USEDRETURNED LATER DATE TO SUPPLY & FIT TINT FILM TO BOTH PANELS
MSA-DCA | WA3344688 | Blocked box gutter | State Theatre Centre (Heath Ledger Theatre)-Main Building-External Area-Courtyard - Entry and External Corridor | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 13:30:00 | Pass | Cleared debris from box gutter and downpipes - Both are now clear and flowing
MSA-DCS | WA3343537 | Unit 3 C12 Cell call making loud buzzing sound | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 25 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 09:15:00 | Pass | Replaced damaged and faulty cell call unit. Job completed.
MSA-DCS | WA3343616 | Unit 4 control room Water leaking through Air Con in ceiling | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 May 2020 | 2020-05-27 17:00:00 | 2020-06-19 13:08:00 | Fail | REPAIRED PREVIOUS LEAK DAMAGE AFTER SOMEONE WALKED ON IT WHEN THEY SHOULDNT.
MSA-DCS | WA3343624 | Unit 2 corridor to unit 2 Extractor fan not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 10:30:00 | Pass | Replaced ex fan
MSA-DCS | WA3343641 | Unit 5 Control room Vesda constantly beeping, even when reset. | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 May 2020 | 2020-05-26 07:19:06 | 2020-05-25 15:00:00 | Pass | Cleaned
MSA-DCS | WA3343680 | Jeelia C4 power socket broken | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 May 2020 | 2020-05-27 17:00:00 | 2020-05-29 11:30:00 | Fail | Replaced damaged gpo
MSA-DCS | WA3343685 | unit 2 walkway roof panels ripped off by storm | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Schlager Construction Group | 1 | CLOSE | 25 May 2020 | 2020-05-26 07:44:08 | 2020-10-27 08:30:00 | Fail | Attended site and made safe damaged sheeting.Quoted replacing all polycarbonate roof sheeting.
MSA-DCS | WA3343697 | control/monitor Intermittent communication issue with door controller to Mtce W/shop-see notes | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 25 May 2020 | 2020-05-27 17:00:00 | 2020-06-03 12:15:00 | Fail | Attended site and checked all Gallagher logs for the last week. All logs tested ok and no alarms activated over the last week. Job complete
MSA-DCS | WA3343710 | Monitor/Control Room-Cam 36 not moving when alarm activated & unable to move with joy stick | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 May 2020 | 2020-05-26 07:58:01 | 2020-06-03 12:45:00 | Fail | Attended site and checked recording playback for the past 8 days. All recording checked ok, checked PTZ functions and alarm activations for correct movement, all tested and working ok. Camera working ok on spare indigo encoder card with no issues. Job complete
MSA-DCS | WA3343748 | Unit 14 - A & C-blocked shower drain and leaking sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-25 14:00:00 | Pass | Remove grate, remove hair, Moflo, rinse, plunge, reinstall grate and test.Remove and replace 1x quarter turn spindle.
MSA-DCS | WA3343757 | Uit 13 - D Wing Cell D10 - toilet bowl leaking from area and smells, shower drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-06-09 13:00:00 | Fail | Removed damaged pan. Installed new pan, tested and removed rubbish.
MSA-DCS | WA3343775 | Unit 2, has no power | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 25 May 2020 | 2020-05-25 12:30:37 | 2020-05-25 16:00:00 | Fail | Replaced damaged overhead cable and attachments
MSA-DCS | WA3343803 | Unit 3 A wing gas heater not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-06-09 14:00:00 | Fail | Repair gas wall furnace. Make adjustments to balanced flue. All working perfectly.
MSA-DCS | WA3343821 | Unit 14 - A & C Low water pressure in cell C3 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-25 15:00:00 | Pass | Remove blocked restrictor and install one quarter turn valve and adjust the flow.
MSA-DCS | WA3343825 | Control room - omnitrax 1inch cable fault | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 May 2020 | 2020-05-25 16:42:44 | 2020-05-27 14:19:00 | Fail | Investigated perimeter faults after lightning storm, repaired multiple faults and tested all perimeter detection and calibration - OK.Job Complete
MSA-DCS | WA3343850 | unit 3, B wing - first ceiling loight nog working on B wing landing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-27 15:00:00 | Pass | Repaired multiple faulty lights in unit 3 b wing
MSA-DCS | WA3343851 | Unit 2 - A & C A/C oven electrical fault, when turned on blue flash of electric | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 25 May 2020 | 2020-05-26 08:44:57 | 2020-05-25 15:30:00 | Pass | Fitted new connectors to wire and tested ok.
MSA-DCS | WA3343895 | Unit 1, A&C - cell power keeps on tripping out and cant be resest. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-26 10:30:00 | Pass | Repaired damaged gpos in AC wings.
MSA-DCS | WA3343966 | Medical unit -Sluice room roof leaking from rain | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-06-12 13:08:00 | Fail | located leak and rectified
MSA-DCS | WA3343986 | unit 4, D13 - Hatch missing needs replacing | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-06-08 11:45:00 | Fail | RE FIXED VIEWING HATCH
MSA-DCS | WA3344016 | Unit 5 - B4 - The toilet is leaking into the toilet bowl constantly,-see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-25 12:00:00 | Pass | Replace Inlet valve in toilet cistern
MSA-DCS | WA3344026 | camera's (CCTV) in cells U1 3.08 & 3.09 and Maxi Yard Dayroom-see notes | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 May 2020 | 2020-05-26 09:25:48 | 2020-05-25 14:00:00 | Pass | Contacted site and advised that issue was related to power outage. Had site reset camera system and all reset and tested ok. Job complete
MSA-DCS | WA3344144 | Unit 1, Cell Call system is not working correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 May 2020 | 2020-05-25 17:55:56 | 2020-05-25 15:00:00 | Pass | Rectified and fixed the cell call functions from unit 1, job completed.
MSA-DCS | WA3344156 | Gascoyne laundry dryer lint trap broken-see notes | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-06-16 10:30:00 | Fail | AMS627531 WA3344156 - Wandoo - Gascoyne laundry dryer lint trap broken-see notes Additional Notes: Dryer out at stores12/6 - Remove Dryer to Workshop16/6 - Dismantle Dryer, supply & fit new lint filter housing & drive belt. Assemble & test, return to site.
MSA-DCS | WA3344170 | Motion sensor entry zone 1 has been activated | Riverbank-Riverbank Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 May 2020 | 2020-05-26 10:08:09 | 2020-05-25 14:13:00 | Pass | Checked area clear, PIR sensor entry zone 1active, found front entrance door swinging, bolted 1 door closed and added alloy plate to latch other door. Area secure. Alarm restored
MSA-DCS | WA3344187 | Unit 5, Cell B1- Reading light on bottom bunk not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-27 11:30:00 | Pass | Repaired faulty lights in unit 5 b1
MSA-DCS | WA3344192 | Gatehouse,Control room- security internal perimiter cabinet rusted/leaking water & causing damage/G4 | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-06-04 09:00:00 | Fail | Replaced failed (corroded) Cabinet on Perimeter. Removed control equipment from leaking cabinets, drilled cable entry points in new cabinet and fixed to pole. Reinstalled cable and equipment, terminated and tested.
MSA-DCS | WA3344200 | Gate house, perimeter fence - camera faulty/blurred Zone B2 PT 4 | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-07-07 13:00:00 | Fail | Attended site.Found contamination on internal glass - cleaned and sealed housing.Adjusted settings on camera.Tested.All ok at departure
MSA-DCS | WA3344206 | Level 4 - Install two touch screens for lighting control | Westralia Square | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-06-05 15:30:00 | Fail | Replaced failed lighting touch screens with new.
MSA-DCS | WA3344217 | Kitchen sea container breaker faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 13:00:00 | Pass | Replace circuit breaker
MSA-DCS | WA3344220 | Administration, Lobby Area - Camera 113 faulty (path way to lobby) | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-12-16 11:30:00 | Fail | Camera bracket and housing replaced camera reinstalled tested ok.
MSA-DCS | WA3344225 | WWTP PH probe not working | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2021-06-08 12:01:00 | Fail | Arrived on site to sign in at security, hand over phone and complete JHA and take 5.Met with client and discussed service.Checked alarm history - no alarms.Inspected process - plant is still running very well with a good quality final effluent.Checked all pumps and actuators - all pumps and actuator valves were working.Checked clarifier - clarifier is in good condition.Checked chlorine levels - checked chlorine levels with handheld meter due to chlorine probe being faulty. Chlorineprobe requires replacing still.Checked media filters - backwashed media filter and checked settings which were all good.Checked flow meters - treated effluent meter blocks up and reads incorrectly, instructed client to clean weekly.Checked DO sensor - DO levels were okay approx 1.6 mg/l.Checked chemical levels - all chemical levels were sufficient.Checked dosing pumps and non returns - all pumps were healthy and no returns and lines were good.Checked pH probe - new pH probe has been installed cor
MSA-DCS | WA3344229 | Skills w/s - lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 11:30:00 | Pass | Repair lights in Skills W/S
MSA-DCS | WA3344257 | external remove tree that has fallen over | Wandoo Rehabilitation Facility | GMP-BR- HO | Landscaping & Gardening | Tree Lopping (LG) | KENNEDY'S TREE SERVICES | 1 | CLOSE | 25 May 2020 | 2020-05-26 10:52:34 | 2020-05-28 08:45:00 | Fail | Work completed
MSA-DCS | WA3344286 | Unit 14, D wing, Cell D13- Cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-27 10:00:00 | Pass | Repaired faulty lights in unit 14 d13
MSA-DCS | WA3344303 | Murchinson A04 light switch broken | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 09:00:00 | Pass | Repaired light switch
MSA-DCS | WA3344325 | Control Room - Cell Call computer is very slow | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-06-19 12:55:00 | Fail | Investigated cell call computer fault, disassembled and tested hardware, optimised software, cleaned operating system, rearranged files and tested OKJob Complete
MSA-DCS | WA3344330 | Control Room - A1 & A2 infra red beam in constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 May 2020 | 2020-05-25 15:18:59 | 2020-05-25 16:00:00 | Fail | Attended site checked and found A1&A2 inferred beam were in constant alarm. Checked on field found a lot of weeds along the footpath. Clear most of the weeds along the footpath. Tested alarm activated and reset correctly. Advised customer to arrange weed cleaning in the area.
MSA-DCS | WA3344374 | Reception/Key Issues- carpet squares need replacing as they are damaged | Banksia Hill Detention Centre | SPA-GR | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-07-04 14:30:00 | Fail | DAMAGED CARPET SQUARES REPLACED
MSA-DCS | WA3344378 | Unit 1, B13 - GPO Faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 25 May 2020 | 2020-05-26 11:29:46 | 2020-05-25 12:30:00 | Pass | Replaced gpos
MSA-DCS | WA3344409 | Unit 7, E24 - Light hanging from ceiling | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 14:00:00 | Pass | New light
MSA-DCS | WA3344436 | Unit 7, Cell E18- Light not working new ballast required | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 15:00:00 | Pass | Repaired light
MSA-DCS | WA3344450 | SITE COST Behind Kitchen - Broken hot water pipe in ground | Bandyup Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 25 May 2020 | 2020-05-25 16:02:49 | 2020-06-08 15:34:00 | Fail | Attended site,Removed existing asphalt and excavate to expose burst 32mm hot water line.Isolate water line and cut out burst section. Supply and install 1m of new copper with sockets and crimp to complete repair. Tested works on completion. Backfill and supply and install new asphalt to complete repairs.
MSA-DCS | WA3344492 | Abattoir- No power supply to hockcutter | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 15:00:00 | Pass | Replaced damaged light causing circuit to trip
MSA-DCS | WA3344504 | Unit 5, House 8- roof leak, water coming in through light fitting | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-07-24 13:21:00 | Fail | REPLACE FLASHING AND SHEETING
MSA-DCS | WA3344508 | Unit 5, House 6- 600x600 hot plate glass is smashed | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 25 May 2020 | 2020-05-26 12:23:14 | 2020-06-10 14:00:00 | Fail | Replaced cooktop
MSA-DCS | WA3344527 | S O P - Court Yard Three sets of lights are out over the garden door,-see notes | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-26 09:00:00 | Pass | Repaired faulty lights in SOP courtyard
MSA-DCS | WA3344545 | JJT Conference Room - 2x ceiling lights are not working | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-29 11:30:00 | Fail | Replaced failed light fittings after sourcing replacement parts.
MSA-DCS | WA3344552 | Video link - roof water leak in various cells | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 25 May 2020 | 2020-05-26 12:47:34 | 2020-06-19 13:11:00 | Fail | REPAIR/SEALED WINDOW ABOVE MAIN HOLD ROOM AND OPPOSITE WALL
MSA-DCS | WA3344619 | A tree branch has landed on house 22 Driscoll Drive | DCS - 22 Driscoll Drive Canning Vale | GMP-BR- HO | Landscaping & Gardening | General Tree Works (LG) | KENNEDY'S TREE SERVICES | 1 | CLOSE | 25 May 2020 | 2020-05-26 13:21:28 | 2020-05-26 11:30:00 | Pass | Work completed
MSA-DCS | WA3344659 | Zone 16 electric fence wire snapped | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-25 20:50:00 | Pass | Replaced 70m 0f Gallagher electric fence wire and tightened loose wires
MSA-DCS | WA3344660 | Tearoom, Front Door 1- Lock is not self closing | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-26 08:30:00 | Pass | Adjusted door closer.
MSA-DCS | WA3344679 | Kitchen, tearoom - Urns not boiling | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-26 13:05:00 | Pass | On arrival unit working correctly. Ran through multiple tests and unit operated as it should
MSA-DCS | WA3344715 | Unit 9, A wing Grille - The tongue has broken off the latch in the lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 25 May 2020 | 2020-05-25 18:14:53 | 2020-06-03 11:00:00 | Fail | Supplied and installed new custom built 4L42 lock.
MSA-DCS | WA3344725 | Unit 5 - B Wing B Wing Grill will not operate from Control panel. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 12:00:00 | Pass | 29/05/2020 Reassessed operation of Grill. Grill continues to operate correctly, staff advise no problems over last two days.
MSA-DCS | WA3344728 | Administration building - faulty aircon (see notes) | Hakea Prison | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 25 May 2020 | 2020-05-26 14:24:58 | 2020-05-26 08:27:00 | Pass | No fault present. Set point was set for previous workers in office. Raised setpoint to match workera preference and to accommodate for changing season. All ok at time of departure.
MSA-DCS | WA3344778 | Jasper, A wing, Kitchen - sink tap leaking form under bench | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 16:10:00 | Pass | Replaced kitchen set
MSA-DCS | WA3344807 | Unit 3, D Wing, Vinyl flooring is lifting end of wing | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-09-08 13:54:00 | Fail | replace damaged flooring
MSA-DCS | WA3344995 | Water leaking heavily outside front gate on lawn coming from ground - unknown source | Hakea Prison-Main Gatehouse | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 May 2020 | 2020-05-26 22:50:27 | 2020-05-26 02:45:00 | Pass | Burst retic pipe.Advised client to get retic guys in.
MSA-DFES | WA3343635 | Check all air con due to power outage and re supply desel fuel tank | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 25 May 2020 | 2020-05-25 17:00:00 | 2020-05-27 10:00:00 | Fail | Attend site. Building power out and generator running. Monitor plant operation. Found crac units in alarm. Access server rooms and found alarm to be warning only of condenser water flow loss. Crac units in data and comcen server rooms working as normal. Check chilled water system and found chiller 1 in fault. Found fault to be low line voltage. Reset chiller and found to start and run as normal. Monitor diesel bulk tank in carpark and found to be full. Continue to monitor tank and transfer pump operation. Found diesel tranfer pump 1 to start and pump diesel up to generator day tank. Bulk tank is now 3/4 full. Arrange for tanker to attend site and top up bulk tank. Continue monitoring mechanical plant. Tanker arrived and filled tank with 250ltrs. Power has returned and dropped out a number of times throughout the day. Power has now been reinstated and on for a couple of hours. Access server rooms and reset condenser water flow loss alarm. Chiller required another low line voltage lockou
MSA-DFES | WA3343740 | front side of station gate has blown off the hinges and brick work broken | CFRS Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-06-04 15:00:00 | Fail | Make safe & Repairs for gate
MSA-DFES | WA3343919 | north western side, external door, stair 2 - handle lock mechanism not working – faulty | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 11:25:00 | Pass | replace broken handles and service to electronic lock
MSA-DFES | WA3343926 | Light pole down in top carpark cnr of leak & durban street, just needs to be isolated | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 13:15:00 | Pass | Made cable safe and removed damaged light pole
MSA-DFES | WA3343984 | Reception fire panel battery is going flat may need to replaced | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 10:45:00 | Pass | Tech attended site due to P1 call out.
MSA-DFES | WA3344179 | Accommodation corridor- External door closer not operating correctly, | CFRS Rockingham | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 15:45:00 | Pass | Works are now completed and the closer is functioning correctly
MSA-DFES | WA3344211 | FOBS and intercom button do not open the gates | CFRS Canning Vale | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 12:40:00 | Pass | 25/5/20 - Dylan ParslowInvestigated issues with gate control.Gallagher hardware appears to be faulty.Advised that authorised technician that installed, needs to look at this system.
MSA-DFES | WA3344460 | Check UPS afyter power failure | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 11:40:00 | Pass | Complete
MSA-DFES | WA3344513 | Fire panel - batteries are not charging off generator, after power failure | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 13:30:00 | Pass | Tech attended site due to power failure.
MSA-DFES | WA3344549 | Heritage shed ground Damage caused to front guttering caused by storms-see notes | FESA RHQ - Forrestfield | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-06-09 10:30:00 | Fail | BRAF has been submitted for approval- Install replacement gutter
MSA-DFES | WA3344571 | 2nd floor, office - water leak | DFES Cockburn Emergency Services Complex | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-27 09:00:00 | Fail | Works are now completed and we have had confirmation that the repair does not leak
MSA-DFES | WA3344588 | FOBS and intercom button do not open the gates | CFRS Canning Vale | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-06-10 14:22:00 | Fail | 25/05/2020, 235-335Arrived onsite and found the Gallagher controller offline to software.Rebooted Controller. Replaced old batteries.Controller still will not connect to Software.Manually tested input and relay functions.Controller is completely non responsive. Needs to be replaced.As temp fixBypassed controller,. Gate is operating correctly via Intercom and Keypad.Gate does not operate via timed open/ close or via Airkey remotes (Fobs)09/06/2020, 900-1200Replaced Gallagher 6000 controllerReplaced Software licence file.Reprogrammed controller.Tested gate, operational via remote airkeys (fobs), intercom, keypad and via timer.All ok.
MSA-DFES | WA3344664 | main admin Bad stench in TFFS Instructor cadre office,-see notes | FESA RHQ - Forrestfield | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 12:00:00 | Pass | Roof void / above suspended ceiling TFFS Instructor cadre office. Lifted panels (suspended ceiling) and searched for dead rodent, could not find a carcass. Placed 2x deodoriser bags in roof void.
MSA-DFES | WA3348058 | RETROSPECTIVE WORK ORDER DO NOT ATTEND-Cleared by ops | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 25 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 00:15:00 | Pass | ZONE 41 MRS ENTRY 2 DOORNO STAFF ON SITE , SITE APPEARS SAFE AND SECURE ON DEPARTURE , CLEARED BY OPS
MSA-DTAG | WA3343758 | main switch board strong electrical smell | Mandurah Courthouse | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 16:45:00 | Pass | Replaced burnt out fuse holder and fuse due to loose connection.
MSA-DTAG | WA3343901 | Lvl 3, JSO, Off the main walkway halfway up the office- Light blown | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-25 14:32:00 | Pass | Repalced faulty lamps to LVL3 JSO office. Parts supplied by site. Job completed
MSA-DTAG | WA3343921 | Lvl 10, Kitchen- Kitchen tap is leaking | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-26 12:00:00 | Pass | Complete
MSA-DTAG | WA3343989 | Water leaking through light fitting in upstairs magistrates area. | Rockingham Justice Complex | GMP-BR-HO | Roofing | Tiled Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-06-22 10:06:00 | Fail | Realigned tiles
MSA-DTAG | WA3344025 | Ground Water cooler near main entrance is leaking | Rockingham Justice Complex | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-26 09:51:00 | Pass | Leak reported. Ran unit for 10mins and then left under pressure of 10 mins. No leak from internal/external or fromFdrainage visible. No signs of leak internally. Check compressor operation and all working ok. Thermostat operating correctly. All ok
MSA-DTAG | WA3344247 | Lvl 3- Hose reel drum has a small water leak, cupboard next to lift 1 | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 08:30:00 | Pass | Investigate fire hose reel leak, feed hose to drum connection corroded and clamp loose. Cleaned up connection and repair, supply and install new hose clamp. Test unit, no leaks.
MSA-DTAG | WA3344327 | ground cell 4 Person in custody today with flu like symptoms, -see notes | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 23:30:00 | Pass | WA3344327 completed as pert work order
MSA-DTAG | WA3344489 | Custody - CCTV Screen in security office is not functioning | Armadale Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 13:30:00 | Pass | 25/5/20 - Dean Simpson, Joshua ParkReset tv screen in the security office.All tested ok.No call out fee as already onsite.
MSA-DTAG | WA3344499 | Lvl 4, Plant Room- ACU 2 belts are slipping | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-07-03 15:00:00 | Fail | Replace pulleys and v belts
MSA-DTAG | WA3344573 | Court Regisry entry and exist door to outside public grounds glass in door smashed-see notes | Joondalup Courthouse | GMP-BR-HO | Building | Doors (BU) | O'Brien Glass With Care | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 15:27:00 | Pass | Supply & Install Solar Film First Panel
MSA-DTAG | WA3344780 | L11 kitchen Clicking sound and no water-see notes | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 10:30:00 | Pass | Complete
MSA-DTWD | WA3343630 | T block both lifts not working | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 25 May 2020 | 2020-05-25 17:00:00 | 2020-05-25 15:39:00 | Pass | Reset lifts after power spike
MSA-DTWD | WA3343725 | C Block Student services has no power | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 14:30:00 | Pass | Attended site and signed in. Located tripped lights. Located faulty ballast due to water leak. Informed site and replaced ballast. All now working
MSA-DTWD | WA3343942 | S Block, Room S206, Library- Light not working | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-26 14:48:00 | Pass | Attend site. Replaced faulty fluros in library . Also replaced 4x faulty light fittings in corridor in front of lift. Inspected lights not working around admin corridor. Forums to be faulty switch. Replaced . All working properly job completed
MSA-DTWD | WA3343965 | F Block, Library & toilets- 2x roof leaks | Balga Campus | GMP-BR | Roofing | Tiled Roofing (RF) | AWB Co. | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-07-20 15:45:00 | Fail | Sourced leaks - Found BRAF will be needed as box guttering needs replacing in front of the male toilets. Will need to return to repair library box gutter when dry as seals lifted and rust was evident beneath.Sourced materials and returned to site, had to dress sections of flashing to patched rusted gutter, also resealed joints on gutter and on flashing of other leak. Will need to return again to complete fix of male toilet leak. Removed and replaced box gutter - picked up materials and refitted all flashings, installed new fixings to flashings and sheets, sealed all splits in sheets
MSA-DTWD | WA3343979 | A Block, A126 training services- lights blown | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-28 12:15:00 | Pass | Replaced multiple lamps throughout building as shown by site. Job completed
MSA-DTWD | WA3344039 | H Block, HG06- roof leak | Mandurah Campus (formerly Peel) | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-07-02 13:30:00 | Fail | Attended site and assessed leak from below- unable to access roof due to inclement weather. Will need to return when weather permits to resolve.-Measured up for materials for BRAF preparation -Attended site to carry out repairs- installed dry pan and flashing around A/C unit -Site confirmed leak has been resolved
MSA-DTWD | WA3344044 | S block Library - wet carpet, water needs extraction | Balga Campus | GMP-BR | Cleaning | Cleaning (CL) | Workzone Pty Ltd | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 15:00:00 | Pass | Remove water from carpet in Library and shampoo
MSA-DTWD | WA3344045 | ground Water leak in Vehicle Body Building Project store. | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-06-17 13:00:00 | Fail | Attended site and identified leak from below. Unable to access roof to assess from above due to inclement weather. Will need to return when weather permits to assess from the roof 11/6 BRAF has been submitted and we are waiting for approval to proceed with the repair works 17/6 Fitted flashings and new aircon band to extractor fan. Job completed
MSA-DTWD | WA3344115 | Block 6 Carpentry and Joinery Water leak on mezzanine floor above classroom. | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-26 14:30:00 | Pass | Works are complete. Will need to wait for next rain to confirm repairs have been successful
MSA-DTWD | WA3344177 | Main front foyer door randomly opening. door keeps opening/closing on it's own | Kwinana Automotive Centre | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-25 12:58:00 | Pass | On inspection, found doors actuating due to heavy weather conditions.Adjusted sensitivity as required, tested and adjusted, all ok.
MSA-DTWD | WA3344208 | Block 1 - West end passage way doors- Door closers allowing doors to bang in wind | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-07-14 12:35:00 | Fail | Attended site and adjusted door closer to maximum setting, door is still banging. Will need to investigate further.
MSA-DTWD | WA3344351 | B Block, External door glass panel smashed | Mount Lawley Campus | GMP-BR | Glazing | Door Glass (GL) | ACTION GLASS & ALUMINIUM | 0 | CLOSE | 25 May 2020 | 2020-05-25 15:21:48 | 2020-05-25 14:10:00 | Pass | ATTENDED SITEREGLAZED BROKEN DOOR PANEL6.38 CLEAR LAMINATED SAFETY GLASS1-1040 X 876
MSA-DTWD | WA3344372 | T block student lunch room HWS hardly any water coming out | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-26 11:00:00 | Pass | Feed pipe from unit toTap completelyBlocked with scale. Cleared scale and now working ok
MSA-DTWD | WA3344538 | L1 office entry Back-up battery failure during power cut | Perth Campus B5 | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 3 | CLOSE | 25 May 2020 | 2020-06-02 17:00:00 | 2020-05-28 07:55:00 | Pass | 26/05/2020, 812 - 840Replaced battery for Campus B5 residence building
MSA-DTWD | WA3344683 | Gilmore Incident ID: IR40464: "Front Foyer door fault" | Kwinana Automotive Centre | GMP-BR | Building | Automatic Doors (BU) | BJ SYSTEMS | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 10:00:00 | Pass | Investigate main entry autodoor fault. Check physical connections at autodoor head PCB for access control integration and off site programming at Gallagher workstation located at Rockingham TAFE. All seems ok at access control side. Dorma have been on site yesterday to turn sensitivity down for exterior sensor. Door should be monitored over the next week or so
MSA-DTWD | WA3344773 | tower block L4 west seal leaking windows | West One Services | GMP-BR | Building | Windows (BU) | AWB Co. | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-06-18 17:00:00 | Fail | Investigated tower block Level 4 west side windows. Spoke with debbie who informed us a glazier had attended. No obvious roofing issue or leaks.Silicone sealed all windows shut and around the glass and frames from the inside on the West wing facing the city as windows on other levels that have been done before
MSA-DTWD | WA3344792 | Tower block, level 4 west, Office - repair / replace venetian blinds | West One Services | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 1 | CLOSE | 25 May 2020 | 2020-05-26 17:00:00 | 2020-05-28 12:30:00 | Fail | Repairs to blinds
MSA-MRWA | WA3344261 | Ground floor gardens - One broken sprinkler riser between NDM facility and FWD shed requires repair | Materials Engineering Branch | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 2 | CLOSE | 25 May 2020 | 2020-05-28 17:00:00 | 2020-05-25 16:15:00 | Pass | Call Out & Labour & Supply Gear Drive Sprinkler
MSA-DCA | WA3347935 | Boardwalk Damage to board walk from storms-see notes | Maritime Museum Victoria Quay-Main Building-External Area | GMP-BR | Building | Foundations (BU) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 26 May 2020 | 2020-05-26 14:01:14 | 2020-05-26 16:00:00 | Fail | Have installed temporary fencing to make safe. Have been asked by PFM to close off work order and prepare a quote
MSA-DCA | WA3348330 | Lift 2 issues with doors | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 15:30:00 | Pass | Lift 2 Art-Geared :Found rope break tripped, reset and tested ,couldn't duplicate fault left lift running
MSA-DCA | WA3348416 | foyer Auto revolving door in fault-see notes | Maritime Museum Victoria Quay-Main Building | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 18:00:00 | Pass | Attended site to investigate why door was not working and electric lock was not engaged. Keypadstill had power but was shown an unknown error code of 00. I went to the control box and foundthe evac cables to have come out of the terminal block, i reconnected these and tidied them upbest i could, i powered up again and door began working as should. I have tested operation andensured lock was engaging before leaving site. I expect door had gone into manual mode due tothe safety evac cables being disconnected.
MSA-DCS | WA3345309 | Unit 10 water leaking in everywhere, coming from ceilings, flooding the cells | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 26 May 2020 | 2020-05-26 04:43:20 | 2020-05-26 14:35:00 | Fail | Repaired leaking pipe in th e ceiling of u10
MSA-DCS | WA3347535 | Can't reboot the perimeter cameras, can't reset the cowel zone 4 | Karnet Prison Farm | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 May 2020 | 2020-05-26 09:34:40 | 2020-05-26 11:10:00 | Fail | Returned all systems to normal status, found CCTV system logged in as wrong user, systems now fully operational, checked and confirmed zone zone operational. All ok.
MSA-DCS | WA3347544 | Albany Regional Prison-Gatehouse - External delta 2 PE beam fault | Albany Regional Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-02 17:00:00 | 2020-06-08 16:00:00 | Fail | Fault not with D2 but the next zone along which is E1. Transmitter beam set full of ants. Sprayed ants and cleaned the sensors. Cleared alarm on Cardax PC. Repaired tamper. Zone tested ok.
MSA-DCS | WA3347579 | Reticulation pipe broken near round about at front gatehouse flooding driveway. | Hakea Prison | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 1 | CLOSE | 26 May 2020 | 2020-05-27 07:12:42 | 2020-05-28 10:30:00 | Fail | MAIN LINE BREAK, DUG UP AND FIXED.
MSA-DCS | WA3347582 | Unit 7, Cell E4- Tap is faulty & broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 May 2020 | 2020-05-27 07:16:41 | 2020-05-26 15:38:00 | Pass | Replaced broken pillar tap
MSA-DCS | WA3347628 | Kitchen- Large kettle not working | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 26 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 10:00:00 | Pass | Kitchen Large Kettle faulty. Check kettle & controls. Top up jacket water level. Recreate vacuum. Run temperature, test. All working correctly.
MSA-DCS | WA3347634 | Unit 6, A Wing Dayroom- Water ingress into A wing dayroom light fittings next to fridge | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 26 May 2020 | 2020-05-27 07:52:48 | 2020-07-22 11:46:00 | Fail | REPAIRED ROOF SHEETING AND FLASHING - SEALED
MSA-DCS | WA3347642 | Zone 25 internal mircophonics in constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 May 2020 | 2020-05-26 11:55:49 | 2020-05-26 12:00:00 | Fail | Rectified and fixed the damage and corroded connections. Job completed
MSA-DCS | WA3347668 | Unit 8, C & D Regi Light- ballast is damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-27 12:00:00 | Pass | Repaired light
MSA-DCS | WA3347705 | Kitchen- Bakery lights going on & off | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-26 15:30:00 | Pass | Replaced 4x led batten lights
MSA-DCS | WA3347708 | Unit 2a Kitchen- Oven fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-29 10:30:00 | Pass | Replaced oven fan
MSA-DCS | WA3347711 | Infirmary - Door handle and lock on treatment room needs repair | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-27 10:00:00 | Pass | Repaired handles and lubricate lock
MSA-DCS | WA3347719 | SHU(9)- Computer room window not closing. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-07-03 14:30:00 | Fail | NEW SPIRAL BALANCES/ FEET FITTED
MSA-DCS | WA3347738 | Unit 3, B & D Wing- bottom windows at end of landing will not close | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-09-15 14:30:00 | Fail | NEW HARDWARE FITTED- WINDOWS NOW FULLY OPERATIONAL
MSA-DCS | WA3347741 | Rear Of Front Gate Black Plastic Cover For Sensor Post Broken | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 May 2020 | 2020-05-27 08:34:29 | 2020-07-03 11:15:00 | Fail | Removed intact cover from redundant beam set at the front of the gatehouse. Cut the cover to size and cleaned. Cleaned and checked alignment of all beams in the stack at the rear of the gatehouse. Installed cover on beam stack. All beams tested ok. Removed redundant beam stack. Removed beam stack taken to PFM stores.
MSA-DCS | WA3347742 | S O P, Cell A2- Personal lock faulty when using officer key. Cannot open. | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-07-22 13:00:00 | Fail | Temp. repair lock.Replace lock and barrels.
MSA-DCS | WA3347784 | unit 1 D wing shower only cold water coming out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-27 08:00:00 | Pass | Replace missing split pin in spindle in plumbing duct and test.
MSA-DCS | WA3347788 | Amenities/Bookings- Air Con is faulty | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 11:20:00 | Pass | Checked over aircond found no faults, found set point at 20.5 degrees, adjusted to 22 degrees, unit started up in heating mode.
MSA-DCS | WA3347824 | Observation tower 4 Repair toilet and water feed to tower to enable use | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 May 2020 | 2020-05-27 09:16:20 | 2020-05-26 17:28:00 | Pass | Investigated water issue at the tower 4. No water to the fixtures in tower4. Dug up where the isolation valve is but not sure whether the valve is charged. Unable to find other isolation valves. Nobody on site to give us the permission to shut the water off.
MSA-DCS | WA3347853 | Fault with gatehouse interlock | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-07-24 11:00:00 | Fail | Attended site and replaced 2 x airlock doors with new 9mm reed switches and magnets. All realigned and tested door function with correct alignment, no issues found with new reed switches and interlocking between door. Parts used 2 x 9mm reed switchesSundriesJob complete
MSA-DCS | WA3347903 | BR-east side of the gate house IR beam 1 cover missing or storm damaged | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-27 11:30:00 | Pass | IR beam cover damage , for replacement. Job to be completed through WA3347741.
MSA-DCS | WA3347920 | Lenard, C Wing- Broken lower sash window Approx 600mm x 500mm | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-26 12:15:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3347951 | E3 outer fence- Voltage issue on battery test | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 09:30:00 | Pass | Installed replacement battery, confirmed battery charging.
MSA-DCS | WA3347962 | Gate House - x ray machine faulty at front gate entrance/not operating | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-29 10:00:00 | Pass | Unable to reproduce Fault. Observed for 3 days. No issues raised by officers running machine.
MSA-DCS | WA3347966 | INF (10) - Lobby Area-repair transition strips pretruding/trip hazard/INF kitchen & laundry passage | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-10 11:30:00 | Fail | NEW TRANSITION STRIPS FITTED
MSA-DCS | WA3348051 | rear entry house- roof leak in sun room | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-09-04 14:14:00 | Fail | REPAIR TO ROOF AS PER ROY'S INSTRUCTIONS
MSA-DCS | WA3348078 | Unit 6 A17 Light switch hanging off wall | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 May 2020 | 2020-05-27 11:30:22 | 2020-05-26 15:00:00 | Pass | Replaced light switch
MSA-DCS | WA3348084 | Urquhart, D Wing- circulation pump 1 not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 16:50:00 | Pass | replaced faulty pump
MSA-DCS | WA3348124 | L4 W4.71 flickering light | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 10:30:00 | Pass | Replaced failed lamps and starters.
MSA-DCS | WA3348156 | Bakery - Workshop THE BAKERY WORKSHOP FLOORING HAS POT HOLES ETC. | Casuarina Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-12-15 10:00:00 | Fail | REPAIRS TO POT HOLES MADE
MSA-DCS | WA3348162 | S O P - Room 10 Toilet flush button Cell HA10 is not working. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-27 09:00:00 | Pass | Realign push button assembly in cistern in plumbing duct and test.
MSA-DCS | WA3348175 | S O P - Room 10 toilet duct cupboard between cell HA9 and HA10 is wet and smelling damp | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-27 12:00:00 | Pass | Remove cistern inlet valve blank plug and replace rubber seal.
MSA-DCS | WA3348193 | gate house 3x fire extinguishers been used 2x dry chem and 1x carb dioxide | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Portable Fire Equipment (Extinguishers/Blankets) (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 07:43:00 | Pass | Replaced extinguishers as requested
MSA-DCS | WA3348195 | gate house fire panel is not audible and looks like someone may have turned it off | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 14:10:00 | Pass | Found loose connection on buzzer repaired and tested ok.
MSA-DCS | WA3348201 | Sallyport inner gate has dropped, cannot open or close | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 26 May 2020 | 2020-05-26 16:48:00 | 2020-05-26 15:00:00 | Pass | 26/05/20Raise internal sally port gate
MSA-DCS | WA3348206 | Diary- 2x flood lights blown | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 15:00:00 | Pass | Repair Dairy floodlights
MSA-DCS | WA3348226 | Security Area - Security Office download footage for security/cell call | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 15:30:00 | Pass | Supplied CCTV and audio data related to two incidents as requested.
MSA-DCS | WA3348235 | Laundry, Number 1 Wash Machine (IPSO)- Showing steam problem | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 26 May 2020 | 2020-05-27 13:02:16 | 2020-05-27 09:45:00 | Pass | HAKEA - AMS628692 WA3348235 - WM#1 - Steam ErrorInspect and test washing machine, trace fault to a crack in the rear drum liner. Clean liner of grime build up and silicone treat the crack.Staff to advise of any further issues.
MSA-DCS | WA3348241 | Gardens, office - Leak in roof above light | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-08-05 11:21:00 | Fail | REPAIRED RUSTED SECTION AND REPLACED, WATERPROOFED.
MSA-DCS | WA3348244 | Main Roof Opposite Gardens Office- Flashing pulled away from roof | Hakea Prison | GMP-BR- HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-09-04 14:17:00 | Fail | Repaired Flashing
MSA-DCS | WA3348250 | Unit 5, Lunch Room/Tea Room- Light is broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-27 13:00:00 | Pass | Repaired damaged lunch room lights in unit 5
MSA-DCS | WA3348268 | PDA main unit is not responsing | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 May 2020 | 2020-05-27 13:21:44 | 2020-05-26 15:30:00 | Pass | Replaced the corroded and damage bosch receiver, job completed.
MSA-DCS | WA3348287 | 7x PDA need to be reprogrammed | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 May 2020 | 2020-05-27 12:47:53 | 2020-05-26 17:00:00 | Pass | Reprogrammed 8 existing personal duress alarms (183,185,186,187,188,189,190,191) and added 2 new (182,184) on MDAS system.Conducted test.All ok at departure
MSA-DCS | WA3348323 | Music Room - Gas heater not operating correctly | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-11 13:00:00 | Fail | Reconnect sensor adjust gas pressure
MSA-DCS | WA3348334 | Boiler House- Boiler number 2 is not starting up | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-26 15:00:00 | Pass | Like with Boilertronics in the boiler house from the crypt switching boilers on the BMS.
MSA-DCS | WA3348350 | Diary - power point broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-29 09:00:00 | Pass | Replace broken power point and switch
MSA-DCS | WA3348365 | Zones MWH 3, 5, and 20 not responding-SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-07-28 23:14:00 | Fail | Sourced custom made brackets and sundries.removed faulty MPS 4100 and installed Ultrawave.programmed and tested activation with control. confirmed correct operation
MSA-DCS | WA3348373 | Admin plant room door showing open when closed | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-06-24 09:30:00 | Fail | WA3348373Removed and replaced faulty reed switches and magnets. Replaced small section of corroded cabling between the 2 reed switches. Parts used:2 x heavy duty reed switches and magnets from SEME stockConsumables
MSA-DCS | WA3348376 | Spiritual centre UPS failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-26 20:00:00 | Pass | Removed faulty UPS. Installed new brackets to accommodate the new UPS. Swapped over the network card to the new UPS. Load tested ok. Parts used:APC UPS (SEME site stock)
MSA-DCS | WA3348378 | Unit 5 UPS low run time-SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-26 22:00:00 | Pass | Removed faulty UPS. Installed new brackets to accommodate the new UPS. Swapped over the network card to the new UPS. Load tested ok. Parts used:APC UPS (SEME site stock)
MSA-DCS | WA3348379 | Court services cameras faulty SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-26 18:00:00 | Pass | Intermittent poor, shaking image on cameras 59, 60, 61 and 62. One half of the receiver modem tested faulty. Removed and replaced modem. Cameras 55 - 62 on the 8 channel modem tested ok. Parts used:S708VR-RST (site stock)
MSA-DCS | WA3348381 | ICF monitors failed-SEME on site | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-06-25 15:00:00 | Fail | Replaced ICF workstation. Setup to run Indigo and Cardax. Tested ok.
MSA-DCS | WA3348397 | unit 1 B18, B31, B7, B2, taps all damaged may need to be replaced | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-05 11:00:00 | Fail | Attended site,Serviced taps to cell 18 & 31 including new washers and reseating. Service failed to taps in cell 2 & 7, replacement required. Returned to site, supplied and installed new pillar taps and flexi hoses to cell 2 & 7 as required. Tested all works on completion
MSA-DCS | WA3348399 | unit 1 A wing A2 and A6 damaged taps may need replacing | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-10 11:40:00 | Fail | COMPLETED
MSA-DCS | WA3348403 | unit 2 C and D wing D2, C10 and C1 taps damaged may need to be replaced | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-07-28 13:00:00 | Fail | COMPLETED
MSA-DCS | WA3348405 | Unit 2 Awing showers lights not working water proof | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-04 08:00:00 | Fail | Replaced 2x 18w tubes and starters
MSA-DCS | WA3348408 | unit 2 verandah lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-07-01 08:30:00 | Fail | Replaced various light fittings
MSA-DCS | WA3348411 | unit 5 external area all wall lights in limestone walls not working near stairs | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-04 11:00:00 | Fail | Replaced 9 external wall lights
MSA-DCS | WA3348413 | unit 1 B wing water running out of the wall near control ablusions out of pipe | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-10 12:40:00 | Fail | COMPLETED
MSA-DCS | WA3348451 | kitchen main water coming through light fitting from ceiling | Bandyup Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 26 May 2020 | 2020-05-26 20:03:41 | 2020-06-22 13:13:00 | Fail | GYP ROCKED HOLE TO CEILING AND PAINTED
MSA-DCS | WA3348459 | perimeter fence zone 5 unable to activate during fence check | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 May 2020 | 2020-05-27 16:12:11 | 2020-05-27 10:30:00 | Pass | Travelled to site and replaced end of line resistor for zone 5 and reset main intelliflex controller . All replaced and reset ok. Job complete
MSA-DCS | WA3348461 | kitchen main water coming through light fitting from ceiling | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 26 May 2020 | 2020-05-26 20:17:53 | 2020-05-26 18:20:00 | Pass | Attended site after hours,Locate burst hour water Pointe in roof space of kitchen,Supply and install 1m of 20mm copper and 2 joiners to repair. Tested works on completion
MSA-DCS | WA3348500 | Fire panel fault - Unit 1 Pod 9 corridor smoke | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 07:46:00 | Pass | Unit 1 pod 9 detector 7060 in maintenance fault located and fitted new detector and reset ok
MSA-DCS | WA3385634 | Boom gate fault with control box for boom gate | Pardelup Prison Farm | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 3 | CLOSE | 26 May 2020 | 2020-06-02 17:00:00 | 2020-05-27 16:30:00 | Pass | Additional two hours labour on site to assess further issues with Compound Boom gate.
MSA-DFES | WA3347988 | L1 alfresco 2x Skylight Perspex sheetings dropped and broken - see notes | CFRS Kiara | GMP-BR | Roofing | Rooflights and Skylights (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-06-26 12:54:00 | Fail | Access issues and materials supply will require a BRAF - preparation in hand - Replaced 2 x diffuser panels @ height
MSA-DFES | WA3348096 | ground room 37 Cement fibre sheeting in alfresco area is sagging, screws have pulled through | CFRS Ellen Brook | GMP-BR | Building | External Walls (BU) | AWB Co. | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-11 13:00:00 | Fail | Secure sheeting of ceiling in alfresco area - extra fixings where needed. Patch all holes old and new - Ceiling will need repaintPrepared and painted fibre cement sheeting in alfresco as quoted.
MSA-DFES | WA3348099 | Zipboil unit dispense button is damaged | CFRS Ellen Brook | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 11:30:00 | Pass | Replaced tap and cleared vent tube
MSA-DFES | WA3348371 | G, Block 8- Downstair sink is blocked | CFRS Fremantle | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 10:15:00 | Pass | Cleared blockage Behind station to clear gully plunged and cleared
MSA-DTAG | WA3347652 | Court 3 Building- Card reader faulty, no light & emitting a squeal | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 26 May 2020 | 2020-05-26 17:00:00 | 2020-05-26 09:45:00 | Pass | 26/5/20 - Dean Simpson, Joshua ParkReset card reader at court 3.Tested all working ok.
MSA-DTAG | WA3347660 | Front door is stuck open. Not closing | Perth Children's Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-26 17:38:00 | Pass | Requires ixio moving to the outside and activation sensor moving to the inside so threshold detection does not see post box on door leaf. Sensor will also need to be set to critical environment. Ixio will deem a mounting bracketReturned later that day - Moved outer sensor to inside and ixio to outside on mounting bracket attempted set up and found threshold safety ratchet not adjusting. Replaced sensor and tested all ok at time of test. Have made site aware of repairs from old sensor from outside.Due to door being under warranty, there is no charge for this call out so no claim will be submitted
MSA-DTAG | WA3347686 | Lights in magistrates garage not working | Rockingham Justice Complex | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 09:45:00 | Pass | Fault found to be circuit breaker feeding timer had tripped,reset breaker and timer settings, tested, all in working order
MSA-DTAG | WA3347796 | kitchen No hot or cold water coming out of billi unit | International House-Main Building-Level 17 | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-28 16:20:00 | Fail | Replaced cracked hex slotted brass flare nut on Billi Quadra A401889874 (not a stocked part that we yet used before part had to come from East as WA Manufacturer does not stock them in WA
MSA-DTAG | WA3348003 | Lvl 2A, Filing Corridor- light not working | Central Law Courts | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-29 11:15:00 | Pass | Job complete
MSA-DTAG | WA3348005 | Lvl 4,Adult Community Corrections Hallway (Hay St end)- Light globe blown | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-06-03 08:00:00 | Pass | Job complete
MSA-DTAG | WA3348116 | court 33 Air-conditioning does not appear to be working | Central Law Courts-Main Building-Level 3 | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-29 08:00:00 | Fail | Return to site and check court 33 temps sfter adjustment was made. Found court temp to be 22 degrees. Ac system is woring as normal.
MSA-DTAG | WA3348290 | Lvl 12, Staff Kitchen/passageway- skirting coming away from wall | Central Law Courts | GMP-BR-HO | Carpentry | Joinery (CA) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-06-02 09:15:00 | Pass | skirting re attached
MSA-DTWD | WA3347575 | A Block, Room A354a- Faulty Billi Quadra hot/cold water tap | Leederville Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 26 May 2020 | 2020-05-26 17:00:00 | 2020-06-02 13:30:00 | Fail | Repairs are over koi so required approval 2/6/20 Replaced faulty Billi tap and faulty front PcB board. Unit was still causing faults, hot pump not working, lvl sensor errors etc etc. also need to replace main PCB board. Additional works approved by Steve Meyer
MSA-DTWD | WA3347682 | C Block, Room CG37- Water build up in ceiling which is cracking | Mandurah Campus (formerly Peel) | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-06-23 15:00:00 | Fail | Sealed up roof leaks and removed leaves from valley. Removed and replaced water damaged ceiling tiles. Job complete.
MSA-DTWD | WA3347713 | Teaching block - Class room 2 has leaking roof | Clarkson Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 14:15:00 | Pass | Inspected ceiling void during shower/ nothing apparent. Consistent heavy rain would probably reveal more, also ductwork over area /sealed side flashing and tightened loose screws over areaSolar panel installed poorly, causing leaks
MSA-DTWD | WA3347826 | H Block, Room HG06- Power issues in office | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-06-09 13:15:00 | Fail | Attended site and signed in. Replaced damage e stop. All now working.
MSA-DTWD | WA3347835 | Tower Block west side at roof level & below patio roof damage and if there are any safety issues | West One Services | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 08:30:00 | Pass | Attended site and removed fallen debris. Small dents on verandah roof sheet. No major damage or works needed. Difficult area to access to replace hardiflex sheets (photos attached) removed all waste.
MSA-DTWD | WA3347859 | Room U66A, ablutions service duct- Faulty door lock | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 10:30:00 | Pass | repairs to locks
MSA-DTWD | WA3347878 | main variable speed drive has tripped out on overload and has not reset. | Murdoch Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-26 12:15:00 | Pass | Technician reset lighting protection equipment and test operation of VSD and pumps, all work well
MSA-DTWD | WA3347926 | Block 8 gardeners shed Loose roofing sheet blowing in wind | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-26 15:00:00 | Pass | BRAF Declined. Have closed off with costs to date
MSA-DTWD | WA3347942 | Room D3- water leak above staff desks | Murdoch Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-07-08 10:30:00 | Fail | This is a recurring issue - will need to return to measure yp to install a few types of flashing as this is a wind directional issue. will return when dryreturned and measured up flashings for around window and over wndow. Will need scaffold and BRAFSourced materials and delivered to site. Installed multiple flashings as discussed and sealed all joints. put in series 500 screws to fit steel frame and removed waste from site. Complete.
MSA-DTWD | WA3348012 | D block, Mechanical Plant Room- Gas boiler not working | East Perth Campus | GMP-BR | Mechanical Services | Pumps (MS) | Precise Air Group | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-27 12:30:00 | Pass | BRAF approval has been received under WO WA3301671 to commence further works for this job
MSA-DTWD | WA3348103 | B Block, Room BG15- Faulty LED fittings in CRS Spray Booth | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-12 09:33:00 | Fail | Repalced 3x faulty led lights in spray booth with new. Job completed
MSA-DTWD | WA3348274 | Classroom D14 - Roof leak SE corner near box gutter | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-06-23 16:00:00 | Fail | Resolved leak - confirmed with Frank
MSA-DTWD | WA3348302 | A Block, Plant Roo- Boiler is not working | East Perth Campus | GMP-BR | Mechanical Services | Boilers (MS) | Precise Air Group | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 10:30:00 | Pass | Attended site and signed in.Checked operation of boiler system in a block and found boiler running but short cycling. Carried out tests and found boiler short cycling is caused by the bypass valve being manualled because of a faulty dp switch.Also found some possible issues with bms operation like the boiler and pump showing alarm when they are both operating. Requires replacement dp switch which has been quoted previously and then bms works by bms contractor.
MSA-DTWD | WA3348305 | C Block, Room C006 - Door lock is damaged | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 12:40:00 | Pass | replaced lock
MSA-DTWD | WA3348306 | A block Daikin Air conditioning control faults-see notes | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-06-05 16:08:00 | Fail | On site to enable AUTO at 2 pipe VRV systems and change HEAT/COOL masters as required. Made changes insetting mode 3 at outdoor control pcb s, enabled masters 1.3, 3.2 and 4.2 as instructed by FM. Returned to siteand set 1.2 and 2.5 as masters due to excessive temperature fluctuations. To conclude, the site is better suited to 3pipe VRV as classrooms etc require cooling where reception is cool and requires HEAT, I recommend replacementof systems at end of life with 3 pipe VRV where simultaneous HEAT/COOL is available.
MSA-DTWD | WA3348312 | U Block, Wellness centre- multiple faults with alarms from block reporting to EDSEC | Joondalup McLarty Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 10:30:00 | Pass | Attend site to investigate fault on Zone 117 located on DGP 7 in T Block. Put system in walk test input mode, unable to locate. Put cable on tracer, unable to locate. Tested all sensors visible, unfortunately no zone 117. Possibly in roof. I have discussed with Barry and he was happy to program out. Programmed out Zone 117Note: Found sensor on T Block Ground East Entry sensor hanging by cables, no cover, will require replacement
MSA-DTWD | WA3348342 | N Block, Room N119, N235- Shelving needs repair | Mount Lawley Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 12:00:00 | Pass | Arrived at site, spoke with Steve M about shelving. Required x10 slot units to be rehung. Measured leveled and spaced shelving units. Installed anchors and fixed into place. Tidied each area before moving on. Packed away tools.
MSA-DTWD | WA3348426 | E block ground Outside Kitchens E74 & 75 Water leaking through ceiling | Bentley Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-08-25 12:00:00 | Fail | Have attended site and sealed the leak. site sonfirmed leak resolved. patched and painted ceiling
MSA-DTWD | WA3348437 | E block roof C & E blocks Down pipes blocked with leaves. | Bentley Campus | GMP-BR | Roofing | Guttering (RF) | High Tech Maintenance | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 14:00:00 | Pass | TAFE Reported Blocked down pipes on C & E blocks, crew attended unblocked down pipes on both blocks. Cleared gutters causing blockages, all down pipes down functional.
MSA-DTWD | WA3348440 | A block ground A2 Door closer on internal door is not working and needs replacing | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 May 2020 | 2020-05-29 17:00:00 | 2020-05-27 13:30:00 | Pass | Works are now completed and a new door closer has been fitted
MSA-DTWD | WA3348473 | E block E617 male toilets blocked toilet | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 26 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 11:50:00 | Pass | Cleared blockage
MSA-MRWA | WA3348367 | Kitchen - No hot water from Billie Unit | Road Network Operation Centre (RNOC) | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 08:42:00 | Pass | Inspect and tested billi units x2 in level 2 kitchen.All units are working fine.
MSA-DCA | WA3348661 | Low steam alarm | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 27 May 2020 | 2020-05-27 17:00:00 | 2020-05-27 11:00:00 | Pass | Attended call-out at AGWA. Multiple P1 alarms active. Comp air station and direct feed station offline. Reset both stations and Steam Boiler 1 & 2 units. Monitored operation and conditions. All P1 alarms cleared. Stations only require manual reset after a power fluctuation or outage. All plant operating as per BMS programmed control.
MSA-DCA | WA3348696 | Fire pump in alarm | Collection and Research Centre Welshpool-Harry Butler Centre-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 27 May 2020 | 2020-05-27 12:08:27 | 2020-05-27 12:00:00 | Pass | Tech attendedPressure switches faulty and required replacing with new
MSA-DCA | WA3348743 | roof - External flood light, not operating | Art Gallery of WA - James St - Main Building (Block B)-Level 4 - Roof Ventilator Plant | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 16:00:00 | Pass | Re-set Flood light / re-set Dynalite system.
MSA-DCA | WA3349037 | Blocked downpipe on roof of City of Perth Carpark | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-29 09:14:00 | Fail | Jet wash storm water drains
MSA-DCA | WA3349197 | Small Winch Room- Fire detection isolation due to building works | Maritime Museum Victoria Quay-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 15:00:00 | Pass | Tech attended and isolated fire detection to small Winch Room due to building works.
MSA-DCA | WA3349544 | Remove strobe and detector from small winch room | Maritime Museum Victoria Quay-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 08:00:00 | Pass | Remove bell/sounder above pumps due to demolition works - Stored in FIP cupboard.
MSA-DCS | WA3348637 | Canteen- Numerous fluro lights not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 May 2020 | 2020-06-03 17:00:00 | 2020-06-03 09:30:00 | Pass | Replaced faulty lamps and ballast
MSA-DCS | WA3348675 | Unit 2, B Wng- Cell B3- toilet cistern broken & wont flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 May 2020 | 2020-06-03 17:00:00 | 2020-06-30 13:00:00 | Fail | Replaced new inlet valve in cistern.
MSA-DCS | WA3348678 | Unit 13, Cell B1- cell light faulty not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-05-27 08:30:00 | Pass | Repaired faulty lights in unit 13 b1
MSA-DCS | WA3348715 | Unit 2, C Wing- Cell C8- main light switch has been blowing out the fluro lights | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-05-29 12:00:00 | Pass | Repaired faulty lights in c8 unit 2
MSA-DCS | WA3348733 | Unit 2, A wing, cell A7 - window not opening and closing as wont stay up or close correctly | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-07-02 11:00:00 | Fail | DOUBLE UP - JOB COMPLETED ON WA3415244
MSA-DCS | WA3348739 | Unit 3, B wing - ceiling light near the grill not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 10:00:00 | Pass | Replaced damaged gpo in odp
MSA-DCS | WA3348749 | Boiler House, Boiler no 1- blowdown pipe has a hole | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-06-16 06:55:00 | Fail | Investigate leak on boiler 1 found the copper auto blowdown line was leaking from a 1/2” flare union I reflared it testedand found no other issues with the blowdown Line tony requested that a copper drain line that had been cut in 2 placesbe re welded and also asked for a drain line to be installed on a valve in the boiler house I rewelded the pipe and listeditems required to complete drain line cleaned work area signed out and returned to workshop
MSA-DCS | WA3348766 | Visits centre - Auto boil not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 09:35:00 | Pass | On arrival. Units were working correctly. Time and date correct. All ok.
MSA-DCS | WA3348769 | unit 7, H9 - Toilet & sink damaged | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 May 2020 | 2020-05-28 08:33:41 | 2020-05-27 18:10:00 | Pass | Removed broken basin toilet and cistern Replaced with new toilet Replaced with new basin and tap and pipeworkReplaced with new cistern and pipework
MSA-DCS | WA3348770 | Unit 4, Donga Verandah lights not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 12:30:00 | Pass | Investigate and repair all unit 4 external lights.
MSA-DCS | WA3348773 | Kitchen office light covers broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 09:30:00 | Pass | Investigate and replace broken kitchen lights.
MSA-DCS | WA3348776 | unit 7, H9 - Viewing hatch glass & mirror damaged/smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 27 May 2020 | 2020-05-28 08:45:56 | 2020-05-29 11:45:00 | Fail | OBS GLASS/ MIRROR REPLACED
MSA-DCS | WA3348805 | kitchen, Delivery door - False alarming at the control pod | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 May 2020 | 2020-05-28 08:52:48 | 2020-05-27 12:45:00 | Pass | Attended site and inspected reed switch for kitchen delivery door, checked all programming and all tested ok. Found that door drop bolt has been installed and bracket has been mounted over reed switch. Advised security manager and has been made aware to locksmith to relocate drop bolt. Job complete
MSA-DCS | WA3348839 | Unit 7, H9 - Main Cell Window Smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 27 May 2020 | 2020-05-28 09:14:49 | 2020-05-28 12:00:00 | Fail | reglazed window
MSA-DCS | WA3348881 | Unit 4, Roof - shade cloth screen damaged repair/repalce | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-11-25 09:00:00 | Fail | SHADE CLOTH REPLACED
MSA-DCS | WA3348972 | PTZ 51 - no functioning, doesnt pan, tilt or zoom | Hakea Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 May 2020 | 2020-05-28 10:08:30 | 2020-08-14 16:30:00 | Fail | Decommissioned old pelco ptz and installed new axis ip ptz camera as per quoted. Job completed.
MSA-DCS | WA3349017 | Perimeter zone 11 tree blocking camera 11 | Wandoo Rehabilitation Facility | GMP-BR- HO | Landscaping & Gardening | Tree Lopping (LG) | KENNEDY'S TREE SERVICES | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-05-28 09:45:00 | Pass | Work completed
MSA-DCS | WA3349047 | turner A wing part of the essential power not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 27 May 2020 | 2020-05-28 11:00:27 | 2020-05-27 15:30:00 | Pass | Replaced fuse
MSA-DCS | WA3349055 | Disabled Female Toilet exhaust fan is worn out. | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 13:00:00 | Pass | Replaced failed exhaust fan after sourcing replacement.
MSA-DCS | WA3349185 | B wing - cleaning cupboard stiff to lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-08 13:00:00 | Fail | replaced bolt throw and service, repaired face plate
MSA-DCS | WA3349198 | Unit 5 house 7 day room, 2x ceiling fans switches faulty | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-06-04 12:30:00 | Fail | Replaced ceiling fan
MSA-DCS | WA3349203 | medical centre treatment room 4 x fluos need changing to LED as have fallen apart | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-06-04 14:30:00 | Fail | Replaced LED panel lights
MSA-DCS | WA3349240 | Kitchen rear delivery door - Drop Bolt Retaining Plates Broken & Blocking Alarm Sensor | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 27 May 2020 | 2020-05-28 12:32:29 | 2020-06-17 13:00:00 | Fail | Able to rectify issue without additional parts
MSA-DCS | WA3349245 | Unit 1 & 2, Control Pod Electrical Rooms - Fire panels showing faults for Cells | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 27 May 2020 | 2020-05-27 16:35:23 | 2020-05-27 15:23:00 | Pass | Attended site for faults on fire panel.When arrived found unit 1&2 with faults.Unit 1 c/d 15/16 with valve closed pipe 1 manually closed and opened valve and all sitting normal when leftUnit 1 a/b 11/12 too many scans in the week adjusted scan threshold on alert back to normal working condition when leftUnit 2 c/d 3/4Valve closed pipe 2 closed opened valve all back to normal working condition when left
MSA-DCS | WA3349278 | Unit 13 - A Wing A 04 unit 13 sink tap not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 14:09:00 | Pass | nil
MSA-DCS | WA3349287 | Gatehouse - Internal intercom for black gates not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-06-09 09:30:00 | Fail | Stentafone intercom on black gate replaced for new and sealed from weather, tested fully operational. Screws weathered and required drilling and tapping.
MSA-DCS | WA3349294 | comms room netork switched failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-17 14:58:00 | Fail | Installed new network switch and programmed.
MSA-DCS | WA3349378 | Gatehouse - broken power point to right of door | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 09:30:00 | Pass | Replaced gpo
MSA-DCS | WA3349519 | Gate Control room - Multiple receiver faults on duress system | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-08 12:30:00 | Fail | All 6 receiver on TR10 BUS2 offline. Used PC map to locate receivers on the back side of U4 C/D wing. Found 10.2.2 full of water. Replaced damaged PCB. Revealed enclosure. Cleared alert messages and stress tested from the PC. Parts used:Bosch receiver EA102A-304Consumables
MSA-DCS | WA3349530 | Unit 7, E6 - Leaking roof above E6 | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 27 May 2020 | 2020-05-28 15:42:21 | 2020-06-10 15:00:00 | Fail | SOURCE OF LEAKING LOCATED & REPAIRED
MSA-DCS | WA3349537 | gate house CCTV server fault is preventing camera's from recording | Greenough Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 May 2020 | 2020-05-27 23:48:02 | 2020-05-27 16:45:00 | Pass | Attended site and investigated the fault.Checked DVM system.Found that server cannot connect with cameras.Restarted server and conducted test.All ok at departure
MSA-DCS | WA3349591 | monitoring room zoon 8 disalarm | Boronia Pre-release | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 May 2020 | 2020-05-27 21:06:33 | 2020-05-28 13:04:00 | Fail | Replaced 2x splice kits for new, all ok
MSA-DFES | WA3348700 | Lift stuck between floors | CFRS Vincent | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 11:54:00 | Pass | Job completed - LIFT ABOVE TOP FLOOR, 0021 & 0170 FAULTS, RESET, CONFIRM OPERATION, MONITOR OPERATION AND RETURN TO SERVICE - no charges
MSA-DFES | WA3348760 | Tunic Room- positive pressure fan is constantly running | CFRS Armadale | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 13:15:00 | Pass | Complete Attended site and located non working exhaust fan, found sensor to be broken, replaced and tested all in working order
MSA-DFES | WA3348856 | Workshop - Bad roof leaks in workshop and stores area.Leaks are affecting inventory & require repair | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-07-23 15:00:00 | Fail | Attended site and carried out temp cleaning to resolve leak. Will need to return to complete when weather permits
MSA-DFES | WA3349034 | Appliance room groud Single pane of Perspex on rear roller door broken from weather | VFRS Rockingham | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-08-14 14:00:00 | Fail | Technician attended the site of Rockingham Fire Station Volunteers to the Engine bay door 3 rear left A40352182E on 29/05/2020. Following a full test and inspection of door components found fault to be broken perspex window pane on fourth panel. Removed damaged section of perspex from panel as it was posing a safety risk (could fall down on someone). Measure and quote for replacement window pane. Full test and inspection of door function completed prior to leaving site.Note: Did the perspex on the maintenance rather than the quote.
MSA-DFES | WA3349584 | Engine room door on the west side not comming down | CFRS Duncraig | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 19:45:00 | Pass | Technician attended the site of 310 Hepburn Avenue, DUNCRAIG, WA to the Engine bay door 4 Bi-Fold DoorA40352153C on the 27/05/2020.Following a full test and inspection of door components found door staying open and not responding to controls.Checked PE beams ok, opened control panel and closed door using contractors.Reset controller and seems to work fine.Full test and inspection of door function completed prior to leaving site.
MSA-DTAG | WA3348831 | Basement carpark Sallport carport doors not interlocking | Perth Children's Court | GMP-BR-HO | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 13:02:00 | Pass | Found gate to be working correctly. Alarm/ closed position monitor contacts still not been adjusted since last visit. Remounted alarm contacts to make visually better contact. Tested and security staff advised it now works. Security tech may be required to properly test.
MSA-DTAG | WA3348975 | ground level, Court 1 & Magistrate Huges chambers - Lighs flickering | Perth Children's Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-27 13:45:00 | Pass | Job complete
MSA-DTAG | WA3349157 | L3 Drug Ct Interview Rm 3.1 Digi Lock not opening the handle turning not opening door-see notes | Central Law Courts | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-05-28 11:10:00 | Pass | Attended site, gained entry to locked door.
MSA-DTAG | WA3349371 | court 53 court room is a bit cold so the Magistrate has asked if it can be turned up if possible | Central Law Courts-Main Building-Level 5 | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 11:00:00 | Pass | Completed works as per service report, Court 53 a bit too cold, carried out adjustments to VAV box 5.20, test and monitored operation, all appears to be functioning satisfactory.
MSA-DTAG | WA3349384 | Cell 4 PIC with golden staff-requires a special clean during normal cleaning time | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 10:00:00 | Pass | Job carried out as per work order.
MSA-DTAG | WA3349587 | COVID 19; possible contamination by prisoner-see notes | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 11:40:00 | Pass | Job carried out as per work order
MSA-DTWD | WA3348611 | E block, Skills kitchen 2. Combi oven not working | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 27 May 2020 | 2020-05-29 17:00:00 | 2020-07-09 17:00:00 | Fail | 29/ 5/20 BM Arrived at site, liaise with kitchen staff, identify faulty oven, isolate, remove panels, test/fault find, diagnose and found steaming system blocked with calcium build up, decalcified tank, pump, hose lines, removed steamer sensor and found build up of calcium all over the sensor and had broken off into little pieces. The sensor will require replacement, tested other functions and seem to be all operating correctly, the steam function won't work until the sensor is replaced.Also found the motor is making a lot of noise and will require replacement in the future.Part required:1 x water level and temp sensor probe 29/05/20 WSReturned to site with new water level probe to find the element also blown and requires new. Parts required:1 x immersion element. 09/07/20 BM Returned to site with parts fitted and tested all okay.
MSA-DTWD | WA3348642 | Cleaners room, B Block, West Level 1- Light requires replacing | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 27 May 2020 | 2020-06-03 17:00:00 | 2020-06-03 11:00:00 | Pass | Attended site and signed in. Found faulty light. Isolated power and replaced fitting. Tested all ok. Job completed.
MSA-DTWD | WA3348650 | Carpark 4 (in front of A Block)- Carpark lights not coming on | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 27 May 2020 | 2020-05-27 17:00:00 | 2020-05-28 14:00:00 | Fail | Replaced faulty sensor and checked light. Recommendations to replace timer in future with a digital 24/7 with back up battery. Work completed.
MSA-DTWD | WA3348747 | Level 2,A block. FCU43, FCU20 and FCU22 not working and in error | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-07-29 08:00:00 | Fail | Fan motor replaced.
MSA-DTWD | WA3348872 | L Block - security lights constantly tripping | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-09-09 10:00:00 | Fail | BRAF Declined invoice costs to date
MSA-DTWD | WA3348885 | teachers block classroom 1 Error code C5 on A/C panel | Clarkson Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-06-26 13:00:00 | Fail | Picked up parts, accessed site,& replaced controls on a.c. as required, set up controls & tested ok
MSA-DTWD | WA3349060 | west block External entry door near W116 Repair Lock to west block door entry off external corridor | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-05-28 11:05:00 | Pass | replace cylinder components and repair to lock. W116.
MSA-DTWD | WA3349093 | S block L1 S209 hot water unn tap fault | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-05-28 14:00:00 | Pass | Complete
MSA-DTWD | WA3349219 | E block, ground - Electric roof vents not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 14:00:00 | Pass | Investigate roof vent motors in E block. All 3 motors are seized . Plug and sockets are rusted. All other cabling is broken and rusted Located where switched from aswell . Have advised site of findings job completed
MSA-DTWD | WA3349227 | E block, ground, EF2 - water leak from roof | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-07-10 09:45:00 | Fail | Attended site and located leak, unable to access the roof due to inclement weather. Will need to return when weather permits to complete inspection/repair.No further leaks reported. job complete
MSA-DTWD | WA3349320 | G Block, Room G129 Disabled toilet- Blocked toilet | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 27 May 2020 | 2020-06-04 17:00:00 | 2020-05-28 12:20:00 | Pass | Cleared blockage
MSA-DTWD | WA3349344 | Lift - stopped operating | Mount Lawley Campus | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 27 May 2020 | 2020-05-27 17:48:01 | 2020-05-27 14:57:00 | Pass | Job completed - Found lift stuck in the middle of floors with safety circuit complete and having error code, reset H2 with ESE lost speed up. Reset and tested operation. Fault could notrepeat
MSA-DTWD | WA3349393 | Blocks T, U and V - Rats in various locations | Rockingham Campus | GMP-BR | Pest Control | General Pest (PC) | JODAN PEST CONTROL | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 09:40:00 | Pass | Rodent control indoors.
MSA-DTWD | WA3349413 | G Block,Outside GG03 W/S- Bottom of post on lean-to is rusted through & has come away from footing | Carlisle Campus | GMP-BR | Building | Steel Work (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-07-06 13:45:00 | Fail | BRAF has been submitted and we are now waiting for approval to proceed/.2 x posts replaced and guttering re levelled
MSA-DTWD | WA3349448 | Level 1, Chalk and cheese cafe - Ceiling is leaking | Perth Campus B2 | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-06-02 10:15:00 | Pass | Found silicone joints perished on balustrades, repaired. Other leaks appear to come around support pillars. Rubber flooring would have to removed to access pillars. Please note long term issue with water proofing under soft floor beingadequate on balcony. Works have been looked at before, please see Steve Dancy for further details
MSA-DTWD | WA3349469 | BLD 822a reception Faulty downlights Ballasts Humming | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-06-16 12:15:00 | Fail | replaced ballasts
MSA-DTWD | WA3349480 | V block A/C services room and passageway adjacent v51 student toilets roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-06-23 10:17:00 | Fail | A/C units causing the roof leak. Contactractor attended to install drain trays for air con units to resolve the leak
MSA-DTWD | WA3349557 | E block E23 Staff Female Toilet – Leaking Outlet | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-05-28 10:42:00 | Pass | Replaced leaking pan cone
MSA-DTWD | WA3349560 | B block B2111 Faulty Keypad Lock | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 27 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 11:35:00 | Pass | Room B2111 Key Pad lock faulty.Lock repaired.
MSA-MRWA | WA3349109 | L2 Middle of floor behind desk 059 leak behind desk | Road Network Operation Centre (RNOC) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 27 May 2020 | 2020-05-27 15:36:38 | 2020-05-27 13:00:00 | Pass | Base building equipment to be repaired
MSA-MRWA | WA3349154 | Level 1, North West Corner - inspect and rectify faulty light above Rene Shipp | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-05-28 06:45:00 | Pass | Complete
MSA-MRWA | WA3349160 | Level 7, 706 - Inspect and rectify loose GPOs under desk | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 27 May 2020 | 2020-06-02 17:00:00 | 2020-05-28 07:15:00 | Pass | Complete
MSA-DCA | WA3349773 | CRC Boiler 1 is in fault-Please contact Sue Murray on to arrange site access | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Plant Room - Loading Bay Area | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 28 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 12:30:00 | Pass | Attended site. Boilers servicing CRC to not be operating correctly (boiler 1 in fault). Applied tests and checks. Investigation found Air present in HW pipework servicing CRC and BWS. Attempted in multiple locations to bleed air out of system at various points. Investigation found water leakage present. Isolated boiler and HW pumps. Applied control strategy change's to BMS to take manual control over CRC conditions as best as possible. Contacted PFM, Job to be closed with a new LVM to be raised. To return to site tomorrow under new job to meet PFM supplied tech to search for water leak.
MSA-DCS | WA3349727 | yeeda Nicol Air con not heating | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 28 May 2020 | 2020-06-02 17:00:00 | 2020-06-25 16:29:00 | Fail | System is running
MSA-DCS | WA3349765 | U10 D14 Leaking pipe under sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 28 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 14:38:00 | Pass | Tighten up and thread taped leak on basin set
MSA-DCS | WA3349767 | U10 B4 Leaking Sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 28 May 2020 | 2020-06-04 17:00:00 | 2020-06-12 07:55:00 | Fail | Ordered parts 4/6/20
MSA-DCS | WA3349769 | unit 1 D16 Toilet Cistern Flush pipe is not connected and flooding Electrical Fire Alarm Panel Below | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 28 May 2020 | 2020-05-29 07:46:32 | 2020-05-28 12:29:00 | Pass | Renew kinky rubber to flush pipe. Renew Flexi to cistern
MSA-DCS | WA3349779 | Unit 1 pod 8 kitchen faulty exhaust fan | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 28 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 11:30:00 | Pass | Replaced faulty exhaust fan
MSA-DCS | WA3349800 | U6 A11 Toilet continuously running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-12 09:40:00 | Fail | Pulled apart cistern replaced outlet washer
MSA-DCS | WA3349807 | Kaartdijin Mia - Office-Exit/Entry Door next to the refrigerator/Door lock is not working properly | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-16 11:00:00 | Fail | replaced mortise lock, re fit lock to align with strike.
MSA-DCS | WA3349809 | Unit 6, C5 & C6 - sink taps continually runs unable to turn off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-12 08:48:00 | Fail | Reseated and washerd x2 taps
MSA-DCS | WA3349810 | unit 3 ablusion blockd broken window | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-16 12:30:00 | Fail | WINDOW RE GLAZED- FRAME REPAIRED
MSA-DCS | WA3349815 | Gatehouse, reception - power point broken | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 12:00:00 | Pass | Replaced broken gpo
MSA-DCS | WA3349817 | reception area split system air con has iced up | Warminda Hostel | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-07-01 09:00:00 | Fail | Carried out new installation and removal of old AC unit.
MSA-DCS | WA3349821 | demountable training room leak from the ceiling | Warminda Hostel | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 1 | CLOSE | 28 May 2020 | 2020-05-29 08:26:06 | 2020-06-02 09:30:00 | Fail | Attended site and carried out repairs to the demountable training room roof.
MSA-DCS | WA3349825 | unit 1 B wing east ablusions block broken glass to window | Bandyup Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-04 12:00:00 | Fail | REGLAZE SASH WINDOW
MSA-DCS | WA3349829 | Unit 1 B wing west ablusion block roof leak over vent over chair | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-07-31 09:39:00 | Fail | flashing's, vents, seals,decktites, sheeting sealed and repaired
MSA-DCS | WA3349896 | camera's (CCTV) in cells U1 3.08 & 3.09 and Maxi Yard Dayroom-see notes | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-26 09:00:00 | Fail | Job complete
MSA-DCS | WA3349923 | Urquhart, C wing, program room - window broken approx 700mx400 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-07-03 11:30:00 | Fail | WINDOW REGLAZED
MSA-DCS | WA3349969 | Stores outside the prison, Purchasing offices, near mail sorting table - Roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-08-05 11:25:00 | Fail | REMOVED OLD INSULATION AND REPLACED. AIRCON WAS POSSIBLE MOVED BY AN ELECTRICIAN CAUSING THE LEAK. AIRCON RE-POSITIONED
MSA-DCS | WA3349979 | Unit 14, B & D - Exterior air lock door hadle and lock faulty/repair | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-08-03 14:15:00 | Fail | Obtain broken handle, unable to repair.Attend site replace handle and loctite screws in place
MSA-DCS | WA3349983 | ground main kitchen Mixer tap lever is stiff and does not work properly - tight to swivel.-see notes | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-02 09:00:00 | Pass | Complete
MSA-DCS | WA3349991 | cleaing, bin lifter - tripped circuit breaker (possibly a water issue) | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-16 12:00:00 | Fail | Removed, repaired and reinstalled faulty bin lifter motor and controller
MSA-DCS | WA3350004 | Female Ablutions near training room 6 and 7 Repair faulty cistern - crack on cover | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-02 10:00:00 | Pass | Complete
MSA-DCS | WA3350010 | Outer perimeter sensor C4 not operating | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 May 2020 | 2020-05-28 14:36:41 | 2020-05-28 14:30:00 | Pass | Checked information on perimeter workstation, no fault evident. Attended External perimeter Zone C4, Tested Fence voltage and tested alarms, as per signature Slip.
MSA-DCS | WA3350028 | Female Ablution near rooms 6 & 7 HWS Tray and overflow pipe for hot water system for shower rusted | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-02 12:00:00 | Pass | Complete
MSA-DCS | WA3350032 | stores, office - water leaking from smoke detector, aircon tray not draining causing fault | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 13:04:00 | Pass | Checked for water leak,found out door drip tray had been moved realigned, also found water running back down main drain line into another tray,lifted tray off the floor,all water now flowing away from trays.
MSA-DCS | WA3350034 | Unit 14, B & D dayroom - top draw on the right broken | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-18 14:30:00 | Fail | DRAWER RUNNER REPLACED
MSA-DCS | WA3350043 | Stores - roller door not operating correclty | Casuarina Prison | GMP-BR- HO | Building | Automatic Doors (BU) | UNIVERSAL DOORS | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-29 08:30:00 | Pass | REFIT CURTAIN INTO GUIDES, ADJUSTED SPRING TENSION, RESET LIMITS
MSA-DCS | WA3350049 | ground, Unit 13 - rear camera pole lighting distractor bent | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-16 12:30:00 | Fail | Attended site.Resecured retaining nuts of lightning rod on PTZ camera pole near unit 13.All ok at departure
MSA-DCS | WA3350063 | Turner yard Flood light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-18 13:00:00 | Fail | Repaired bollard lights turner yard
MSA-DCS | WA3350067 | MPU (8) - M9 Aeiral socket faulty/broken in cell | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 1 | CLOSE | 28 May 2020 | 2020-05-29 11:21:36 | 2020-05-29 12:00:00 | Fail | Replaced broken TV point in MPU M9, tested OK
MSA-DCS | WA3350108 | Laundry washing machine No 7 - Showing No Water, faulty inlet solenoid | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 28 May 2020 | 2020-05-29 12:04:50 | 2020-05-29 11:00:00 | Pass | AMS629916 WA3350108 - Hakea - : Laundry washing machine No 7 - Showing No Water, faulty inlet solenoidThe main cold water supply line had some scale and sediment block the valves and pipe work. Removed pipes and cleaned. Cleaned filters and flushed the main water line. Checked solenoid valves and drain pilot valve operation. Mike on site said there had been work done in the plumbing.
MSA-DCS | WA3350112 | Laundry washing machine No 3- Dumping Water. Faulty Dump Valve | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 28 May 2020 | 2020-05-29 12:10:08 | 2020-05-29 12:30:00 | Fail | AMS629919 WA3350112 - Hakea - Laundry washing machine No 3- Dumping Water. Faulty Dump ValveLocated PVC water directing tube that had fallen down blocking the siphon breaker causing the inlet water to spray out the vent hose. Fitted the directing tube at the top and securely clamped it. Tested.
MSA-DCS | WA3350129 | Admin Superintendent office Tombstones on fluro have perished | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-03 11:00:00 | Pass | Replaced damaged tombstones and lamps
MSA-DCS | WA3350144 | Unit 2, Control room, broken light above control desk | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-29 11:00:00 | Pass | Repaired light
MSA-DCS | WA3350181 | Kitchen - Freezer alarm will not stop beeping | Wooroloo Prison Farm | GMP-BR- HO | Refrigeration | Freezers (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 28 May 2020 | 2020-05-29 12:43:33 | 2020-05-28 16:00:00 | Pass | Spoke with kitchen staff about events.Reset locked in alarm.Alarm cleared.Evaporator started.System running okay.
MSA-DCS | WA3350197 | Unit 2 A4 Cell Door Has Dropped & Dragging on The Floor | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 May 2020 | 2020-05-29 13:05:54 | 2020-05-29 13:45:00 | Fail | Realigned Unit 1 A4 Cell Door
MSA-DCS | WA3350201 | Master Control POD- external monitors are showing purple should be red | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 May 2020 | 2020-05-29 13:09:42 | 2020-05-28 14:15:00 | Pass | attend site, tested & currently indicating correctly. zones indicate & display correct system. currently fully operational.
MSA-DCS | WA3350211 | Unit 2 Cell A11 - Cell light broken | Hakea Prison | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-29 13:00:00 | Pass | Repaired light
MSA-DCS | WA3350213 | Unit 2, cell A14 - cell door has dropped on the floor | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 May 2020 | 2020-05-29 13:18:58 | 2020-05-29 14:45:00 | Fail | Realigned Unit 1 A14 cell door.
MSA-DCS | WA3350220 | unit 1 D11 Cell Door Has Dropped & Jamming on The Door Frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 May 2020 | 2020-05-29 13:18:00 | 2020-05-29 11:00:00 | Pass | Realigned Unit 1 D11 Cell Door
MSA-DCS | WA3350225 | Unit 2, A3 Cell Door Has Dropped & Jamming on The Door Frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 May 2020 | 2020-05-29 13:27:48 | 2020-05-29 13:00:00 | Pass | Realigned Unit 1 A3 Cell Door.
MSA-DCS | WA3350226 | Unit 2, cell A9 - Cell Door Has Dropped Lose Hinges | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 May 2020 | 2020-05-29 13:27:44 | 2020-06-10 15:45:00 | Fail | Supplied and fitted parts and realigned door
MSA-DCS | WA3350250 | Recreation gym Goose neck tap broken of drink fountain | Wandoo Rehabilitation Facility | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 16:38:00 | Pass | Replaced faucet and bubbler cartridge ZIP FOUNTAIN
MSA-DCS | WA3350274 | MPU (8) - M11 cell power keeps tripping out . | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-29 08:30:00 | Pass | Replaced damaged cell gpos in mpu m11
MSA-DCS | WA3350309 | unit 1, Safe Cells - Lens covers damaged. Unable to see through | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-29 08:00:00 | Pass | Unit 2 Cell D9 works in progress refer to WA3253947, clean front camera window cell D2 camera. Job completed.
MSA-DCS | WA3350339 | Gate control - perimeter lighting needs to be time adjusted as turns on when already dark | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 28 May 2020 | 2020-05-29 14:55:37 | 2020-05-29 09:00:00 | Pass | Reprogrammed timer for perimeter lights
MSA-DCS | WA3350361 | Exit of admin building - lock faulty on middle door, as wont unlock once locked | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-08 14:30:00 | Fail | Supplied and fitted parts
MSA-DCS | WA3350372 | New Canteen back area - roof leaking above shelving | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-19 13:15:00 | Fail | ROMOVE SHEETING TO PULL UP ENDS OF VALLEYS. REPLACED FLASHING
MSA-DCS | WA3350375 | Unit 1 AWing Cell A4, cell door top hinge has snapped | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 28 May 2020 | 2020-05-29 15:35:38 | 2020-05-29 09:30:00 | Pass | Attended site and carried out repairs to the cell door hinges that had snapped.
MSA-DFES | WA3349849 | roof solar HWS not working | CFRS Fremantle | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 28 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 14:00:00 | Pass | Electrical connection disconnected to one solar unit and second unit detected power to booster off. Turned power on all working
MSA-DFES | WA3349956 | Stores - water leaking in the roof, that is leaking onto equipment | FESA RHQ - Forrestfield | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 28 May 2020 | 2020-05-29 17:00:00 | 2020-05-28 14:30:00 | Pass | Have attended site and carried out repairs will need to confirm in next rain if repairs have resolved the issue. Bucket tested on site
MSA-DFES | WA3350012 | Kitchen & watchroom - 2x 240v light switch arcs when switched 1xkitchen & 1xwatchroom | CFRS Hope Valley | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-03 13:45:00 | Pass | COMPLETED
MSA-DFES | WA3350059 | Administration, hot desk - Skirting Board near door have damage skirting board from Termites. | FESA RHQ - Forrestfield | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-08-05 14:45:00 | Fail | Attended site and located damaged skirting. Approximately 4m of skirting damaged by termites that will need to be replaced. Will need to return with materials to complete Works now complete 5/8/20
MSA-DFES | WA3350076 | Administration building, Instructors office - roof leaking on the north wall | FESA RHQ - Forrestfield | GMP-BR | Roofing | Tiled Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 28 May 2020 | 2020-05-29 17:00:00 | 2020-07-08 14:15:00 | Fail | Cleaned Box gutter and found rust casing leak measured to replace rusted section of box gutter. BRAF will be required . Box gutter replaced as per BRAF scope
MSA-DFES | WA3350185 | print room between lecture room 7 and 8 admin, roof leak | FESA RHQ - Forrestfield | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 28 May 2020 | 2020-05-29 17:00:00 | 2020-07-30 13:00:00 | Fail | Cleared downpipe outlet and applied silicone to suspected source of leak. Will need to reassess during next rain to determine if repairs have resolved the problem22/6 BRAF has been submitted and we are waiting on approval to proceed. Installed new flashings and sealed
MSA-DFES | WA3350389 | Ground Floor Stair 5 External door not latching properly, door latch is showing damage | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-04 14:53:00 | Fail | Works are completed and the door is operating correctly
MSA-DFES | WA3355622 | **Retrospective work order** Bypass reporting on Zone 19 App Bay 1 rear roller door | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 28 May 2020 | 2020-05-28 17:00:00 | 2020-05-28 09:34:00 | Pass | EXTERNAL CHECK CARRIED OUT. ALL APPEARS SECURE.
MSA-DTAG | WA3349875 | ground front door Front door is stuck open. Not closing. | Perth Children's Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 28 May 2020 | 2020-05-29 17:00:00 | 2020-06-25 07:30:00 | Fail | Inspected door and suspect internal sensor is latching on requires replacing with 1x eagle one sensor. Also requires brush on doors replacing grey sticky back 12m site have asked this to be done at 6.30am.Will return to siteReturned 25/6/20 - Replaced internal sensor and fitted brush strip and brush to door set up and tested all ok at time of test.
MSA-DTAG | WA3349915 | Grd front door Old sensor removed for auto doors, wasn’t patched a hole is left in the ceiling-note | Perth Children's Court | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-07-14 12:31:00 | Fail | REPAIR HOLE IN CEILING AND PAINT
MSA-DTAG | WA3349993 | ground court 3 Leak from roof at the back of court 3, dripping onto chair. | Armadale Courthouse | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-26 13:23:00 | Fail | LEAKS LOCATED & REPAIRED
MSA-DTAG | WA3350121 | Level 2A, Admin Services, Store room - Fluro light out in store room | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 4 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-03 09:30:00 | Pass | Job complete
MSA-DTAG | WA3356203 | L11 kitchen Clicking sound and no water-see notes | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-03 11:00:00 | Pass | REPLACED POWER CONTROL PCB ON BILLI QUADRAPROMAP NOT WORKING
MSA-DTWD | WA3349759 | T block disable toilet when flush water goes over the floor | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 2 | CLOSE | 28 May 2020 | 2020-06-02 17:00:00 | 2020-05-28 10:15:00 | Pass | Replaced inlet valve
MSA-DTWD | WA3349818 | B block, ground level, B16 - blocked toilets male & female | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 12:43:00 | Pass | Cleared blockage
MSA-DTWD | WA3349835 | Level 2, D224 - damaged/faulty Mech Services access panel please repair/fix | Perth Campus B4 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-03 15:53:00 | Pass | collected required material for job. Attended site collected keys and carried out isolation and repairs to damaged electrical cover panel. Works area left tidy.
MSA-DTWD | WA3349840 | H block ladies toilet Leaking basin tap | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-02 16:00:00 | Pass | Repalce taps h block
MSA-DTWD | WA3349868 | foyer area where the 2 x post hoist is located roof leak-see notes | Kwinana Automotive Centre | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-07-10 14:30:00 | Fail | Assessed roof leak from below will need EWP to access roof to carry out further investigationInspected roof space - Re-siliconed rainhead to resolve leak. No further reports of leaking. Job complete
MSA-DTWD | WA3349901 | J block Rusted out/Damaged hand rail to J Block external walkway | Bentley Campus | GMP-BR | Carpentry | Staircases, Balustrades and Handrails (CA) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-07-31 12:00:00 | Fail | 2 and 3 Badly rusted hand rail will need to be replaced with new. BRAF will be required 11/6 BRAF Submitted and we are now waiting on approval to proceed with the works
MSA-DTWD | WA3349944 | E block, E300, ground - No power on R42 GPO's (RCD will not reset keeps tripping) | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-03 10:00:00 | Pass | Attended site and signed in. Located faulty rcd. Isolated and megga tested the circuit found dead short. tested further and found ceiling rose full of water and damaged. Replaced ceiling rose. Tested all ok. Reset rcd. Advised pfm. Job complete.
MSA-DTWD | WA3349966 | E block E16 Female Student Toilets – Faulty Cistern in last cubicle | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-09 15:00:00 | Fail | Replaced cistern and buttons
MSA-DTWD | WA3350036 | L4 C401 emergency glass botton on slidding door faulty | Perth Campus B2 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 16:03:00 | Pass | Inspected and found that the break glass unit has been damaged and requires replacing ASAP. Will return with partReplaced damaged breakglass unit on manual swing door, tested all ok.
MSA-DTWD | WA3350132 | Level 1 - repair/replace filters to AC LG-5 as filters are dirty to the point of being blocked | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 28 May 2020 | 2020-06-05 17:00:00 | 2020-06-09 09:35:00 | Fail | Returned to site after 3.30pm complete required paperwork set work area up isolation unit removed celling tile and replaced air filters. Checked and confirmed airflow through unit. Confirmed system operation restored without fault. Old filters removed. Spare filter set has been left with unit for 6 monthly change over due to equipment location in high traffic area. Work area left tidy.
MSA-DTWD | WA3350138 | B block, Main Walkway - 6x skylights leaking requiring repairs/replacement | Murdoch Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-30 11:30:00 | Fail | Sourced cracked skylights - access around roof difficult. Measured 6 fibreglass skylights - may need BRAF depending on pricingPicked up materials and returned to site. 3rd man required to hold sheeting and assist due to heavy wind and safety concerns as it is a round shaped roof. Works completed.
MSA-DTWD | WA3350216 | L3 A block A310 lock to cabinet stuck | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 28 May 2020 | 2020-05-28 17:20:32 | 2020-05-28 14:30:00 | Pass | service to locks and replace broken and damaged keys for rm A310
MSA-DTWD | WA3350253 | B block B2417 Staff Room – Roof leak | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-06-26 09:45:00 | Fail | Assessed leak from ground level. Unable to access the roof due to inclement weather. Will need to return when weather permits to assess from the roof. Leak Resolved and water damaged wall panels replaced
MSA-DTWD | WA3350270 | P block P024 water leak coming in through ceiling could be damaged gutter | Balga Campus | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-07-02 14:45:00 | Fail | P block 024 leaking along gutter line - found water ingressing from sheet laps due to build up of silt and dirt, cleaned section of roof over the area.
MSA-DTWD | WA3350278 | West Block Level: 1 Panel has fault and doesn't arm up | Mount Lawley Campus | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 28 May 2020 | 2020-05-29 17:00:00 | 2020-06-09 13:27:00 | Fail | System showing checkTested all voltagesTested all Polling loopsReplaced 1 of panel batteryLocated floating polling loop and disconnectedSystem now showing normal
MSA-DTWD | WA3350293 | U block U017 Altendof pannel saw appears seams to be limp mode | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-05-28 16:00:00 | Pass | U Block U017 Altendof Panel Saw faulty. Check machine & controls. Lube warning on, machine doesn't have auto lube. Give regular maintenance service, clean & lube where required. Assemble & test.
MSA-DTWD | WA3350343 | Gutters have overfilled causing them to come away from roof. | Carlisle Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 May 2020 | 2020-06-03 17:00:00 | 2020-07-08 09:00:00 | Fail | Gutters needed clearing, weight of the water retained in the gutter bent canter lever section of the walkway roof down. Cleared gutters, straightened frame, re-tightened fixings and add new additional fixings to secure
MSA-DTWD | WA3350351 | Fire pump - Pump running, no know cause (manually turned off). No notification | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 28 May 2020 | 2020-05-29 17:00:00 | 2020-05-29 16:00:00 | Pass | JACKING PUMP WAS NOT WORKING CAUSING LOSS OF PRESSUREON FURTHER INVESTIGATION DISCOVERED MAIN POWER SUB STATION WAS ISOLATED AND OFFLINEWE RESET THE POWER AND SYSTEMS ARE NORMAL
MSA-DCA | WA3350944 | Conservation Office-Active leak coming from pipe above ceiling in shared office | Shipwreck Galleries-Administration Building -Level 1 | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-06-10 12:15:00 | Fail | Cleaned off old silicone and sealed pipe with storm PVC coupling joint. Site confirmed leak resolved.
MSA-DCA | WA3350947 | Staff tea room Water leaking into tearoom from under the window | Shipwreck Galleries-Administration Building -Ground Floor | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 14:15:00 | Pass | Attended site and located leak from below Second storey window leaking. Need boom lift and traffic management to get access. 11/6 BRAF has been submitted and we are now waiting on approval before proceeding.15/6 BRAF Declined and site requested to close off job and charge costs to date
MSA-DCA | WA3350955 | Backstage hallway- Emergency Exit Light is not working | Short Street Theatre-Main Building-Level 1-Rehearsal Room | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-11 11:30:00 | Fail | COMPLETED
MSA-DCA | WA3350956 | Various leaks in the Theatre Auditorium-see notes | Short Street Theatre-Main Building | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-07-24 15:15:00 | Fail | Attended site and located 6 x leaks, Gutters were full of leaf debris some of which we were able to remove before the bad weather made it impossible to continue. Will need to return to complete gutter clean and measure up22/6 BRAF Submitted for repairs
MSA-DCA | WA3351297 | Various leaks coming into the Gallery and flooding at the main entrance doors | Old Customs House-Main Building-Ground Floor | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 29 May 2020 | 2020-05-29 17:53:22 | 2020-06-19 13:45:00 | Fail | BRAF Declined
MSA-DCA | WA3351332 | FOH – Ladies toilets: The first on the left is leaking from the floor from a black seal | His Majesty's Theatre-Theatre Building-Level 2-Upper Circle Female Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 15:45:00 | Pass | Replaced pan rubber
MSA-DCA | WA3351336 | Basement Rehearsal: Men’s toilet – First on the left, the porcelain bowl is cracked | His Majesty's Theatre-Theatre Building-Basement-Male Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 12:35:00 | Pass | Replaced cracked pan and adjusted pipe work to suit
MSA-DCA | WA3351352 | Stalls Level 1: One toilet is not flushing, and the hot water tap on the sink is not working. | His Majesty's Theatre-Theatre Building-Level 1-Side Stage Area | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 16:55:00 | Pass | Replced faulty inlet valve and reeashed pillar tap
MSA-DCA | WA3351354 | ground gift shop Water leak coming through to the giftshop | Shipwreck Galleries | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 29 May 2020 | 2020-05-29 18:32:25 | 2020-07-20 11:00:00 | Fail | Attended site and located leak, unable to access the roof due to inclement weather. Will need to return when weather permits to complete inspection/repair 15/6 BRAF has been submitted and we are waiting for approval to proceed with the works
MSA-DCS | WA3350442 | Cell call system in fault - not working. | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 May 2020 | 2020-05-30 01:49:47 | 2020-06-02 13:28:00 | Fail | check function of unit 1,2,& cell call 3 confirmed functioning locally to control room.u6 errors are bombarding central control room & flooding the unit .node status checked on server & units 1,2,3,4s central control all online. send report offsite. job complete.
MSA-DCS | WA3350488 | Major system wont work | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 29 May 2020 | 2020-05-29 10:09:43 | 2020-07-06 16:30:00 | Fail | Major system failure due to electrical works. All systems now back online. Two faults remain.Replaced Moxa 6250 serial modem for Transponder 5 (Gym Office). Programmed and investigated issue. Found TR5doesn't communicate with the server.Checked TR5 operation. No fault present. Reset VM MDAS server. All transponders online. Tested system operation,ok.Job completed.
MSA-DCS | WA3350500 | Key barrel failed on entry door into PFM critical spares store-see notes | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 29 May 2020 | 2020-06-05 17:00:00 | 2020-06-24 16:30:00 | Fail | Supplied and installed parts as required
MSA-DCS | WA3350605 | main kitchen freezer is not working correctly minus 9 degr | Boronia Pre-release-External Area-Ground Floor | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 May 2020 | 2020-05-30 07:00:47 | 2020-05-29 13:15:00 | Pass | Checked found the control breaker off turned on and started the unit found OK.
MSA-DCS | WA3350665 | Unit 10 Pa system not working. No sound coming in or out of hand piece. | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 May 2020 | 2020-05-30 07:33:02 | 2020-05-29 14:00:00 | Pass | Replaced damaged CI-OH with new CG-OH, tested ok . Job completed.
MSA-DCS | WA3350705 | Bakery - Workshop THE PROVER APPEARS TO HAVE TRIPPED-see notes | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 29 May 2020 | 2020-05-30 07:51:46 | 2020-05-29 14:00:00 | Pass | 29/5/20Arrived at site, liaise with reception, walk to the kitchen, identify faulty prover, isolate, remove all panels, test every single element and components for faults and found bugs running everywhere around the elements, cleaned and serviced all components, repaired hot join on overtemp, reassembled all components and energise then tested all okay.
MSA-DCS | WA3350710 | Unit 4 - B Wing light hanging by wires in B Wing cleaning store | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 May 2020 | 2020-05-30 07:55:49 | 2020-06-03 12:00:00 | Fail | Isolated and removed damaged light in unit 4. Picked up replacement and installed
MSA-DCS | WA3350723 | Unit 14 - A9 Blocked shower drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 May 2020 | 2020-06-05 17:00:00 | 2020-06-02 14:06:00 | Pass | nil
MSA-DCS | WA3350741 | O D P - Lunch Room faulty double power point | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 08:30:00 | Pass | Repaired damaged gpo in odp
MSA-DCS | WA3350742 | Unit 4, B & D - oven door still keeps popping ope when running replace/repair broken seal | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-03 09:40:00 | Pass | Replaced Doorseal, adjust door catch, test ok.
MSA-DCS | WA3350751 | Unit 2, A & C - Hot water urn in the common room comes out milky & bubbly, it appears contaminated | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-02 14:04:00 | Pass | nil
MSA-DCS | WA3350773 | Unit 1 D12 cell light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 May 2020 | 2020-05-30 08:23:12 | 2020-05-29 10:00:00 | Pass | Repaired light
MSA-DCS | WA3350779 | Unit 2 A2 cell light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-05-29 12:00:00 | Pass | Repaired light
MSA-DCS | WA3350811 | BR-control external camera 187 issues with PTZ motor | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 May 2020 | 2020-05-30 08:51:19 | 2020-05-29 12:30:00 | Pass | Trace the faulty telemetry function from melaleuca equipment room up to hakea . Rectified and fixed the fault. Job completed.
MSA-DCS | WA3350839 | Unit 4, B Wing- no hot water | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-25 15:00:00 | Fail | Remove faulty tempering valves underneath transportable building. Bridge pipe work. Supply and install new thermostatic mixing valve on hot water supply in an accessible location. Commission hot water. Prisoners happy about the hot water, not happy about being in prison.
MSA-DCS | WA3350840 | various Repair roof leaks in various areas - Business services office 1 & 2 .See comments | Nyandi Training Academy | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 May 2020 | 2020-05-30 09:08:20 | 2020-07-27 10:06:00 | Fail | MULTIPLE LEAKS REPAIRED
MSA-DCS | WA3350847 | York cooling tower - system 1 fault & temp is rising in packing room, | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Cooling Tower (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 May 2020 | 2020-05-30 09:09:50 | 2020-05-29 14:30:00 | Pass | essential Ref. attended , found stage 2 compressor contactor faulty, replace contactor and clear oil trip fault.Left operational
MSA-DCS | WA3350850 | Unit 4, Cell E19 - light switch broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-02 14:00:00 | Pass | Investigate and replace broken light switch in unit 4 cell E19
MSA-DCS | WA3350858 | SOG Pod - GPO in external equipment cabinet inner defence G4 Faulty | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-03 11:00:00 | Pass | Replaced power supply for external defence cabinet in zone g4
MSA-DCS | WA3350859 | Training gym grounds clear blocked drains that has caused flooding in patio area and gym | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 May 2020 | 2020-05-30 09:20:42 | 2020-06-12 11:44:00 | Fail | Attended site,Investigate issues with storm water system to site gym. Locate drains undersized and with back fall causing drains to hold water and block. Used jet wash to clear all storm water lines. Used camera to site all drain paths and locate soak wells and connection points.Quote requested for rectifications
MSA-DCS | WA3350872 | reception multiple joins in vinyl floor liffting needs to be re glued | Bandyup Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-09-26 16:45:00 | Fail | VINYL REPAIRS COMPLETED
MSA-DCS | WA3350874 | Jeelia, Office - Cell exhaust fan panel fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 29 May 2020 | 2020-05-30 09:26:15 | 2020-05-29 12:00:00 | Pass | Attended site, investigated exhaust fan fault light showing. Exhaust fan required resetting. Fault light gone, exhaust fan running. Tested all working well.
MSA-DCS | WA3350884 | Kimberley wing office-Repair flickering light and inspect lights in area-possibly wet from water | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-03 09:00:00 | Pass | Repaired faulty lights in Kimberly wing and male toilets
MSA-DCS | WA3350911 | Kitchen- Kitchen bells is not working | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 29 May 2020 | 2020-05-30 10:02:10 | 2020-05-29 13:30:00 | Pass | Kitchen Bell faulty, no ignition. Check kettle & controls. Main gas valve faulty. Dismantle, remove faulty valve. Install new gas valve. Assemble & test. All working correctly. Report to staff.
MSA-DCS | WA3350919 | Unit 1, B11 - Cistern broken and leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 May 2020 | 2020-05-30 10:13:46 | 2020-05-29 14:30:00 | Pass | Removed broken cistern replaced with new cistern and pipework
MSA-DCS | WA3350928 | Unit 2, A Wing Showers- Shower handle broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-07-03 12:38:00 | Fail | Ordered in new tap from tradelink 4/6/20Installed new tap assembly
MSA-DCS | WA3350932 | Unit 2, Cell D7- Tap broken on sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 10:08:00 | Pass | Replaced broken pillar tap
MSA-DCS | WA3350938 | Perimeter - zone 10 fence is on constant alarm and zone 2 fence seems to be over sensitive | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 May 2020 | 2020-05-30 10:32:26 | 2020-06-04 15:30:00 | Fail | Replaced a total of 5 splice kits between 2 zones, replaced around 400 cable ties and repaired / replaced connections, zones now registering 1Mohm and tested operational.
MSA-DCS | WA3351073 | unit 4 cell B8 exhaust fan faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-02 15:30:00 | Pass | Investigate and replace exhaust fan in unit 4 cell B8
MSA-DCS | WA3351085 | Main building. Glass door rubber seal, rubber strips coming off | Nyandi Training Academy | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-05-30 15:25:00 | Pass | This work was advised to be for a glazier and as such will not be charged by assa Site and call center advised
MSA-DCS | WA3351101 | Outcare/ reset building - roof leak | Bandyup Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 May 2020 | 2020-05-30 11:41:42 | 2020-06-19 13:17:00 | Fail | INSTALLED NEW STEEL SHEETS AND FLASHING
MSA-DCS | WA3351107 | Outcare/ reset building - roof leak casuing power to trip and not resset. | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 29 May 2020 | 2020-05-30 11:44:13 | 2020-05-29 15:30:00 | Pass | Checked report of water damage to electrical, nothing found
MSA-DCS | WA3351135 | Unit 4, control room - camera feed has disappeared from the screen | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 May 2020 | 2020-05-30 12:00:54 | 2020-06-02 11:00:00 | Fail | Acquire 2 x 6 way power adapter boards with surge protection from local supplier offsite and install onsite. Cables tidied and boards fixed to desk railing
MSA-DCS | WA3351144 | Pharmacy, Roof leak above electrical outlets | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-09-04 14:19:00 | Fail | CLEANED BOX GUTTER - REPLACED SARKING - GENERAL REPAIRS TO ROOF
MSA-DCS | WA3351153 | Unit 6, B wing shower tap not turning off 1st shower on the right | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-12 10:32:00 | Fail | Replaced and reseated taps x2
MSA-DCS | WA3351162 | Unit 9, Cell A15- Hot water tap leaking underside of basin | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-05 13:30:00 | Pass | repaired leaking tap
MSA-DCS | WA3351250 | Unit 4A, near cell 27- ablutions fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 10:00:00 | Pass | Replaced 3x exhaust fans
MSA-DCS | WA3351253 | officers house- garage powerpoint is faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 13:30:00 | Pass | Removed faulty cabling
MSA-DCS | WA3351265 | Unit 1, A/C yard camera is not displaying in the control room | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-10-13 12:54:00 | Fail | Job to be complete under Wa3587893
MSA-DCS | WA3351273 | Maining Building, ground , various levels - Clean, blow dry and sanitise wet carpet from roof leaks | Nyandi Training Academy | GMP-BR- HO | Cleaning | Cleaning (CL) | DUNBAR SERVICES (WA) PTY LTD | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-03 14:39:00 | Pass | Sanitised and dried wet carpets
MSA-DCS | WA3351289 | External Stores, Robyn Cains office - roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-10-05 09:00:00 | Fail | SOURCE OF LEAKS LOCATED & REPAIRED
MSA-DCS | WA3351294 | Kitchen - Drain is blocked attached to the Rational oven that is nearest the office | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 14:11:00 | Pass | nil
MSA-DCS | WA3351305 | visits room entry of the prison water is coming into entry | Wandoo Rehabilitation Facility | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 May 2020 | 2020-05-30 14:07:41 | 2020-05-30 12:15:00 | Pass | INVESTIGATED LEAK - CLEANED GUTTER
MSA-DCS | WA3351306 | Unit 7, Lobby- Roof leak (Rain is flooding lobby) | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 May 2020 | 2020-05-30 14:08:27 | 2020-06-19 13:24:00 | Fail | TEMP REPAIR. SEALER MAY NEED REPLACING
MSA-DCS | WA3351311 | Education, office - lock sticking | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-04 12:30:00 | Pass | Service to lock
MSA-DCS | WA3351342 | Unit 2 A1 Door Dragging on the floor | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-03 15:30:00 | Pass | Realigned door Unit 2 A1
MSA-DCS | WA3351379 | ground Computer room 7 Water leaking through ceiling in middle of room and along walls | Nyandi Training Academy | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 May 2020 | 2020-05-30 14:37:32 | 2020-06-19 13:27:00 | Fail | REPLACED ROOF SHEETS
MSA-DCS | WA3351383 | Unit 7 control flooding | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 29 May 2020 | 2020-05-29 18:43:23 | 2020-05-29 17:04:00 | Pass | Investigate leak in roof above unit , after inspection found leak to be coming from roof above, will need roof plumber to inspect job.
MSA-DCS | WA3351387 | Visits area - Fire Alarm is activating | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 29 May 2020 | 2020-05-30 14:46:42 | 2020-05-29 17:48:00 | Pass | Zn 81 in alarm on arrival. Found conv thermal head in constant alarm state. Replaced with new conv tyco thermal head and base. Alarm cleared.
MSA-DCS | WA3351389 | Gate house upstairs manitenance computer not working | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-12-10 15:08:00 | Fail | Installed replacement server, configured and tested OK.Job Complete
MSA-DCS | WA3351411 | Unit 2, B & D, Cleaning Room- light is faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-03 13:30:00 | Pass | Repaired faulty lights in unit 2 store rooms
MSA-DCS | WA3351423 | ERU HUT - weather strip on the main door has come off. | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-08-14 10:00:00 | Fail | Door replaced
MSA-DCS | WA3351440 | investigate a sink hole at unit 9 and 10 compound. | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | Pumps n Pipes | 1 | CLOSE | 29 May 2020 | 2020-05-30 16:17:04 | 2020-06-05 09:30:00 | Fail | NO CAUSE EVIDENT FOR HOLE, INSPECTED AREA, MADE SAFE AND CEMENTED IN HOLE TO MINIMISE/PREVENT FUTURE EROSION.
MSA-DCS | WA3351446 | Front Gate=- monitor screens not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 May 2020 | 2020-05-29 20:58:12 | 2020-06-23 10:20:00 | Fail | Investigated fault with CCTV displays.Corrected faults and tested OK.Job Complete
MSA-DFES | WA3350912 | Lvl 1, Dormitory - A/C Unit Dorm room 16, “Error” code flashing | CFRS Fremantle | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-04 09:00:00 | Pass | Unable to find a.c. with fault spoke to station captain and firefighter who's dorm it was and found out the unit had been replaced on the 2/06/20
MSA-DFES | WA3350958 | Major roof leaks in workshop area in Bay 4 - (photos to be emailed) | Fleet Management Services - O'Connor Workshop | GMP-BR | Roofing | Tiled Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-07-03 14:00:00 | Fail | Attended site and located leak, cleared gutters but will need to return to carry out repairs to the downpipe covers 2/6 Attended site and completed gutter cleaning, DAS report to be prepared 3/7 Removed old gasket and installed new one and resealed old joins. Job has now gone to quote for roof repairs RFQWA2580006
MSA-DFES | WA3351131 | Various locations light issues - see notes | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-25 11:30:00 | Fail | COMPLETED
MSA-DFES | WA3351209 | Toilet no.2, applied training grounds, Abultion block - the flush button is not working properly & | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 12:00:00 | Pass | Unable to repair buttons so fitted new uniset cistern and new flexi.
MSA-DFES | WA3351280 | Radio communciation - Ladies toilets, roof is leaking | DFES Regional Office - Belmont | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-07-14 13:30:00 | Fail | Located cause of leak, removed old lead flashing around roof and replaced with new, then resealed. Remove damaged ceiling, lights and smoke detectors and installed new ceiling, primed and painted. Re-installed lights and detectors. Cleaned site. Job complete
MSA-DFES | WA3351335 | Ambulant Toilet- sink tap is loose & water not draining properly | Armadale Regional Office | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-09 12:45:00 | Fail | Did up nut under mixer tape in bathroom tested and fixed issue. Checked drain and all clear
MSA-DFES | WA3351357 | Multiple leaks throughout the station | CFRS Maddington | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-06-10 09:45:00 | Fail | Attended site and located leak, unable to access the roof due to inclement weather. Will need to return when weather permits to complete inspection/repair Reattended and carried out repairs. Confirmed successful by site during next rain
MSA-DFES | WA3351439 | Tunic Room door coming off rail, it appears it needs new rubber stopper | CFRS Welshpool | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-07-02 14:15:00 | Fail | Attended site and inspected door. Door track has several damaged parts which will need to be ordered
MSA-DTAG | WA3350502 | Check mains power, PDU and surge protection in custody security rack-see notes | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | COMPFIN | 29 May 2020 | 2020-06-05 17:00:00 | 2020-06-02 15:00:00 | Pass | Lightning strike caused equipment failure in the Custody area data room. Checked electrical supply ok as equipment is still failing some weeks after the strike. All appears ok . Suggest fitting of surge arrestors in the switchboard and fitting power logger to check stability of electrical supply as a precaution.Job is not complete BRA sent 9.6.20
MSA-DTAG | WA3350505 | Upstairs Billi water unit tripping RCD | Supreme Court | GMP-BR-HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 May 2020 | 2020-06-05 17:00:00 | 2020-06-02 16:45:00 | Pass | Reported faulty Billi unit to Niall from Programmed and he will get it repaired under warrenty.
MSA-DTAG | WA3350531 | Custody NVR failed to record | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 29 May 2020 | 2020-06-05 17:00:00 | 2020-07-07 12:30:00 | Fail | Collected repaired NVR from supplier. Attended site. Installed NVR. Removed Loan Unit. Set up system. Synced allcameras to NTP server. Tested operation, all OK. All cameras recording and time synced.Job completed.
MSA-DTAG | WA3350784 | SAT building as having issues - Please see notes below | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 15:30:00 | Pass | Investigated reported faulty on Entry Door. Tested door, all working fine and opening as required. Tested schedule all programmed OK
MSA-DTAG | WA3350907 | Roofing - There is a water leak in the ceiling located in the stairwell entry by the Magistrate into | Joondalup Courthouse | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-09-04 14:08:00 | Fail | REPAIRS TO WATERPROOF MEMBRANE IN BOX GUTTER. REPAIRS TO LOCAL AREA IN RELATION TO LEAKS
MSA-DTAG | WA3350936 | Court 1 & 2-Keypad flashing different colours and behaving as if someone using it no one is near | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-26 08:00:00 | Fail | Replacement and testing of access control system batteries and PSU. Tested OK. While onsite customer asked us to look at card programming issue. SEME unable to rectify as cards as locked to SONTEC contractor.
MSA-DTAG | WA3350993 | Lvl 4, light next to the back TV in Court 42 that is flickering. | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-03 10:45:00 | Pass | Job complete
MSA-DTWD | WA3350774 | E Block, Level 2, Pavillion restaurant - Water leak behind bar | Joondalup Kendrew Campus | GMP-BR | Building | Internal Walls (BU) | M Construction (WA) | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-06-02 13:14:00 | Pass | Job complete
MSA-DTWD | WA3350797 | E block L2 External male toilet. Leak in ceiling above shower | Joondalup Kendrew Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 14:30:00 | Pass | Inspected ceiling void, gantry leg penetration over area of ingress, plit silicone arounf leg to flashing, clean and resealed . (Rain present during repair)
MSA-DTWD | WA3350798 | West side external, External roof - external walkway guttering leaking, opposite A and C block | Joondalup Kendrew Campus | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 15:30:00 | Pass | Box gutters between A + B and A + C blocks leaking (rusted)These are walkway gutters and 4 at 6m need changing and another smaller section.
MSA-DTWD | WA3350806 | Water leak from roof over motor control area | Clarkson Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 0 | CLOSE | 29 May 2020 | 2020-05-29 12:47:15 | 2020-05-29 13:15:00 | Fail | Leak above practice switchboards - shown wrong area initially. Leaking over second box, sealed along welded mean seam. Work was completed during rain so if it recoccurs it may need to be reattended.
MSA-DTWD | WA3350822 | H Block, HG01, Battert test area - roof leak water leaking onto test benches | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-08-10 12:00:00 | Fail | Works are now completed and the leaks have been repaired - confirmed leaks resolved
MSA-DTWD | WA3350824 | B block, BG21, technicians office - Roof Leak – Water running down wall and has flooded carpet | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-10-28 12:30:00 | Fail | Attended site and located leak, unable to access the roof due to inclement weather. Will need to return when weather permits to complete inspection/repair
MSA-DTWD | WA3350832 | C Block, CG08 Technician's Workshop - Roof leaking running down wall behind the drill press onto the | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 12:30:00 | Pass | Attended site and located leak, unable to access the roof due to inclement weather. Will need to return when weather permits to complete inspection/repair 16/6 BRAF has been submitted and we are now waiting on approval to proceed with the works
MSA-DTWD | WA3350838 | S block L1 S209 hot water unn tap fault | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-06-04 12:38:00 | Pass | Tap broken on arrival. Had trouble draining hot tank. Replaced RHEEM wall mount tap. Waited for RHEEM to fill up and be ready. Ran further tests.
MSA-DTWD | WA3350868 | G Block,GG03 Above centre work benches- Roof Leak water leaking onto centre work benches | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-07-21 10:00:00 | Fail | Works are now completed and the leaks have been repaired - We are waiting for next rain to confirm all is fixed 22/6 BRAF has been submitted and we are now waiting on approval to proceed
MSA-DTWD | WA3350886 | D Block, Storm water drain blockage – Creating flooding in walkway outside of ‘D1 Kitchen’ | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 18:00:00 | Pass | Fix stormwater issues job completed the 29/5/20
MSA-DTWD | WA3350926 | Lvl 3, Room B325- Control joint mastic is damaged | Perth Campus B6 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 29 May 2020 | 2020-06-08 17:00:00 | 2020-07-08 09:45:00 | Fail | Removed perished mastic and foam from control joint. Inserted new foam and sealed with Sikaflex. Returned to site and completed works: removed all perished silicone and foam from joints and renewed as per photos attached.
MSA-DTWD | WA3350946 | Lvl 1, Room B139- Faulty GPO | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 08:00:00 | Pass | Attended site, replaced faulty gpo in B6 B139. Tested all working properly.
MSA-DTWD | WA3350950 | E Block - Lock to front door of E011 is faulty | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 13:30:00 | Pass | Replaced lock & triple point kit
MSA-DTWD | WA3350952 | A block, AG07 - Security Access system is Gallagher, Unable to gain access to secured area, | Mandurah Campus (formerly Peel) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-22 11:26:00 | Fail | 03/06/2020, 830-1000 and 1515-1600electric strike faultyordered replacement partreplaced electric strike and tested ok
MSA-DTWD | WA3350960 | lassroom B19- roof leaks at skylight next to mulch hoppers | Murdoch Campus | GMP-BR | Roofing | Rooflights and Skylights (RF) | AWB Co. | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-06-02 13:30:00 | Pass | Investigated leak. cleaned out lap on sheets as were full of dirt and causing water to block up and pour in. sealed lap on joint up top, reinstated sheets
MSA-DTWD | WA3350961 | Classroom B24- roof skylights left of roller door from inside | Murdoch Campus | GMP-BR | Roofing | Rooflights and Skylights (RF) | AWB Co. | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-06-30 13:15:00 | Fail | Sourced leak and found leaking in through joints. Skylight is old and needs replacement - measuredup .may need BRAF depending on prices. Picked up materials and returned to site, existing sheet was heavily glued and had to pry/cut silicone away to remove sheet. Cleaned caps and installed new sheet, needed third man to assist installation due to heavy winds and safety concerns as it is in a public area.
MSA-DTWD | WA3350966 | E Block, Room E70- Water coming through light fitting | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-06-04 08:15:00 | Fail | Removed water damaged light from E70 as requested by site . Job completed
MSA-DTWD | WA3351035 | Faulty weather seal to wooden external door – rain flooding in under door | Armadale Campus? 45 Commerce Ave | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-06-02 16:21:00 | Pass | See notes
MSA-DTWD | WA3351044 | Faulty seals to double doors off student kitchen – rain coming in | Armadale Campus? 45 Commerce Ave | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-07-14 15:15:00 | Fail | Adjusted doors back into frame so they are now square and sealed. Job complete
MSA-DTWD | WA3351046 | E Block, Room E70- Roof leaking through light fitting | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-03 13:00:00 | Pass | Works are now completed and client has confirmed repairs are watertight
MSA-DTWD | WA3351059 | ground various locations-Several car park lights are not working. | Bentley Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-07-24 18:17:00 | Fail | Repalced 6x faulty street light fittings with new. 4x supplied by site . Sissor lift was required . Couldn’t get sig slip signed or pic of sign in book as admin was locked only security on site
MSA-DTWD | WA3351106 | F Block, Room F102, shower facility- Toilet is leaking | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 14:00:00 | Pass | Complete
MSA-DTWD | WA3351194 | Cafe - Tap is broken and could possibly burst | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 29 May 2020 | 2020-05-29 16:53:26 | 2020-05-29 15:17:00 | Pass | Complete
MSA-DTWD | WA3351298 | Childcare- Toilet pan floor & bowel seal perished & leaking | Rockingham Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 13:00:00 | Pass | Replace pan cone and flush pipeEmailed sign slip took much earlier much didn’t get response
MSA-DTWD | WA3351301 | Childcare- Toddler room entry door handle faulty | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 12:05:00 | Pass | job completed - replaced
MSA-DTWD | WA3351314 | A block, Room A52A- Water leaking into Plant room & on to staircase Admin | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-04 13:00:00 | Pass | Plant room/admin staircase. Persistent problem, plantroom top floor found multiple floor cracks which had Previously had works done, found first level plant room with water marks all around vent system. Would Recommend water proofing top level professionally. Also recommend custom flashing along low level wall
MSA-DTWD | WA3351324 | G block, Admin - Emergency lighting C/B has tripped and won’t reset | Rockingham Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-03 13:30:00 | Pass | Attended site and signed in. Located Circuit breaker and tested. All seem to be working fine. Identified possible cause of issue. No faults detected.
MSA-DTWD | WA3351432 | A Block - Down pipes are blocked on roof – need to be cleared | Bentley Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-03 14:30:00 | Pass | Works are completed and blocked downpipes now cleared
MSA-DTWD | WA3351437 | B Block,BG11, Valspar Paint Mixing Room- Water leaking through roof filters for extraction system | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-11 12:00:00 | Fail | Downpipe blocked with old silicone tube plus rag. Downpipe unblocked and sealed with new silicone. Site confirmed leak resolved
MSA-MRWA | WA3350988 | L8 room 804 Leak above work station 804, investigation has revealed a corroded pipe | Don Aitken Centre MRWA Head Office | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 29 May 2020 | 2020-06-02 17:00:00 | 2020-05-29 13:30:00 | Pass | Roof plumbers to be contracted for repairs
MSA-MRWA | WA3351418 | northern men’s toilet - smell from urinals, cartridges need replacing | Road Network Operation Centre (RNOC) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 May 2020 | 2020-06-04 17:00:00 | 2020-06-02 14:00:00 | Pass | Replace cartridges to waterless urinals north male toilets
MSA-DCS | WA3351507 | Perimeter fence, Tamper system is down, also zone 5 and 15. | Karnet Prison Farm-Main Complex External Area | SPA-BR | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 May 2020 | 2020-05-30 17:18:31 | 2020-06-19 13:24:00 | Fail | Sourced parts, attended site, found multiple intermittent x and y data faults on perimeter network.Replaced multiple fibre-optic patch leads. repaired multiple comms faults.Replaced faulty fibre-optic communication board.monitored perimeter for correct operation and tested OK.Job CompleteParts used:Multiple fibre patch leadsSenstar communication PCBConsumables
MSA-DCS | WA3355176 | ** Job already attended too** wiring to buggy’s puled out of walls | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 May 2020 | 2020-05-31 07:00:00 | 2020-05-30 19:30:00 | Pass | Repaired damaged buggy charger lead.
MSA-DCS | WA3351576 | Main Kitchen- Fault on fire panel. keeps going into alarm. | Karnet Prison Farm-Prisoner Accommodation Huts Unit 1 | GMP-BR- HO | Building | Materials (BU) | Automatic Fire Protection (ARA) | 0 | CLOSE | 31 May 2020 | 2020-05-31 13:59:39 | 2020-05-31 12:45:00 | Pass | 31/5 Karnet Prison FarmL4S51, zone monitor in unit 1 kitchen causing continual false alarms. Traced alarm back to cool room detector that had been knocked loose from ceiling allowing condensation build up during defrost cycle. Remounted and cleared out standing water. Alarm cleared and did not return. System normal at time of departure
MSA-DCS | WA3354054 | Unit 1- one of the main monitors in the control room is not working. | Hakea Prison-Unit 1 | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Jun 2020 | 2020-06-01 12:27:08 | 2020-06-01 11:00:00 | Pass | Unit 1 screen not displaying cameras. 2nd screen of cameras hiding behind layout so reset layouts and now all is working. Showed staff how to locate windows when they may have been accidentally closed or monitor resets.
MSA-DCS | WA3354498 | Zone between B2 and B3 wasn't showing secure and needs to be investigated. | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Jun 2020 | 2020-06-01 16:56:51 | 2020-06-01 16:30:00 | Pass | B2 & B3 not showing secure. B2 and B3 are secure upon arrival. B2 was in environmental alarm 31/5/2020 20:22. Checked and zones were alarming through night in logs. Tested operation today and zones are reporting correctly with audible alarm as well.
MSA-DTWD | WA3701067 | D block, DG06 - oil leaking from hoist nearest to door - Retrospective W/O - do not re-attend | Carlisle Campus | GMP-BR | Equipment | Electrical Equipment (EQ) | Precision Automotive Equipment/Bapcor | 2 | CLOSE | 01 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-03 14:00:00 | Pass | job completed - REFIT HYD RAM, BLEED & TEST
MSA-DCA | WA3355653 | boiler room - water leak on boiler 2 | Collection and Research Centre Welshpool-External Area-Ground Floor-Boiler Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-03 17:30:00 | Fail | Please refer to work logs.
MSA-DCA | WA3355720 | Bollards, James street - aren’t dropping for incoming vehicles | Perth Cultural Centre Precinct-James Street Amphitheatre -Ground Floor | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-03 16:59:00 | Pass | Remote card was not recieveing signal, moved antenna connection to " GO DOORS " Remote card and all was fixed
MSA-DCS | WA3354709 | Unit 3, A Wing Dayroom - Roof Leaking | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-07-22 15:00:00 | Fail | REPAIRED BOX GUTTER AND SHEETING. CLEANED GUTTERS
MSA-DCS | WA3354711 | Metal Shop, Workshop - Roof Leaking | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-10-02 15:00:00 | Fail | ROOF LEAK SOURCES LOCATED & REPAIRED
MSA-DCS | WA3354713 | Staff Toilet Outside Security In Main Admin- Cistern Leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-04 11:45:00 | Pass | Pulled apart cistern replacing outlet washer
MSA-DCS | WA3354715 | Unit 3, Cell D15- toilet is cracked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-04 13:48:00 | Pass | Removed old toilet replaced with new
MSA-DCS | WA3354721 | Unit 2, Cell B6- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-04 10:30:00 | Pass | Replaced light switch
MSA-DCS | WA3354722 | Unit 8, Right hand store room- Floor has given way | Hakea Prison | GMP-BR- HO | Flooring | Concrete (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2021-03-02 14:13:00 | Fail | ADVISED TO CLOSE OFF COST TO DATE - PRISON WILL RE ISSUE A NEW JOB ONCE THEY DECIDE WHEN AND IF THEY ACTUALLY WANT THIS JOB DONE
MSA-DCS | WA3354736 | Cell call 1.06b red light is constantly on- Alarm does not work when cell call button pushed | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 06:59:49 | 2020-06-02 08:00:00 | Pass | Contacted site and had site reset austco 3210 and retested cell calls. All had reset and tested ok. Job complete
MSA-DCS | WA3354750 | ISU (Harding)- A & C Wings- Both roof's leaking from under new installed air-con units | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-07-08 14:30:00 | Fail | REPAIRED ROOF SHEETING AND FLASHING - SEALED
MSA-DCS | WA3354753 | Lenard, B Wing, Cell B02- Observation window damaged | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-05 13:45:00 | Fail | OBS WINDOW REPLACED
MSA-DCS | WA3354756 | Jasper B, Cell B08- Samshed observation window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-05 13:00:00 | Fail | OBS WINDOW REPLACED
MSA-DCS | WA3354760 | Jasper B Wing Kitchen- Sink taps damaged | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-03 15:07:00 | Pass | Replaced sink set
MSA-DCS | WA3354766 | Admin Comms Room not responding as per the below faults | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 11:20:50 | 2020-06-02 15:30:00 | Fail | Replaced power supply
MSA-DCS | WA3354774 | Staff Tearoom- Door has dropped affecting lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-08 10:00:00 | Fail | Supplied and installed parts
MSA-DCS | WA3354780 | Admin, Barista- Window seals leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-12 13:30:00 | Fail | WINDOWS RE SEALED
MSA-DCS | WA3354809 | Unit 7, Cell H4- Outside light switch gave staff small electric shock | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 07:38:42 | 2020-06-03 10:30:00 | Fail | Electric shock report
MSA-DCS | WA3354815 | Zone A4- Low battery voltage | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 11:00:00 | Pass | Found fault with backup battery in A4 power fence controller. Replaced with new battery and load tested. Cleared alarm on controller and on Gallagher PC. Zone tested by SOG personnel. Parts used:12V 7AH battery
MSA-DCS | WA3354819 | Unit 7, H22 & E Wing cleaning cupboard- Electrical faults as per below | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-04 15:00:00 | Pass | Replaced gpo and light switch
MSA-DCS | WA3354852 | Unit 3, Cell C9- Window needs fixing not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-07-01 10:15:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3354857 | Unit 3, Cell B6- Window needs fixing not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-07-01 13:30:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3354858 | U8 fire alarm Vesda fire alarm continuously goes off during night even after reset | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 08:08:00 | 2020-06-02 10:08:00 | Pass | Unit 8 in intermittent airflow fault. Pipe 1, B wing, at 55%. Cleaned out all sample points. Airflow returned to normal.
MSA-DCS | WA3354859 | Unit 3, Cell C5- Window needs fixing not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-07-01 11:00:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3354862 | Unit 5, Cell C6- Window support damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-22 09:45:00 | Fail | RENEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3354867 | Unit 14, Cell A12- Top cell call button not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-02 14:30:00 | Pass | Speaker covered with clear tape and stickers. Removed tape and cleaned intercom. Tested to control. Audio loud and clear in control and in the cell. Both master and Slave intercoms tested ok.
MSA-DCS | WA3354868 | Unit 2 - B & D Light not working in Cell D2 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-04 23:30:00 | Pass | Repaired faulty lights in unit 2 d2
MSA-DCS | WA3354880 | Unit 1,B Wing, Cell B3 & B7- Tap is faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-30 14:00:00 | Fail | Removed tap from basin. Installed new locking nut and remounted. Connected pipework and tested
MSA-DCS | WA3354885 | Unit 14, Cell D4- Shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-03 13:58:00 | Pass | Used acid and plunger to clear blockage in shower
MSA-DCS | WA3354886 | SOG-main duty desk gallager security some of the camera's off line | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 08:20:03 | 2020-06-05 09:45:00 | Fail | completed under warranty no costs, as advised of vendor.
MSA-DCS | WA3354888 | Unit 5, Cell A8- Lock is faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-10 12:30:00 | Fail | Replaced cylinder to repair lock.
MSA-DCS | WA3354891 | Unit 5, A Wing- Regi Oven Faulty, making loud humming noise when turned on. | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-05 13:00:00 | Pass | Checked oven
MSA-DCS | WA3354896 | Unit 2, Cell D13- Observation Window Smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 08:27:42 | 2020-06-02 12:00:00 | Pass | obs window renewed
MSA-DCS | WA3354901 | Unit 6 - A Wing A11 Door lock sticking. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-03 12:00:00 | Pass | Replace door plate and lock.
MSA-DCS | WA3354919 | MPU (8) - M10- Viewing window has been broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-05 12:30:00 | Pass | OBS PANEL REGLAZED
MSA-DCS | WA3354961 | All NVR are down on site | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 12:57:41 | 2020-09-16 16:05:00 | Fail | Identified issue with NVR5 not recording correctly. Investigated operating system and suspect indigo software has memory issues which are causing the OS to restart the service intermittently around every 12 hours. Upgraded licence on NVR6 and transferred all recordings from NVR5 to NVR6. Removed NVR5 and returned to manufacturer for repair. Manufacturer could not find any fault and suspect the software on NVR5 may have a glitch with one of the cameras on site. Returned NVR to site, reinstalled and configured to record visits cameras only. Visits cameras are also being recorded on NVR6.Job Complete
MSA-DCS | WA3354971 | Unit 5, A1 - please repair light on top bunk, not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 13:30:00 | Pass | Repaired faulty lights in unit 5 a1
MSA-DCS | WA3354972 | Unit 4, Cell A11- Leaking sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-02 12:00:00 | Pass | Retightened leaking fitting underneath basin in cell. Tested
MSA-DCS | WA3354980 | CCU (11), D Wing, Cell D4- toilet is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-18 13:00:00 | Fail | Plunged toilet to clear blockage.
MSA-DCS | WA3354982 | Unit 5 - C8 window support faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-22 10:30:00 | Fail | RENEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3354984 | Unit 5, A12 - Window support is broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-22 13:00:00 | Fail | RENEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3355000 | Unit 1, Cell D12- Observation light is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-04 13:00:00 | Pass | Repaired faulty lights in unit 1 d12
MSA-DCS | WA3355005 | Unit 13, A wing -here is hole in the brock work in cleaning room. | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-30 13:30:00 | Fail | hole repaired & re tiled
MSA-DCS | WA3355009 | Abbiator chlorine plant- not dosing chlorine | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 09:13:45 | 2020-06-02 16:00:00 | Pass | Attended site and found that both chlorine bottles were empty. The site was also in full vacuum and reading zero ppm chlorine residual.Both bottles changed and scales reset to 70kg. The plant was switched back to auto and system was set to dose @ 450g/h
MSA-DCS | WA3355015 | Unit 5, C13 - Window support needs repairs/replace, broken faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-22 12:00:00 | Fail | RENEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3355018 | Unit 5, A6 - Personal lock is broken | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-10 11:00:00 | Fail | Replaced plate, lock and barrel
MSA-DCS | WA3355023 | Unit 14, B Wing, Cell B13- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-03 13:53:00 | Pass | Used plunger to clear blockage in basin.
MSA-DCS | WA3355024 | jasper unit damage flus and vents on roof | Banksia Hill Detention Centre | WSM-BR-RC | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 13:20:06 | 2020-07-17 12:42:00 | Fail | REPAIR VENTS, FLUES, FLASHINGS AND SHEETING ROOF
MSA-DCS | WA3355027 | Indsustries Admin, Barber shop door- Lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-30 10:00:00 | Fail | Reinstall lock and temp. repair.Attend site replace lock and install custom thickness over size strike.
MSA-DCS | WA3355029 | Jasper unit damaged windows to unit | Banksia Hill Detention Centre | WSM-BR-RC | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 13:23:14 | 2020-07-07 10:21:00 | Fail | Re-glazed and applied sec film to 42 windows
MSA-DCS | WA3355033 | Jasper unit damge to electrical works | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 13:25:01 | 2020-07-06 09:00:00 | Fail | Ordered Diffuser, when ready picked up and supplied to site
MSA-DCS | WA3355038 | Control room - in front of sally port, screen saying unsecured area | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 13:26:47 | 2020-06-02 15:00:00 | Fail | Attended site and found microfonics zone 23 constantly activated. Inspected cabling and all checked ok, found controller located in Hakea side. Found controller and tested controller, controller was freezing and causing issues, reset controller and tested and of line resistance. All tested ok and controller working ok, tested alarms for an hour and all had tested ok with no issues on controller. Job complete
MSA-DCS | WA3355043 | Unit 14 - B7 Cell call not clear enough. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-04 15:27:00 | Pass | Removed intercom. Stripped and cleaned. Cut off and recrimped RJ45 connector. Assembled intercom and secured. Tested, audio is loud and clear in the cell and in control. Slave point tested ok. Parts used:Consumables
MSA-DCS | WA3355092 | Camera 43 will not function | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 09:50:59 | 2020-06-02 13:00:00 | Pass | Attended site.Checked MAXPRO system.Checked wiring on PTZ camera 43 in EC 2.Checked fibre link from EC cabinet 2 to equipment room in Gatehouse.Found rodents damaged fibre patch lead.Replaced with new 2m ST-ST OM1 Multimode Fibre optic cable ( supplied by SEME).Tested.All ok at departure.
MSA-DCS | WA3355117 | Unit 3, end pod veranda walk way has couple leaks | Wooroloo Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-11-25 09:00:00 | Fail | REPAIRS MADE TO GUTTERS & DOWN PIPES TO CORRECT LEAKS
MSA-DCS | WA3355131 | Large sally port gate is not opening/closing, not responsing | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 14:11:53 | 2020-06-02 14:15:00 | Fail | Travel to and from NON METRO site. Inspect right hand side larger main entry gate. Found the inner PE has moistureblocking the lens. Clean and test, all okay. Test operation several times, all okay.
MSA-DCS | WA3355177 | Amenities (rear end) burst water pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-02 13:24:00 | Pass | Investigated. Collected materials. Isolated water. Exposed pipework. Repaired damaged valve and pipework. Tested and backfilled.
MSA-DCS | WA3355193 | Lvl 4,work stations W4.31 & W4.40- light is flickering | Westralia Square | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-05 17:00:00 | Pass | Replaced failed lamps and starters
MSA-DCS | WA3355274 | SOG base old training shed - Old training shed roof damaged in the storm | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 11:11:01 | 2020-06-15 13:15:00 | Fail | ROOF (STORM) DAMAGE REPAIRED
MSA-DCS | WA3355281 | Kitchen- no power to dishwasher | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 09:30:00 | Pass | Investigate and repair power to dishwasher
MSA-DCS | WA3355284 | Unit 1, Cell C8- Light switch smashed | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 11:23:13 | 2020-06-02 15:00:00 | Pass | Replaced gpo repaired light
MSA-DCS | WA3355292 | Unit 1, Cell B15- toilet is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 11:25:53 | 2020-06-02 13:56:00 | Pass | Drain machine to unblock drain removing bed sheet
MSA-DCS | WA3355305 | Unit 1, B Wing Showers- Middle shower blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 11:27:17 | 2020-06-02 15:58:00 | Pass | Unblocked shower removing clumps off hair
MSA-DCS | WA3355312 | Unit 4 - B wing first shower not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-08 08:00:00 | Fail | Replaced split pin and flushed restrictor in shower head.
MSA-DCS | WA3355314 | Education, Patio area of art room - Skylights damaged | Casuarina Prison | GMP-BR- HO | Roofing | Rooflights and Skylights (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-09-04 14:16:00 | Fail | REPLACE POLYCARBONATE SHEET
MSA-DCS | WA3355353 | Unit 1, B Wing, Cell B1- Sink P trap pipes are cracked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-10 14:45:00 | Fail | COMPLETED
MSA-DCS | WA3355354 | Unit 4, Footpath overhead lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-10 13:30:00 | Fail | Replaced 4x led flood lights
MSA-DCS | WA3355355 | Unit 1, external path lights facing unit 2 not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-07-01 10:00:00 | Fail | Replaced wall lights
MSA-DCS | WA3355356 | Recreation- globes/driver to recreation library & passages lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-10 12:00:00 | Fail | Replaced downlights with LEDs
MSA-DCS | WA3355358 | Staff Carpark- kerbing is broken | Bandyup Prison | GMP-BR- HO | Paving & Roadworks | Paving (PR) | Schlager Construction Group | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-24 11:30:00 | Fail | Removed damaged concrete kerbing and disposed off.Supplied and laid new concrete kerbing where required.Backfield soil and cleaned work areas.
MSA-DCS | WA3355364 | Unit 10, A8 - leaking tap, water going under spout and dripping ono floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-05 15:35:00 | Pass | Resilconed basin waste/trap
MSA-DCS | WA3355388 | Unit 10, B11 - sink requires reattaching to wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 12:26:09 | 2020-06-02 17:58:00 | Pass | Replaced broken basin
MSA-DCS | WA3355460 | CCU, office - Camera (monitor 4) needs attention as showing incorrect image | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-11 10:00:00 | Fail | Monitor 4 displaying a quad image within a quad image. Traced fault to Maxpro subrack card. Repaired and tested ok. Parts used:Coax T pieceConsumables
MSA-DCS | WA3355497 | Kitchen- Brat pan not switching on | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-12 10:30:00 | Fail | Kitchen, Brat Pan not switching on. Check pan & controls. Found main thermostat to be faulty. Over temp safety cutout faulty. Replace thermostat & overtempt cut out. Assemble & test.
MSA-DCS | WA3355501 | Metal Shop- Damaged power point | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-03 11:00:00 | Pass | Replaced 6 damaged 3 phase plug tops
MSA-DCS | WA3355504 | Unit 4, Cell 35- Window rollers damged | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-07-15 09:00:00 | Fail | NEW ROLLERS FITTED
MSA-DCS | WA3355523 | Kitchen, Staff Smoking Area External Zone Gate- Grill Lock Jamming When Opening | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 13:14:36 | 2020-06-15 09:20:35 | Fail | Grille lock service completed
MSA-DCS | WA3355559 | Medical centre, room 6 - ceiling light fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-03 12:30:00 | Pass | Replaced faulty lamps and leave stock onsite
MSA-DCS | WA3355593 | Unit 3, Service duct - door lock unable to unlock, please repair/service duct door | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 10:45:00 | Pass | Replaced bolt
MSA-DCS | WA3355607 | Kitchen back door - door dropped and lock out of line | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 14:07:30 | 2020-06-03 13:45:00 | Pass | Rehung internal screen door (Kitchen back door) to clear new flooring.
MSA-DCS | WA3355611 | Unit 2, D Wing, Cell D7- Personal lock on cell has completely come off | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-04 11:00:00 | Pass | replaced lock
MSA-DCS | WA3355614 | Gate House - Door 3 not closing properly with door closer piston/adjust /repair | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-04 13:15:00 | Pass | Adjust door closer
MSA-DCS | WA3355662 | Main Entrance Road - Fill in all Pot Holes Leading up to Staff Car Park and Main Gate | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Concreting (PR) | AFD Contracting | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 14:55:58 | 2020-06-03 12:00:00 | Pass | 03/06/20repaired pot holes in road to main gate and staff car park
MSA-DCS | WA3355666 | Unit 1, B5 & A3 - Prisoners Report Getting Shocks from Taps & Door | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 15:12:22 | 2020-06-04 08:30:00 | Fail | Electric shock report
MSA-DCS | WA3355687 | Unit 10, B wing - water coming from the ceiling between cell B2 & B5 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 19:35:17 | 2020-06-02 20:00:00 | Fail | Repair burst in roof of unit 10
MSA-DFES | WA3354908 | Fire fightiers office key cabinet cannot be secured | Butler Career Fire Station | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-02 11:30:00 | Pass | pack out electric strike so lock can latch properly
MSA-DFES | WA3354921 | front security gate is not opening or closing | CFRS Maddington | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-02 10:15:00 | Pass | Technician attended the site of Maddington Fire Station front security gate W21772 on 02/06/2020. Turned off power, checked cables and did up all loose cables.Cleaned track and safety. Turned up checked operation if gate via push button 30 to 40 times without any problems. Full test and inspection of gate components completed prior to leaving site.
MSA-DFES | WA3355077 | Various blown light bulbs/fluorescents throughout entire station | CFRS Welshpool | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-25 16:30:00 | Fail | Complete
MSA-DFES | WA3355183 | Kitchen, Filter under the sink is leaking water | CFRS Maddington | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-02 14:40:00 | Pass | Leaking from top of housing. No damage evident to cause leak. Removed cleaned, lubed and reinstalled o’ring. Re positions pressure valve. On test for 10mins and no leak.
MSA-DFES | WA3355212 | Engine room door number 3, green light not operational | CFRS Murdoch | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-07-13 13:00:00 | Fail | Technician attended the site of Murdoch Fire Station Engine Room Door 3/W22123 on 03/06/2020. Following full test and inspection of door components identified fault was green strobe light not working to engine room door 3. Tested for voltage which was ok, after doing so the light began working for a few moments before stopping again, recommended replacing light. Could be the water has got into this one and is causing it to fail, can see corrosion marks on the inside of fitting. 13/07/2020. Returned on site and replaced green strobe light.Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3355238 | Kitchen - Main air conditioning unit will not turn on | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-03 09:00:00 | Pass | Attend site. Access bunker and check AC unit. Found not responding to on/off switch. Access rooftop and check unit. Check unit controls and found control circuit breaker tripped. Reset circuit breaker and found unit to start. Check operation of unit and found to work as normal. Monitor operation and cycle unit on and off. Unit working as normal. Possible cause being power issues previously.
MSA-DFES | WA3355253 | Rear Gate- Remote Control for the station rear gate is unserviceable. | CFRS Perth | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 11:45:00 | Pass | Technician attended the site of Perth Fire Station entry gate to rear compound A40352107B on 09/06/2020. Following full test and inspection of components identified that the remote was faulty, unable to be coded in. Supplied and coded 3 new remotes for entry gate.Carried out full test of operation ok.Full test and inspection of gate components completed prior to leaving site.
MSA-DFES | WA3355339 | Rear Engine room under awning 1 Fluro light (2tubes) lights not working | CFRS Daglish | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 08:45:00 | Pass | competed
MSA-DFES | WA3355357 | There are 5 light fittings that require replacement fluorescence globes | DFES Regional Office - Joondalup | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-04 14:45:00 | Pass | Fixed 5 x fluro lights throughout building
MSA-DFES | WA3355466 | Electric Fence behind Dome 2 (Buses), approximately 4 Insulators have broken off and need replacing. | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-11 12:30:00 | Fail | Replaced broken insulators with new
MSA-DTAG | WA3354838 | DMJC as unable to open doors via unison from our control room | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 02 Jun 2020 | 2020-06-02 11:57:39 | 2020-06-02 08:30:00 | Pass | Restarted workstation and checked all functions
MSA-DTAG | WA3355086 | Executive Managers Office- Door stop has broken, small rubber door stop at bottom of door | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-03 09:00:00 | Pass | Door stop replaced
MSA-DTAG | WA3355230 | hay street door stays open for 40 seconds , time needs to be changed. | State Administrative Tribunal (SAT) | GMP-BR-HO | Building | Automatic Doors (BU) | Sapio Pty Ltd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-02 12:30:00 | Pass | Intermittent door to be serviced. No fault with access control.Job completed.
MSA-DTAG | WA3355400 | Various levels - saying the air-conditioning is too cold. | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-03 10:30:00 | Pass | Attend site. Building too cold. Access plantroom and check bms. Found boilers not operating. Check roof plant boilers and found no gas supply. Access lower ground floor gas valve and found to be tripped. Reset mains gas supply. Access lev 6 bms and found boilers to now start. Monitor temps and found supply air temps to reach desired setponit. Heating is working correctly.Return to site. Confirm main gas valve still on and boilers are working correctly. Building temperature is satisfactory.
MSA-DTAG | WA3355473 | Garden grounds to the side of main entry - Limstone Fence damaged | Joondalup Courthouse | WSM-BR-SITE | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-07-22 15:00:00 | Fail | MISSING BLOCK REPLACED
MSA-DTAG | WA3355550 | SAT cameras dropping in and out from a live view | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-03 13:30:00 | Pass | Reset both Recorder Servers. SAN Unit will not communicate with Recorders correctly. Problem with Raid Controller Module.
MSA-DTAG | WA3355699 | L5 court 58 Flashing light | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-05 08:30:00 | Pass | Job complete
MSA-DTWD | WA3355039 | E Block, ET02 Classroom- Fault lock on door | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-05 13:55:00 | Pass | ET02 - lock faulty.Lock repaired
MSA-DTWD | WA3355055 | Level 2, Male shower - repair damaged shower tile wall | Perth Campus B5 | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-10 18:00:00 | Fail | Complete
MSA-DTWD | WA3355099 | P block ground alarm panel showing low battery, can not set | Joondalup McLarty Campus | GMP-BR | Air Conditioning | Materials (AC) | BJ SYSTEMS | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-16 15:15:00 | Fail | Zul Isnin (02/06/2020) - Work NoteArrive on site, sign in for access keys/card. Dave has gone home, no access to McLarty site. Follow up job work history for P Block AdminZul Isnin (16/06/2020) - Work NoteSign and key access Joondalup site, drive to McLarty North Metro. Install power supply, power supply cabinet, replace with new backup battery. Run cabling for power supply to panel. Run extension lead power from GPO. Terminate battery output power in panel terminal. Bridge AC power. Download site Challenger database P Block Admin. Check and clear mains/battery alarms, confirmed with Monex monitoring, ok
MSA-DTWD | WA3355151 | Faulty padlock to main gate – foreign object in lock | Armadale Campus? 45 Commerce Ave | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-02 11:23:00 | Pass | Padlock to main gate faultyPadlock repaired.
MSA-DTWD | WA3355160 | D block D 105 / D 104-Hand basin taps leaking. in both areas | Leederville Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 13:30:00 | Pass | Complete
MSA-DTWD | WA3355166 | Building, 6D31 Workshop - gutter leak | Thornlie Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 12:30:00 | Pass | BRAF Declined - As per Dom Gileno have closed off job and charged costs to date
MSA-DTWD | WA3355184 | Water leak in west end passageway near skylights | Thornlie Campus | GMP-BR | Roofing | Rooflights and Skylights (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-25 15:30:00 | Fail | sealed roof leak with roof and gutter silicone
MSA-DTWD | WA3355219 | Block B1- Security DGP 11- Battery faulty | Perth Campus B1 | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 09:47:00 | Pass | 08/06/2020, 845-915Replaced backup battery in dgp 11. Cleared ok.
MSA-DTWD | WA3355220 | E block E012 lock is faulty | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-02 13:10:00 | Pass | Serviced lock to E012
MSA-DTWD | WA3355250 | Back of the building - Graffiti at the back of building | Perth Campus B1 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 09:30:00 | Pass | REMOVAL OF GRAFFITI FROM BACK OF BUILDING
MSA-DTWD | WA3355319 | level 3, A319 - Repair leak in A319 training room | Leederville Campus | GMP-BR | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-08-05 11:31:00 | Fail | REPAIRS TO VARIOUS AREAS - REQUIRING BOOM LIFT
MSA-DTWD | WA3355331 | A block foyer - ceiling damage, Box guttering above ceiling in A block appears to be leaking | Mandurah Campus (formerly Peel) | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 02 Jun 2020 | 2020-06-03 17:00:00 | 2020-08-20 14:15:00 | Fail | Attended site and located leak, have carried out repairs, will need to assess during next rain before returning to repair water damage to the ceiling - Confirmed with Martin on site that the leak has been resolved. Will prepare BRAF to repair ceiling 6/8/20
MSA-DTWD | WA3355346 | E block E400 (Main north door)Sliding door difficult to open | Midland Campus | GMP-BR | Building | Automatic Doors (BU) | AWB Co. | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-07-10 15:00:00 | Fail | Sign inLocate doorLarge workshop doorsGuides filled with rubbishGuide rails rusted and worn away in slabGuide on door worn away over time and useCleaned out guide and remove rubbishOrganised to get NWSM out to site to inspect and give quote for replacing guides and carriages to 4 doorsWaiting to hear back and confirm to raise BRAF (Quote came in below PO value so no BRAF necessary)Informed siteSpecialists attended site to make repairs.
MSA-DTWD | WA3355347 | Investigate site for possible water leak as advised by the Water Corporation | West One Services | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-29 17:00:00 | Fail | Complete
MSA-DTWD | WA3355382 | carpark 2 - Broken branch overhanging the Childcare Centre Playground shade cloth | Thornlie Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 08:32:00 | Pass | STORM DAMGED BRANCHES REMOVED3 STAFF @ $100 PER HOUR MIN $3002 VEHICLES $200 PER HOUR MIN $200
MSA-DTWD | WA3355551 | Lvl 3- Roof leak above A Block Stairwell | Leederville Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-09-15 09:00:00 | Fail | SOURCE OF LEAK LOCATED & REPAIRED - MULTIPLE VISITS
MSA-DTWD | WA3355564 | Muresk Hall BLD 831- 3 single back doors Push bars faulty | Muresk Institute | GMP-BR | Building | Doors (BU) | Lee Carpentry | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 10:30:00 | Pass | Adjusted door
MSA-DTWD | WA3355657 | Room B40 Student Zone - a water leak coming from the light fitting (near vending machine) | Murdoch Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-05 15:15:00 | Pass | Checked lights in B40. No electrical fault found. Site advised it’s a roof leak.
MSA-DTWD | WA3355658 | store room A1 ceiling leak | Murdoch Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 02 Jun 2020 | 2020-06-05 17:00:00 | 2020-07-10 12:30:00 | Fail | Detected leak, rremoved large amounts of debris from roof, lifted flashing and removed debris. Measured up for new apron flashings + capping flashings BRAF APPROVEDSourced materials and delivered to site - installed all new custom flashings to area that was leaking. Removed waste from site.
MSA-DTWD | WA3357122 | Campus Grounds- Sink hole next to cycle rack block 1 | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 02 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-17 13:33:00 | Fail | Sink hole we think happened over a long time and from previous issues and ground not back filled properly Expose whole areaBackfill Wait for rain Remove fences
MSA-DCA | WA3356686 | Disable Toilet blocked | PICA-Main Building-Level 1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-03 16:10:00 | Pass | unblocked toilet
MSA-DCS | WA3355971 | Kitchen, Rational oven faulting (service 12) | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 03 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-03 08:00:00 | Pass | Rational oven faulty (service 12). Check oven & controls. Dismantle, clean electrodes, replace control filter & flap care container. Recalibrate controls & test.
MSA-DCS | WA3355979 | Unit 6, Cell B4- Toilet not flushing & continually running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 03 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-19 11:05:00 | Fail | repaired leaking toilet
MSA-DCS | WA3355980 | Unit 6, Cell D5, D6, D7 - Leaking Taps | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 03 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-12 11:24:00 | Fail | Reseated and replaced x3 washers , valves
MSA-DCS | WA3355994 | MPU/SPU- Unit haa multiple fluro globes faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-10 14:30:00 | Fail | Repaired multiple faulty lights in mpu day rooms and corridors
MSA-DCS | WA3355998 | Unit 1, B & D, Cell D10- Toilet button not operating | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-23 11:00:00 | Fail | Cleaned debris and paint from around button, preventing it from operating correctly.
MSA-DCS | WA3356004 | Bakery - broken copper pipe/leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-03 13:34:00 | Pass | Investigated job. Collected parts. Repaired and replaced broken pipework. Tested
MSA-DCS | WA3356085 | Unit 4A pod 1 verandah lights not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-11 12:30:00 | Fail | Replaced faulty light fittings
MSA-DCS | WA3356159 | Bakery - Workshop Bakery proover power box wet after pipeburst please check for safety before use | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-04 14:00:00 | Pass | Dried out water logged proover control box. Returned and commissioned. Reset time clock and tested
MSA-DCS | WA3356175 | Amenities, Showers - No hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 14:30:00 | Pass | Investigated. No issue found. Water at correct temp.
MSA-DCS | WA3356177 | Amenities no hot water in kitchen in amenities area at the front of the prison | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 14:34:00 | Pass | Investigated. No issue found with hot water.
MSA-DCS | WA3356187 | Perimeter, zone 3 & 5 - constantly going into alarm in the master control room | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 09:15:20 | 2020-06-03 11:30:00 | Pass | Attended site and checked FlexPS system.Found that internal MX zone 3 and external MX zone 5 are in constant alarm.Checked FlexPS controllers in perimeter cabinets 2 and 3.Checked microphonics cable for any damage and replaced missing cable ties.Found damaged splice kits in both zones and disconnected wires on third.Replaced damaged 2 splice kits with new (supplied by SEME) and reconnected wires on third.Checked EOL resistor on both zones - 0.98 MOhm.Conducted test.All back to normal and operational.
MSA-DCS | WA3356189 | Unit 2, NDAS, received ablution block is faulty | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 09:19:19 | 2020-06-03 10:30:00 | Pass | Attended site and investigated the fault.Found damaged receiver near ablutions in unit 2.Replaced with new Bosch receiver EA 102A-304 (critical spare from site).Tested.All ok at departure
MSA-DCS | WA3356195 | unit 1 Far End of C-Wing & C-D Wing Kitchen 5x lights not working-see notes | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 09:20:43 | 2020-06-04 10:30:00 | Fail | Repaired and refixed lights
MSA-DCS | WA3356197 | Health Centre- logining new user to for cardex (drug centre) | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-04 08:00:00 | Pass | Consult with security and health staff on requirements in regards to programming new users to arm and disarm the health surfaces building through the RAT. Programming changes mate and functionality confirmed as ok with staff.
MSA-DCS | WA3356201 | Unit 1 D3 Top Bunk Light broken Falling out of the Head Board exposed wires | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 09:28:12 | 2020-06-03 15:30:00 | Pass | Repaired light
MSA-DCS | WA3356317 | Unit 4 - B9-Window mechanism in cell B09 is faulty. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-22 15:30:00 | Fail | RENEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3356323 | SOG-laundry GPO needs to be removed faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-08 15:00:00 | Pass | Removed faulty gpo
MSA-DCS | WA3356357 | Unit 14 - A Wing Water leak steady flow from ceiling in laundry. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 09:00:00 | Pass | 3/6/20-Investigated source of leaks. Special materials required to fix problem.8/6/20-removed waste pipe. Sealed penetration from c-wing to a-wing. Reconnected pipes and tested.
MSA-DCS | WA3356365 | DDU Office, Male Bathroom – flickering light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 11:00:00 | Pass | Repaired light
MSA-DCS | WA3356369 | DDU Office, Executive” toilet - light blown | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 09:30:00 | Pass | Replaced globe
MSA-DCS | WA3356371 | DDU Office, Vault – Bulb takes time to warm up | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 10:15:00 | Pass | Replaced light
MSA-DCS | WA3356382 | Kitchen Oven - Large Convotherm Oven Door Seal damaged | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 11:03:57 | 2020-06-04 10:00:00 | Pass | Found oven door springing oven, found welds on corner plate of door to have been snapped and bent out of place. Rebent into shape but will still need to be rewelded back. Organised a welder for Friday 12th but returned 9/06 to another job to find the corner plate to be already welded. Was told Prison got a prisoner to do the welding.
MSA-DCS | WA3356393 | DDU - storm damage to a garden shed and equipment shed | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 15:00:00 | Pass | REPAIRED DAMAGE SHED CAUSED BY RECENT STORMS
MSA-DCS | WA3356396 | INF, dispensary room - key snapped off in barrell and unable to get out. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 11:19:22 | 2020-06-03 15:30:00 | Pass | Repair to lock
MSA-DCS | WA3356400 | Unit 13, Cell D11- Shower screen leaking | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-11 09:30:00 | Fail | SHOWER SCREEN RE SEALED
MSA-DCS | WA3356406 | Visits Centre, assessments office - air con not wokring | Melaleuca Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 11:26:19 | 2020-06-26 09:30:00 | Fail | Arrived on site, signed in. Located controller in visits office. Adjusted the controls and checked temps.Unit is in good working order
MSA-DCS | WA3356425 | staff carpark front gate are harder/heavier to open when lockked feels loose/secured | Walcott Centre (Central West Metro ) | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-23 09:30:00 | Fail | 08/06/20Inspected.Post is loose in ground.Footing needs stabilising.New R4 Hinges required as completely bent.23/06/20Removed and realigned hinges on two gates.Clean drop bolt holes.
MSA-DCS | WA3356432 | ISU (harding), D Wing, Cell D10- Smashed Observation window & 2 cell windows | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-08-24 11:00:00 | Fail | RE GLAZED MULTIPLE WINDOWS AND WELDED GRILLE
MSA-DCS | WA3356437 | Visits Centre, Entrance Passage - Roof Leaking Water Onto PDA Wall Box | Melaleuca Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Schlager Construction Group | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 11:32:13 | 2020-06-08 11:30:00 | Fail | Attended site and carried out repairs to roof area to stop leaks.
MSA-DCS | WA3356446 | Clerical/Reception Area- Skirting boards coming away from wall | Walcott Centre (Central West Metro ) | GMP-BR- HO | Carpentry | Joinery (CA) | Schlager Construction Group | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-04 10:30:00 | Pass | Attended site and carried out repairs to the skirting board that was coming away from the wall
MSA-DCS | WA3356464 | Lenard b wing Cell B4 Smashed Obsevation window, 2 cell windows and mirror | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-09 12:00:00 | Fail | CELL WINDOWS, OBS PANEL REGLAZED - MIRROR REPLACED
MSA-DCS | WA3356467 | Unit 6, Cell 14 - flushing mech in the stainless Steele system is broken | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 11:51:05 | 2020-06-05 10:05:00 | Fail | Attended site,Locate broken flush button assembly to toilet suite,Left site to locate repair or replacement. Returned to site, supplied and installed button assembly to repair. Tested works on completion
MSA-DCS | WA3356488 | Boilerhouse, Boiler 1 - Leak from main steam line drain | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 11:59:24 | 2020-06-16 07:06:00 | Fail | Boiler 1 - carry out leak repairs from main steam drain line.
MSA-DCS | WA3356499 | Boilerhouse, Chlorinator Tank - Reconnect relief line into drain | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-16 07:04:00 | Fail | reconnect relief line into drain
MSA-DCS | WA3356502 | Unit 2, A4 - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-04 11:30:00 | Pass | Repaired light
MSA-DCS | WA3356518 | Old Video Link office Light switch and GPO Faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-16 12:00:00 | Fail | Replaced light switch and gpo
MSA-DCS | WA3356543 | unit 1 C7 Prisoner Lock Jammed Can’t Open Cell Door-see notes | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 12:32:40 | 2020-06-08 16:30:00 | Fail | Supplied and installed required parts
MSA-DCS | WA3356544 | Unit 14, Cell D16 - main cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 11:30:00 | Pass | Repaired faulty lights in unit 14 d16. Picked up replacement cover and installed
MSA-DCS | WA3356547 | Unit 14, A Wing cleaning room light, emergency light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-10 10:00:00 | Fail | Investigated faulty lights in store room. Picked up replacement parts and installed and tested
MSA-DCS | WA3356554 | Unit 4, Cell D7- Door lock & hinges need a service | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-11 11:30:00 | Fail | Replaced door plate lock
MSA-DCS | WA3356571 | Unit 4, - retune fence security system as multiple alarms are being set off and | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-07-10 10:30:00 | Fail | Cable ties retaining microphonics cable to fence in zones 9 & 10 had become brittle and fallen off. Retied these two zones and returned fence zone 9 which was generating continuous alarms.
MSA-DCS | WA3356579 | Date and time stamp not being entered on recorded footage of CCTV | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-04 10:00:00 | Pass | Consult with security in regards to concerns that most cameras do not have a date stamp option when exported due to VMS and cameras compatibility with new digital cameras. Advised to security that when extracting from analogue camera tick date stamp box and with their approval all digital cameras across site were individually programmed to stream live date stamped to overcome incompatibility issues. This was quite time consuming.
MSA-DCS | WA3356617 | Unit 1, Control Room Passage- Repair soft section of floor | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Schlager Construction Group | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 16:00:00 | Pass | Attended site and carried out repairs to the damaged floor in passage.Reglue carpet tiles.
MSA-DCS | WA3356620 | kitchen oven area Push Tap Broken Won’t Turn Off | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 13:41:00 | 2020-06-19 09:04:00 | Fail | Replaced faulty cartridge in the kitchen sink
MSA-DCS | WA3356625 | Bakery- Prover blown electrical components due to water/damage/timer blown | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 13:41:44 | 2020-06-04 15:10:00 | Fail | 04/06/20Arrived at site liaise with reception, walk to the bakery, liaise with kitchen staff, identify faulty prover, isolate remove panels refit circuit breaker, check all components for correct function, test low voltage and extra low voltage circuits, tested all okay.
MSA-DCS | WA3356631 | Visits centre, room 1 - vent hanging out of ceiling | Melaleuca Prison | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 09:30:00 | Pass | Attended site and carried out repairs to ceiling vent that had been vandalised.
MSA-DCS | WA3356642 | Unit 14, B Wing, Cell B16, - Shower drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-03 14:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3356644 | A Wing unit 14 blocked shower drain in A6 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-03 16:50:00 | Pass | Used acid and plunger to clear blockage from shower drain.
MSA-DCS | WA3356730 | front gate, master control - cell call answer panel button not working | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 15:04:39 | 2020-06-04 11:30:00 | Pass | Collected parts and travel to site.Replaced austco 3210 button with new replacement. All replaced and tested working ok. Job complete
MSA-DCS | WA3356741 | reception sallyport extraction suppose to work on sensor on continually | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-15 11:00:00 | Fail | Arrived to site.Fill out new ladder Access form.Awaited guard.Accessed work area.Roof survey completed.Ok to access.Located controls box.Found magnetic interface, adjusted sensitivity and found no change.Sensor circuit closed causing exhaust to run constantly.Spoke with maintenance team on site and tagged out exhaust system.New prisons protocol is to remove keys from truck leaving the original exhaust system obsolete by design.Staff advised.
MSA-DCS | WA3356993 | prem cam 31 not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-03 19:45:00 | Pass | Checked Camera 31 PTZ3, showing 2 vertical lines, no images.Requires cherry picker to access camera & modem box.19/06/2020 - A BRAF has been submitted under WA3350488 for repairs of PTZ3 (Camera 31) to take place
MSA-DFES | WA3356292 | Tunic room & BA Room - lights are not working, may have blown fuse | CFRS Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-12 09:30:00 | Fail | CompleteAttended site and located non working lights in ba room found faulty globes tripping power. Replaced globes and tested all in working order.notified staff and signed out
MSA-DFES | WA3356298 | Heritage Shed - light globe faulty/blown & powerpoint switch not working | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-08 11:15:00 | Pass | COMPLETED
MSA-DFES | WA3356300 | ground CL&D office Room too cold and strong wind from ducting | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-04 15:00:00 | Pass | Mark Kember (04/06/2020)Attend site. Check area complaints of too cold. At time off attendance found no issues. Staff complain will happen randomly throught to the day. Recomend carring out air survey on 4 ducted systems to confirm correct airflow. Dfes staff what whole of admin building air surveyed as there are complaints throughout the building. On the main face bypass system the airflow needs to be checked in heating and cooling. Estimate about 50 outlets will have to be measured with anemometer and calculated.
MSA-DFES | WA3356305 | Faulty fluoro light in engine room | CFRS Claremont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 08:00:00 | Pass | COMPLETED
MSA-DFES | WA3356315 | Faulty light switch in XVR curved screen room next to kitchen. | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 09:45:00 | Pass | Complete
MSA-DFES | WA3356324 | SIMCEN Bunker, Kitchen & toilets - no hot water to kitchen taps, female & male toilet basins | DFES Regional Office - Belmont | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-26 10:30:00 | Fail | Hwu faulty will need to be replaced or upgrade due to fixtures
MSA-DFES | WA3356508 | Rear sink near dryer - cold water tap leaking | CFRS Midland | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 08:57:00 | Pass | Serviced tap in outside sink.
MSA-DFES | WA3356520 | Duty room - faulty downlight, Replace/repair downlight | CFRS Midland | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-18 14:30:00 | Fail | Replaced faulty downlights with new
MSA-DFES | WA3356523 | Tunic Room - Sensor lights not working. Lights stay ON | CFRS Midland | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-07-16 13:30:00 | Fail | Need to replace sensor with new Replaced faulty sensor with new
MSA-DFES | WA3356546 | Kit Bag room - Timer on drying cabinet U/S | CFRS Midland | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-07-16 14:15:00 | Fail | Replaced faulty timer with new
MSA-DFES | WA3356783 | Station building - Remove unidentified alarm component found on the last system inspection, | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-12 08:30:00 | Fail | 08/06/2020, 1430-1445No one on site12/06/2020, 800-830 Disabled unidentified alarm component, causing keyswitch arming.
MSA-DTAG | WA3355988 | CCTV footage is dropping out and in some areas the cameras are not recording at all | Joondalup Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 03 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-03 17:00:00 | Pass | Unable to login on Camera 30 - known issue with Bosch
MSA-DTAG | WA3356090 | Lvl 9 & 10, Lift Lobbies- lights are out in public lift lobbies | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 10:00:00 | Pass | Job complete
MSA-DTAG | WA3356308 | L1 court 2 door from Magistrates Chambers cannot open or close freely-see notes | Midland Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-04 08:30:00 | Pass | DOOR SEAL REPAIRED/ DOOR ADJUSTED
MSA-DTAG | WA3356309 | Level 1, Custody - Crack in the hinge of interview room door | Midland Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-04 09:45:00 | Pass | door repaired
MSA-DTAG | WA3356716 | Lvl 4, Male Staff Toilet St Georges Tce end (with digilock)- Urinal Blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-09 08:30:00 | Fail | Complete
MSA-DTWD | WA3355893 | Male toilets Ground Floor -blocked toilet | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Jun 2020 | 2020-06-03 17:00:00 | 2020-06-03 14:30:00 | Pass | Complete
MSA-DTWD | WA3355983 | Door to Metal Fab, door is not functioning correctly | Naval Base | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 03 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 12:05:00 | Pass | Job completed - replaced padlock
MSA-DTWD | WA3356232 | plant room - The fluorescent light fitting in hanging by the conduit/cable | Kwinana Automotive Centre | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-12 15:30:00 | Fail | Attended site, reattached light fitting that was hanging. Job complete.
MSA-DTWD | WA3356252 | Level 3, room 127/128 - faulty lights requiring repairs/replacing | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-15 10:00:00 | Fail | Repalced multiple lamps out throughout B2.and resecured light covers in he library.job completed
MSA-DTWD | WA3356268 | A Block, Air Con has no flow | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-04 12:30:00 | Pass | Job completeAwaiting return of signature slip via email due to covid 19
MSA-DTWD | WA3356339 | B Block, Zip unit no cold water | Munster Campus (ACEPT) | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-11 16:30:00 | Fail | Installed new Assets as quoted after initial callout - unit deemed unrepairable - replaced after getting approval with Maxiflow Scale A40190488N, Wilson WB90 MF Number R2789902 + IC8 Chiller MF Number 19090246
MSA-DTWD | WA3356341 | H block cafeteria blocked floor waste in coolroom | Balga Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-11 09:30:00 | Fail | Cleared blockage using plunger, cleared pit outside
MSA-DTWD | WA3356435 | A Block, Room 354a - broken Billi quadra unit | Leederville Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Water2water Pty Ltd | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-04 16:00:00 | Pass | Replaced faulty element and all working fine
MSA-DTWD | WA3356468 | N Block, Room N108 - drain is flooding back into lab | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 03 Jun 2020 | 2020-06-03 15:51:34 | 2020-06-08 13:35:00 | Fail | Removed blockage and repaired section
MSA-DTWD | WA3356552 | H block - External light broken | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-09 08:00:00 | Pass | Attended site and signed in. Located H block with staff on site. Located light been removed. Site followed up on locating the light that was removed by others and he was advised that the building is going to be recladded and lights will be replaced. No need to repair anymore. Job complete
MSA-DTWD | WA3357123 | Back of the Building Level 1- Pipe drain stuck Tank over flooding | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 16:00:00 | Pass | Unblocked lines
MSA-DTWD | WA3357130 | B Block, 4th Floor, Above A2417- Down pipe is blocked on roof - need to be cleared | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 10:00:00 | Pass | Investigate leaks and possible blockages
MSA-MRWA | WA3356635 | Remove and dispose of drum from compressor compound. | Materials Engineering Branch | GMP-BR | Waste Management | Environmental Services (WM) | Veolia Recycling and Recovery Pty Ltd | 3 | CLOSE | 03 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 13:14:00 | Pass | FIELD JOB WAS COMPLETED ON 05/06/2020
MSA-DCA | WA3356963 | Livingstone Café, water leak coming from garden bed | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Jun 2020 | 2020-06-04 17:00:00 | 2020-06-04 08:30:00 | Pass | Repair to burst to 25mm retic to LHS of cafe
MSA-DCA | WA3357099 | Lift no.5 is out of service | State Library of WA-Main Building | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 11:52:00 | Pass | Found unit missing t3b in safety circuit due to salsis in fault. Reset salsis and retrieved version numbers.##Due to COVID-19, nosignature is requested. Have spoken to customer on works completed.
MSA-DCS | WA3356926 | Maintenance w/s zip auto boil faulty leaking water from inside unit | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 04 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-23 10:32:00 | Fail | Replaced Zip 7.5 Econoboil A401914307E MF no Zip 2020052005008 and installed new Maxiflow filter system A40191306D client requested we dispose of on site in Skip bin.removed tip fees
MSA-DCS | WA3356938 | Admin, Male Toilet - Toilet leaking from behind cistern | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-10 10:20:00 | Fail | Replced faulty putlet and inlet valve
MSA-DCS | WA3356942 | Gatehous, perimeter- several perimeter lights out Approx 5 | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-18 15:00:00 | Fail | Repaired lights
MSA-DCS | WA3356968 | SHU(9)- East Wing kitchen sink slow to drain, sometimes backing up into sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-04 14:06:00 | Pass | Used plunger to clear blockage in kitchen sinks.
MSA-DCS | WA3356970 | SHU(9), Cell B8 - toilet system keeps running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-04 14:11:00 | Pass | Replaced leaking inlet valve
MSA-DCS | WA3356972 | Unit 10, C & D Dayroom- Light flickering (requires large steps) | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-15 12:00:00 | Fail | Replaced lights
MSA-DCS | WA3356974 | Unit 10, C wing cleaning cupboard- Sink is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-05 14:35:00 | Pass | Replaced trap on trough
MSA-DCS | WA3356978 | Security Area, Demountable Office- Door handle is faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 04 Jun 2020 | 2020-06-10 17:00:00 | 2020-07-16 09:30:00 | Fail | Lubricate lock.Replace lock keyed to site keys.
MSA-DCS | WA3356982 | Unit 1 - Door control screen freezes or switches to another screen | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Jun 2020 | 2020-06-04 11:55:33 | 2020-06-04 10:00:00 | Pass | Rectified and fixed the fault from EBI WS, job completed.
MSA-DCS | WA3356983 | Video Link- Prisoners phone booth- Ceiling lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-17 12:00:00 | Fail | Checked faulty lights. Picked up replacements and installed and tested
MSA-DCS | WA3356992 | Unit 7 - A Wing-SCU A WING LAUNDRY ROOM/POWER POINT DAMAGED/LIVE WIRES | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 08:05:46 | 2020-06-05 15:30:00 | Fail | Investigate unit 7 laundry gpo. Source replacement parts. Replace gpo and plug top
MSA-DCS | WA3357031 | Perimeter zone 6 Loose concrete at base of wall | Hakea Prison | GMP-BR- HO | Building | External Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 08:24:46 | 2020-06-04 15:00:00 | Pass | CONCRETE REPAIRED
MSA-DCS | WA3357034 | Perimeter, Zone 7/8- Hole in brickwork at basse of Obs Tower | Hakea Prison | GMP-BR- HO | Building | External Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 08:26:20 | 2020-06-05 10:15:00 | Fail | INSTALLED PLATE TO COVER HOLE
MSA-DCS | WA3357069 | Skylight at art centre roof damaged | Casuarina Prison | GMP-BR- HO | Roofing | Rooflights and Skylights (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-07-31 09:43:00 | Fail | REPAIR STORM DAMAGED SKYLIGHT
MSA-DCS | WA3357071 | Education - Court Yard gutter is rusted between main builing and pergola | Casuarina Prison | GMP-BR- HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2021-07-19 15:00:00 | Fail | new guttering installed
MSA-DCS | WA3357165 | Unit 7, A & C - Water leak from pipe inside cabinet, located next to outside telephone of A wing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-05 14:17:00 | Pass | 4/6/20- investigated leak and collected materials.5/6/20- isolated water. Repaired broken water main. Tested.
MSA-DCS | WA3357263 | Hotman, A4 & A5 - above windows is leaking, seal has perished | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-12 10:45:00 | Fail | WINDOW LEAKS REPAIRED
MSA-DCS | WA3357320 | Kitchen - indrustrial hobart mixer leaking gear oil | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-16 08:30:00 | Fail | Kitchen Big Mixer leaking oil. Check mixer. Disconnect & remove from kitchen to workshop. Dismantle, grease leaking thru worm drive, remove motor & gearbox. Replace worn parts, bearings & seal, gearbox grease. Assemble & test. Return to kitchen.
MSA-DCS | WA3357332 | gardens shed near kitchen rat infestation | Wandoo Rehabilitation Facility | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-08 08:15:00 | Pass | placed loaded rodent bait boxes around gardeners shed area
MSA-DCS | WA3357336 | Tamper alarm, mobile duress self care | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-04 13:45:00 | Pass | Located self care unit transponder in roof space. Repaired tamper switch and tested back to the gatehouse. Tamper alert on PC cleared ok. Parts used:Consumables
MSA-DCS | WA3357393 | L2 control room Control Room door Lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 11:36:31 | 2020-06-05 09:30:00 | Pass | Serviced and repaired Unit 2 Control Room door.
MSA-DCS | WA3357411 | Library- Hot water system faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-05 14:21:00 | Pass | Investigated and tested unit. No issue found, unit operating correctly.
MSA-DCS | WA3357470 | Unit 7, H3, H$ & H5 - sinks blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-12 14:30:00 | Fail | Unblocked x3 basins
MSA-DCS | WA3357472 | Kitchen, Prisoners toilet- urinal blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-05 12:10:00 | Pass | Removed 500mm deep off struvite out off drain put drain machine down and used a full 1lt bottle off draino
MSA-DCS | WA3357504 | Kitchen - no 4 fan fridge - Dirt, white dust being blown from fan and settling on shelves | Hakea Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-16 09:31:00 | Fail | Notified maintenance personnel to remove netting.
MSA-DCS | WA3357510 | Unit 5 -Drain outside computer room and S/O's office are blocked, emitting a bad odour. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-10-21 08:30:00 | Fail | 8/6/20- Investigated source of bad smell. BRAF required to continue investigation.10/6/20- Prep work. Marked out and cut concrete.20/10/20 - repaired and re concrete steps21/10/20- remove form work and bunting
MSA-DCS | WA3357513 | Vegetable Prep- CL60 machine has stopped working | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-07-07 09:00:00 | Fail | Vege Prep CL60 fault in front stores. Check machine, remove for repairs. PCB board damaged. Replace board, main shaft bearings & seals. Assemble & test. Return to store.
MSA-DCS | WA3357516 | Grounds - The Whole Unit Grounds external lights faulty not turning off during day . | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 12:30:00 | Pass | Investigated and removed faulty latching relays on external lighting controls. Rewired controller and tested
MSA-DCS | WA3357597 | Unit 9, A10 - replace smashed sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 14:06:32 | 2020-06-05 12:30:00 | Pass | Replace basin and tap ware to unit 9 a10
MSA-DCS | WA3357654 | Main front door long delay using swipe card before it is secured again | East Perth | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-05 15:30:00 | Pass | Lock on door replaced due to malfunctioning replaced with an es8000
MSA-DFES | WA3357424 | half of the fire station has lost power - electrical fault | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 13:45:00 | Pass | CompleteAttended site and located non working rcd. Tested and all in working order. Notified staff to monitor
MSA-DFES | WA3357519 | Kitchen & Surrounds- Ant Infestation- see further info below | CFRS Malaga | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 11:45:00 | Pass | Reports of ants throughout building, upon inspection , no ants noted . Treated externally to all garden beds , paved areas , drains and all ant trails . Dusted cavity wall, through weep holes. Gelled internally to all cracks and crevices and harbourage areas. . Treated entry points.Please allow up to 2 weeks for ants to spread chemical back to their queen in order to eradicate the colony. Depending on the size of the colony, re application of gel baits may be required, especially if ants are nesting within the wall cavity in large numbers.
MSA-DFES | WA3357550 | Workshop, toilets- Taps in the male change room are leaking | Fleet Management Services - O'Connor Workshop | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 11:15:00 | Pass | Located to site and serviced tapes in male change rooms tested and working. The spouts on the tapes have no air rator due to the make of the spout.
MSA-DFES | WA3357668 | Malfunction of rear gate possibly due to water leakage into ground connection pit-see notes | CFRS Midland | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-07-09 10:45:00 | Fail | Technician attended the site of Midland Fire Station rear gate on 25/05/2020. Electrical pit which has cable joints in it was flooded and conduit boxes were under water. This is causing cables to short out and not work. Technician have disconnected the keypads so gate is now only operational by remote until issue can be resolved. Pit will require adequate drainage to prevent this happening in future, also identified this issue last year when the keypads also failed.Technician returned on site on 09/07/2020. Attended site to check running new cable for gate. Have problems with running new cable. Unable to start as too much rain. Returned to site and remove old junction box. Installed new junction box, redo connections for keypad. Filled with wonder gel. Sealed conduit entries. Used self-fusing water proof tape to seal over junction box and entries as secondary measure.Full test and inspection of gate components completed prior to leaving site.
MSA-DTAG | WA3357268 | ground Judge’s chambers, Court 6, Judicial corridor faulty light-see notes | Perth Children's Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 17:00:00 | Pass | Job complete
MSA-DTAG | WA3357621 | Level 5, Old Sheriff’s Office kitchen - Kitchen floor waste is broken | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-19 12:30:00 | Fail | Complete
MSA-DTWD | WA3357109 | F Block, FT03 Classroom - Motion sensor hanging from ceiling a making buzzing noise | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 11:15:00 | Pass | Resecured sensor in classroom.job completed
MSA-DTWD | WA3357197 | Block C ground Corridor near disabled toilet CG35 Water fountain leaking water from filter | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-04 20:00:00 | Pass | Fixed jug filler and filter setup
MSA-DTWD | WA3357203 | E block, ground level, Entry door - lock faulty | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Locksmith (SE) | GRONBEK SECURITY | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-12 12:55:00 | Fail | Replace faulty lock on E block, ground level, entry door.
MSA-DTWD | WA3357271 | H2 student zone- Roof /ceiling leak on to left side computers water on floor | Murdoch Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-05 11:30:00 | Pass | Believe leak to be coming from ski of air con unit, lifted ski and siliconed underneath. If problem persists will need new design of ski.
MSA-DTWD | WA3357324 | work shop area goods lift - stuck half way | Clarkson Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 04 Jun 2020 | 2020-06-04 15:03:00 | 2020-06-04 12:30:00 | Pass | Not chargeable
MSA-DTWD | WA3357326 | Ground level, staffroom - flashing light | Armadale Campus - 40 Commerce Ave | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 15:15:00 | Pass | Replace faulty fluro to light in staffroom. Job completed
MSA-DTWD | WA3357376 | E Block, Pines Restaurant – Ceiling GPO has no power | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 14:30:00 | Pass | Attended site and signed in. Located faulty gpo and investigated power loss to circuit. Opened up ceiling tiles and followed cable to find disconnected. Re energised to exisiting circuit. Replace faulty pendant gpo and replaced cracked plug top. Tested all okay. Job complete
MSA-DTWD | WA3357437 | Room B1, Evap Air conditioner units damaged by Friday storm. | Murdoch Campus | GMP-BR-RC | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-09 11:45:00 | Pass | Awaiting approval of braf
MSA-DTWD | WA3357530 | Plant room heating boilers faulty check operation | West One Services | GMP-BR | Mechanical Services | Boilers (MS) | Precise Air Group | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-04 16:00:00 | Pass | Riaised tems on top floor of tower as it was all working correctly just temps wernt hi ghost enough , The admin building i can get pump to run off bms but only for a few seconds , assuming this is a lockout as the building is at temp and no complaints of heating from admin
MSA-DTWD | WA3357563 | L2 S220 Sparking power point in center of the room | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 04 Jun 2020 | 2020-06-05 17:00:00 | 2020-06-05 13:30:00 | Pass | Attended site and signed in. Checked power in room S220. No fault was found. Did find extension board been used which could be the cause. Informed site.
MSA-DTWD | WA3357594 | BLD 822A and BLD 822 Between reception and Dempster Hall Ceiling eave sheeting dangerous | Muresk Institute | GMP-BR | Building | Ceiling (BU) | Lee Carpentry | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 11:30:00 | Pass | Repairs to ceiling
MSA-DTWD | WA3357634 | Staff area- aluminium glassed door is catching on the floor & will not close | Jandakot Campus - Annex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-18 10:12:00 | Fail | Door frame straightened by glazier
MSA-MRWA | WA3357388 | Western personnel access door (outside UAT)- Threshold plate not securely fix | Materials Engineering Branch | GMP-BR | Building | Doors (BU) | MR - Handyperson - PFM | 2 | COMP | 04 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-05 14:48:00 | Pass | Re glued threshold plate back in position
MSA-MRWA | WA3357452 | ground Admin Building Graduates area Carpet tiles lifting - graduate area | Materials Engineering Branch | GMP-BR | Flooring | Carpet (FL) | MR - Handyperson - PFM | 3 | COMP | 04 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-09 09:00:00 | Pass | Re sprayed tiles with glue
MSA-DCA | WA3358074 | Interior gallery 5 - aircon not working | Art Gallery of WA - James St | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 12:30:00 | Pass | Nterior Galkery 5 high temperature alam. AC operating as required. Bulding is in local mid but all plant isolated. ENVAR left locap md on afte being nformed of works in buildn. No issue with plant. ETS was ngaged and alrm cleared after shirt period of tme.Closd jb.
MSA-DCA | WA3358078 | security control room – air con not working | Art Gallery of WA - James St | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 14:30:00 | Pass | security office L1 too warm. Checked operation of AHU 7. Due to building being Local mode even when requested to remain in ETS mode, there was no chilled water. Zone 1 htg valve actuator not driving on either 0 or 10 vdc and was stuck at 100% open. Will need to be replaced. Confirmation of correct KV rating needs to be made before replacement can be ordered. This ties up with commissioning works previously.ETS mode enabled, ChW supplied, all alarms cleared.
MSA-DCA | WA3358473 | ground public male toilet Water leaking over floor from cistern S bend when toilet flushed-see note | Maritime Museum Victoria Quay-Main Building | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 14:25:00 | Pass | Removed toilet replaced pan seal and key seal reconverted in toilet
MSA-DCA | WA3358483 | plantroom Heating water pump 2 failed coupling | Maritime Museum Victoria Quay-Main Building | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-09 12:00:00 | Fail | Returned to site 9/6/20 0930. Removed and replaced defective coupling and rubbers. Carried out rust treatment to pump and applicable mechencical services pipework. Carrie four tests and checks. Works completed & system operating correctly.
MSA-DCS | WA3357796 | Unit 7, S wing cleaning cupboard hot water system is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 06:39:02 | 2020-06-09 11:15:00 | Fail | Need access to turn off mains to prison to replace valves 40x40 ball valve doesn’t shut off mains completely for s wing 25x25 ball valve on hwu doesn’t turn off hwu To replace hwuModel number 1331507Serial number 5228392315 litter eltric 20mm Relief hot side leaking 8/6/20 Replaced 4x valves in s wing 9/6/20 Replaced hwu
MSA-DCS | WA3357821 | Concrete Products- Vibrating table not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-08 12:30:00 | Pass | Disconnect vibrating table
MSA-DCS | WA3357839 | Unit 4, D Wing, Cell D1- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 10:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3357842 | Unit 13, Cell B13 - Leftside of basin continually leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-15 11:00:00 | Fail | Inspected and tested basin for leaks. No leaks found.
MSA-DCS | WA3357848 | Unit 6, B & D Wing- Hot water flooding in day room from under the sink. Pipe appears broken. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-05 14:40:00 | Pass | Replaced burst flexy pipe in kitchen cupboard
MSA-DCS | WA3357851 | Unit 1, D Wing, Cell D06- Main light is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 08:30:00 | Pass | Investigate and repair unit 1 cell d06 light
MSA-DCS | WA3357853 | Unit 4 - B & D B/D WING HOT WATER URN IN THE DAY ROOM NOT WORKING PROPERLY. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 05 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-12 09:36:00 | Fail | ACTUAL START DATE IS 10.6.2020 ACTUAL FINISH DATE IS 10.6.2020MAY HAVE USED WRONG WORK ORDER NUMBER AND ASSIGNED TO INCORRECT TECH.NICOLAS DEGRYS ATTENDED TO THIS SYSTEM ON 10.6.2020 AS PER SIGN SLIP AND DESCALED TAP AS PER INFORMATION (DEBORAH INCORRECTLY ASSIGNED THIS WORK ORDER TO LACHLAN SCULLEY - HE COMPLETED WORKS ON A DIFFERENT CASUARINA WORK ORDER)
MSA-DCS | WA3357869 | INF(10)- Download footage in infirmary | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-05 16:30:00 | Pass | Located and downloaded video from Cell HC1 and delivered to SOSecurity. At same time requested urgent download of CCTV video from Western Sally Port in Gatehouse. Downloaded requested video and supplied to SO Visits.
MSA-DCS | WA3357902 | Zone control 2- male urinal blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 08:30:04 | 2020-06-05 16:00:00 | Pass | Clear blockage to urinal in zone control 2
MSA-DCS | WA3357914 | unit 3 D wing no HW | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 08:44:00 | 2020-06-05 13:30:00 | Pass | nil
MSA-DCS | WA3357919 | unit 2 cell 21 broken light fitting | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 05 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-08 11:00:00 | Pass | Investigate and replace broken cell light unit 2 cell 21
MSA-DCS | WA3357936 | kitchen all the coolrooms require ringer bells repaired not working | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 05 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-29 14:00:00 | Fail | INSTALL 2X DOORBELLS
MSA-DCS | WA3357946 | kitchen slicing machine faulty | Wooroloo Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-07-10 10:00:00 | Fail | Kitchen slicing machine faulty. Check machine. Tag out of Service. Dismantle, remove damaged power lead & broken reset switch. Order new parts, return & install. Assemble & test.
MSA-DCS | WA3357997 | Unit 1 - C10 Cell Door, Hatch lock not releaseing key | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 09:19:24 | 2020-06-05 10:30:00 | Pass | Repair hatch lock
MSA-DCS | WA3358002 | Unit 2, D7 - hole burnt into light cover above the top bunk | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 13:00:00 | Pass | Repaired damaged cell light in unit 2 d7
MSA-DCS | WA3358106 | Unit 3, Pod 1- no tv reception | Wooroloo Prison Farm | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 10:32:23 | 2020-07-02 09:00:00 | Fail | Bypassed amp temp until power fixed, return to connect
MSA-DCS | WA3358108 | Reception - lights not working in reception, see further info below | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-09 11:00:00 | Pass | Replace multiple lights in Reception
MSA-DCS | WA3358149 | unit 7 H8 Cistern leaking through screws-see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 10:53:05 | 2020-06-05 14:00:00 | Pass | Replace cistern to unit 7 H8
MSA-DCS | WA3358165 | Unit 6 - A wing day room - power point broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 11:00:58 | 2020-06-05 14:00:00 | Pass | Replaced gpo
MSA-DCS | WA3358170 | CCU, H11 - Safe cell needs cement wall around bottom left corner of window fixed/filled as it could | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 11:04:26 | 2020-06-05 13:15:00 | Pass | USED SIKAFLEX TO PATCH AROUND WINDOW IN CCU
MSA-DCS | WA3358197 | Bakery workshop - bakery freezer not working, motor and fans Iced up | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 05 Jun 2020 | 2020-06-05 15:14:34 | 2020-06-06 11:53:00 | Fail | Complete
MSA-DCS | WA3358268 | Education office door - difficult to open, barrel seems to have flipped. | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-08 09:45:00 | Pass | Repaired Lock barrel on Door to Education Lock cylinder - repinned and barrel replaced
MSA-DCS | WA3358304 | Unit 5, C wing - tap in cleaning store leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-08 11:00:00 | Pass | Replaced leaking cold spindle.
MSA-DCS | WA3358356 | Main entry door- handle is not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 05 Jun 2020 | 2020-06-05 17:11:15 | 2020-06-05 14:30:00 | Pass | RE FIX DOOR HANDLES
MSA-DCS | WA3358425 | Unit 1, B wing B09 rear window smashed, and viewing hatch cover broken. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 14:00:33 | 2020-06-05 19:45:00 | Pass | SASH REGLAZED, FRAME REPAIR & HATCH REPLACED
MSA-DCS | WA3358534 | Uni 9, rear unit - water leaking from valve | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Jun 2020 | 2020-06-06 15:26:48 | 2020-06-05 19:30:00 | Pass | Replaced burst tee and large section off 50mm pipe
MSA-DCS | WA3358536 | unit 2 A, B day room awning window has come away from frame sash damaged glass intact | Bandyup Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-09-15 14:00:00 | Fail | AWNING WINDOW REPAIRED & RE FIT
MSA-DCS | WA3358582 | Zone 14, camera 2 & zone 15 Camera 1 - not working | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-06 18:30:00 | Pass | Zone 14 Camera 2 & Zone 15 Camera 1 offline. Checked comms in EC15 and no network light on switch. Power cycled encoder & tested operation, all is in working order. Checked voltage and temperature on PSU and all is ok.
MSA-DCS | WA3493285 | Retrospective workorder - Boiler house fault on boiler-already attended | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-09 15:30:00 | Pass | Works completed as per sub contractor report.
MSA-DFES | WA3357904 | northern boundry behind 2 trailers cut in the fence needs to be made safe cyclone fencing | DFES Regional Office - Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-09 12:30:00 | Fail | Attended site and carried out temp repair to make secure. Will need to return with mesh to complete repair
MSA-DFES | WA3357973 | gym circuti breaker keeps tripping | CFRS Canning Vale | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-19 16:15:00 | Fail | Installed new RCD and Driver and tested all lights for function
MSA-DTAG | WA3358224 | ground kitchen Kitchen exit door dropped & the door frame needs to be repaired. | Midland Courthouse | GMP-BR-HO | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 09:00:00 | Pass | Complete
MSA-DTAG | WA3358240 | Ground - Lift 4 is out of service - lift next to Justice Mazza’s Chambers in south corridor | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-09-08 13:00:00 | Fail | Not chargeable
MSA-DTAG | WA3358448 | Lvl 8 - Light is ‘buzzing’ in interview room | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 05 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-09 09:30:00 | Pass | Job complete
MSA-DTAG | WA3358516 | Roofline external water from gutter above main entrance rotting the timber facia-see notes | Midland Courthouse | GMP-BR-HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 05 Jun 2020 | 2020-06-12 17:00:00 | 2020-11-23 09:00:00 | Fail | REPAIRS TO GUTTERS & ROOF COMPLETED
MSA-DTWD | WA3357804 | A block, Room A009 - Access system requires repairs to software on Tuesday 9th June 2020 @ 9am | Joondalup Kendrew Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 3 | CLOSE | 05 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-09 17:30:00 | Pass | Upgrade 7.70 in place on existing server to 7.90. Transferred database to fresh install on 7.90. Server all working ok on 7.90. Workstation imaged for Windows 10. Install v7.90 command centre on new image. 3 controllers offline. D Blk L1, A Blk East Gnd and A Blk East L2. Troubleshoot with IT and bring back online. Update all controllers to v7.9
MSA-DTWD | WA3357859 | Ground male toilets Blocked urinal | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 11:30:00 | Pass | Unblocked urinal and cleaners sink
MSA-DTWD | WA3357949 | Cafe- Bain marie is not working | Leederville Campus | GMP-BR | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-15 14:15:00 | Fail | 8/6/20 - Arrived at site, liaise with maintenance, identify faulty Bain Marie, isolated remove panels, test/fault find and diagnose, found both heat lamps to be faulty and require replacement.2x heat globes15/6/20 - Returned to site with parts required fitted tested all okay.
MSA-DTWD | WA3358045 | GG 05 & GG 13 workshops- lighting issues | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 05 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-19 03:00:00 | Fail | Attended site. Located the scissor lift. Located Lights in need of replacing. Replaced old faulty lights with new led lights. Did paperwork signed out. Job complete
MSA-DTWD | WA3358056 | GG 01 (outside fountain) 2. Lever for drink fountain broken off. Filter for fountain faulty | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 13:07:00 | Pass | Repairs to fountain
MSA-DTWD | WA3358062 | GG 14 workshop 1. Gate valve that the supplies the sink needs to be repaired. tap is faulty | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 13:08:00 | Pass | Tap leaking Valve could not be completely shut off required replacing as well as tap
MSA-DTWD | WA3358086 | E Block, G level, Restaurant Kitchen - two heating globes out in the bain marie | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-08 10:30:00 | Pass | Attend site and inspect globes out, source globes from wholesaler. return and replace globes
MSA-DTWD | WA3358180 | House 818 Transportable Power to transportable at back of house 818 faulty | Muresk Institute | GMP-BR | Electrical | General Electrical (EL) | Damian Rak Electrical Pty Ltd | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 14:00:00 | Pass | fixed power issue
MSA-DTWD | WA3358229 | A block, G level, east end female toilets - ladies toilets blocked | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-05 14:30:00 | Pass | unblocked main sewer line to toilet block
MSA-DTWD | WA3358438 | L3 roof plant corroded refrigerant receiver on Chiller | Perth Campus B4 | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 05 Jun 2020 | 2020-06-12 17:00:00 | 2020-07-31 11:58:00 | Fail | Check oil separator on circuit A of Carrier Chiller and found to be heavily corroded beyond repair.Sent emails off for pricing for replacement of oil separator.BRAF to be submitted when pricing comes in
MSA-DTWD | WA3358452 | L2 tool store Repair A/c controller | Perth Campus B5 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 05 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-16 14:21:00 | Fail | Collected controller and returned to site. Singed in gained access and changed over split A/C controller. Tested and checked operation all ok. Work area left tidy.
MSA-DTWD | WA3358529 | D block, D19 - tap leaking at handwash basin | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 05 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-08 11:45:00 | Pass | Fixed leaking taps
MSA-DTWD | WA3358530 | chiller not starting, possible BMS issues. - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 05 Jun 2020 | 2020-06-10 17:00:00 | 2020-10-08 16:00:00 | Fail | Drove to site signed out the keys , found chiller one out on fault , Reset the condenser pump and test ran all ok . Went through the chiller and reset and checked all sensors , need storm to access the chiller to fault find .
MSA-DTWD | WA3358559 | P block - commication failure so alarms will not arm | Midland Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 0 | CLOSE | 05 Jun 2020 | 2020-06-05 19:47:12 | 2020-06-05 17:15:00 | Pass | Communication Tested - No Problem.
MSA-MRWA | WA3358173 | Lift 4 access control panel not working | Don Aitken Centre MRWA Head Office | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 05 Jun 2020 | 2020-06-05 15:03:50 | 2020-06-05 15:45:00 | Fail | reset the board at the security panel in lift room. Lift 4 security system is working now.
MSA-MRWA | WA3358176 | Auto doors not closing | Jandakot Depot | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 05 Jun 2020 | 2020-06-05 15:07:03 | 2020-06-05 13:15:00 | Pass | 1095727 exit gate. Gate not closing due safety beam wire being cut through. Two techs pulled existing cable back up post and reconnected. Tested ok.
MSA-MRWA | WA3358245 | Power loss to alarm system | Jandakot Depot | GMP-BR | Security | Monitoring (SE) | SONTEC WA PTY LTD | 0 | CLOSE | 05 Jun 2020 | 2020-06-05 15:39:35 | 2020-06-05 13:30:00 | Pass | 5/6/20 - Dean SimpsonInvestigated issue with power loss alarm.Confirmed that expander 1 sent a power loss at 10:22am and restored at 11:24am.All tested ok.
MSA-DCS | WA3358608 | Screen on SO Desk to access gatehouse doors has gone down. | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jun 2020 | 2020-06-06 08:39:05 | 2020-06-06 07:00:00 | Pass | Gatehouse Access Control computer not working. Monitor is showing no signal. Power cycled VGA Receiver and tested operation. All is in working order.
MSA-DCS | WA3358623 | Karnet Prison Farm- zone alarm faulty, unable to select camera in control room | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jun 2020 | 2020-06-06 10:57:49 | 2020-06-06 10:00:00 | Pass | Indigo workstation in full screen mode & operator unable to select cameras. Trained operator how to exit full screen mode. Senstar Tampers Map has multiple alarms that clear and then return. X & Y data path issue. Open job to clean all fibres and rectify issue. Zones still able to access/secure and alarms for fence zones still work to control.
MSA-DCS | WA3358647 | Unit10 -B wing -Hot water leaking from the roof . | Hakea Prison-Main Gatehouse | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 06 Jun 2020 | 2020-06-06 13:01:00 | 2020-06-06 15:15:00 | Fail | Replaced 24meters off 50mm copper and reconnected duct connections in unit
MSA-DCS | WA3358659 | The electronic security grill in D wing unit 3 is not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jun 2020 | 2020-06-06 14:28:09 | 2020-06-06 16:45:00 | Fail | Attended casuarina prison unit 3, found D wing grill failing to operate, checked gate motor not responsive, tested control panel signal to relay operating correctly tested Gallagher input operational upon activation. Found 24v transformer missing 240v feed, traced to unmarked breaker in Distribution board ground corridor. Labelled breaker and notified Senior officer and principal officer electrician required as breaker will not reset. All access equipment operating correctly and gate temporarily released for manual use.
MSA-DCS | WA3358703 | Unit 14- Cell C4 Cell lock door is not double locking | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 0 | CLOSE | 06 Jun 2020 | 2020-06-06 19:06:55 | 2020-06-06 17:00:00 | Pass | Lock service
MSA-DCS | WA3358704 | UNIT 3- Electrician to attend to red 41 is tripping in the downstairs switchboard. | Casuarina Prison-Prisoner Accommodation Unit 3 | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 06 Jun 2020 | 2020-06-06 19:22:48 | 2020-07-03 16:00:00 | Fail | Replaced damaged wing grill control box enclosure in unit 33/7/20 date chosen by unit 3 senior officer as was the best day to lose power for duration
MSA-DCS | WA3358714 | Karnet Prison Farm - Zone 6 fence - Alarm does not activate. | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jun 2020 | 2020-06-06 20:10:38 | 2020-06-06 19:15:00 | Pass | Zone 6 not activating. Set Zone 6 to Access then Secure. Went to Zone 6 EC and measured 1Mohms on cable. Tested Zone 6 and control receiving alarm. All is in working order.
MSA-DCS | WA3358719 | Hakea Prison - Perimeter - Bump house alarm on. | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 06 Jun 2020 | 2020-06-06 22:43:16 | 2020-06-06 20:45:00 | Pass | Attended site and and found that 250volt supply to diesel pump circuit breaker had tripped.Reset circuit breaker and reinstated pump to normal.Reattended site to make sure system was still online after the trip, all ok on departure.
MSA-DFES | WA3359316 | RETROSPECTIV WORK ORDER DONOT ATTEND-APPEARS THAT CREWS WERE OFF STATION | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 06 Jun 2020 | 2020-06-08 17:00:00 | 2020-06-06 15:50:00 | Pass | BYPASS ZONE 22 APP 1 REAR DOORVOICED TO PATROLS: 15:35Patrol Resolution:OFFICER REPORTS NO PERSONS ON SITE. APPEARS THAT CREWS WERE OFF STATION.
MSA-DCA | WA3358771 | fire panal need to be reset zone 39, 42, 43 showing faulty | Maritime Museum Victoria Quay | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 07 Jun 2020 | 2020-06-07 17:24:29 | 2020-06-08 07:00:00 | Fail | Call out, zone 42 & 43 in alarm, both zones isolated, further investigation needed.
MSA-DCA | WA3358795 | A Shed, Victoria Quay, Fremantle-A Shed - Numerous faults on the fire panel due to a power outage. | DO NOT USE TO BE DECOMMISSIONED A Shed, Victoria Quay, Fremantle-A Shed | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 07 Jun 2020 | 2020-06-07 20:55:25 | 2020-06-08 07:00:00 | Fail | Earth fault, bell shorting out, isolated.
MSA-DCS | WA3358742 | SHU- Cell call system is faulty. | Casuarina Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Jun 2020 | 2020-06-07 12:54:03 | 2020-06-09 11:26:00 | Fail | Cell call system is fully operational, site indicating issue with announciator for duress system. Ongoing works with construction zone.
MSA-DCS | WA3358745 | Perimeter SNI communication boxes, constant fault. | Casuarina Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Jun 2020 | 2020-06-07 13:35:09 | 2020-06-09 14:22:00 | Fail | Picked fibre modem for replacement, replaced can S710 modem in EC8 and restored alarm status, system fully operational.
MSA-DCS | WA3358791 | Karnet Prison Farm - Zone 4 and 5 - Fence alarm aren't activating. | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Jun 2020 | 2020-06-07 19:55:57 | 2020-06-07 19:15:00 | Pass | Zone 4 & 5 not alarming. Checked zones & status showing secure. Accessed then secured zones again. Tested operation & control acknowledged Zone 4 plus 5 fence alarms. All is in working order.
MSA-DCS | WA3361077 | PTZ24 camera not rotating not zooming in or out | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Jun 2020 | 2020-06-10 17:00:00 | 2020-08-18 08:30:00 | Fail | Job to be completed under work order WA3500978 SEME job number 90229178.
MSA-DCA | WA3358979 | Brick paver has been cut in half & removed, needs repair | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 14:45:00 | Pass | New paver refitted to position of broken paver
MSA-DCA | WA3358990 | L1 various issues with air conditioner -see notes | His Majesty's Theatre-Theatre Building-Level 1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 14:00:00 | Pass | We have had the subcontractor visit the area to investigate all three FCUs. As the works are quite involved we will not be seeing a price for repair today. The works are very intrusive and will require after hours visits to eliminate any disruption to staff. We will continue to see how best to submit our pricing. Quote will be submitted and new job to be raised for further works
MSA-DCA | WA3359193 | fire panel, device L1-S30 is missing | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 07:58:00 | Pass | System status displaying normal on departure
MSA-DCS | WA3358872 | reception, staff lunch room - Tombstones burnt out | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 12:00:00 | Pass | Repaired light
MSA-DCS | WA3358874 | Hothman - Laundry & Kitchen - Both kitchen & laundry sinks blocking and leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 08:30:00 | Pass | Unblocked kitchen and laundry and installed grates into kitchen to stop food going down drain
MSA-DCS | WA3358880 | Master control room - Inner D fence - section F01 - in constant alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 Jun 2020 | 2020-06-12 17:00:00 | 2020-07-08 15:33:00 | Fail | Investigated Zone alarm. This has been modified with new construction site, traced cables and found 3 PE beams connected in series. Traced fault to vegatatation in construction site. Advised maintenance.Job Complete
MSA-DCS | WA3358882 | Jeelia, B1- B1 Window leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-12 09:00:00 | Pass | WINDOW LEAK REPAIRED- RE SEALED
MSA-DCS | WA3358885 | Jeelia, B wing Laundry - leaking under hot water system | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 09:32:00 | Pass | Replaced trap washer
MSA-DCS | WA3358886 | Jeelia, A1/2 & 7 - shower heads blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 10:35:00 | Pass | Pulled apart 3 shower heads and cleaned out
MSA-DCS | WA3358887 | Jeelia, B2 & B4 - B2 sink blocking & B4 shower leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 11:40:00 | Pass | Removed hair and unblocked basin sinks
MSA-DCS | WA3358889 | unit 8, Front door & A/B control door - Front door not closing properly | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 07:47:44 | 2020-06-16 15:00:00 | Fail | Door lock replaced as instructed on front control door.
MSA-DCS | WA3358890 | Hakea Club - Roller door jams only comes down about 400mm | Hakea Prison | GMP-BR- HO | Building | Roller Shutters (BU) | UNIVERSAL DOORS | 2 | CLOSE | 08 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-25 11:45:00 | Fail | Repairs to roller door
MSA-DCS | WA3358897 | Unit 7, Cell H13- No Signal (tv good, arieal point & leadgood) | Hakea Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-09 13:30:00 | Pass | no issue found
MSA-DCS | WA3358899 | Unit 6, Plant Room- roof space plantroom floro lights not working above fire panel | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 11:30:00 | Pass | Repaired multiple faulty lights in unit 6 plant room
MSA-DCS | WA3358904 | Bakery- rotel oven not starting up | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-08 10:30:00 | Pass | completed 10.30am 8/6/20
MSA-DCS | WA3358905 | Unit 1, Cell A10- light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-08 11:00:00 | Pass | Repaired light
MSA-DCS | WA3358907 | Unit 1, B & D- Light switch not working,not turning on in cell D11, D06, B02 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 13:00:00 | Pass | Investigate and repair lights in unit 1 d11
MSA-DCS | WA3358908 | Unit 1, D Wing- Light switch in cell not working, not turning on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-10 10:00:00 | Pass | Investigate and repair d wing light switch in unit 1
MSA-DCS | WA3358930 | Unit 1, B & D, Cell D11- Both lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 11:30:00 | Pass | Investigate and repair unit 1 cell d11 lights
MSA-DCS | WA3358931 | Unit 7, A Wing, Cell A1- main lock intermittently not double locking with various key sets | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-08 10:30:00 | Pass | repairs to lock
MSA-DCS | WA3358934 | Unit 5, Court Yard- side gate between 4/5 in unit 5 lock jarring on second turn. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-03 13:00:00 | Fail | On site remove lock for repairs, requires rebuild.Attend site remove lock, secure gate with chain and padlock. Rebuild lock in workshop and re install lock into gate.
MSA-DCS | WA3358937 | Unit 14, Cell B15- Shower drain blocked- flooding the cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 12:00:00 | Pass | Used plunger and acid to clear blockage in shower drain.
MSA-DCS | WA3358941 | Unit 14, C Wing, Cell C11- Shower & sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 13:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3358946 | Unit 14, D12 - Shower is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 14:00:00 | Pass | Used plunger and acid to clear blockage in shower drain.
MSA-DCS | WA3358947 | Unit 14, B5 - Tap keeps dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 15:00:00 | Pass | Replaced leaking spindle
MSA-DCS | WA3358949 | Unit 7, B Wing- Laundry lights faulty, tripping | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 08:30:00 | Pass | Repaired faulty lights in unit 7 laundry
MSA-DCS | WA3358956 | Medical centre/Reception - Lights not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 09:30:00 | Pass | Replaced faulty timer
MSA-DCS | WA3358962 | Monitor room - Camera 36 - no moving on alarm and joy stick | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 08:55:52 | 2020-06-19 14:45:00 | Fail | Camera 36 monitored for 5 days and had no further failures. No further action required.
MSA-DCS | WA3358967 | Unit 3 - C Wing C1 SINK BLOCKED | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-22 09:00:00 | Fail
MSA-DCS | WA3358968 | Unit 2, A & C- Vinyl is lifting & bubbling in the dayroom, possible trip hazard | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-30 10:30:00 | Fail | DAMAGED VINYL REMOVED & REPLACED WITH NEW
MSA-DCS | WA3358969 | Unit 14, Cell B16- External lightswitch is broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-08 12:30:00 | Pass | Repaired damaged cell switch in unit 14 b16
MSA-DCS | WA3358970 | Unit 14, B&D laundry - light not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-08 11:00:00 | Pass | Repaired faulty lights in unit 14 laundry
MSA-DCS | WA3358995 | Unit 7, D Wing, Cell D7- Cistern is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-18 14:00:00 | Fail | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3358998 | Response gate - not opening via control panel in the control room | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 09:24:01 | 2020-06-08 15:30:00 | Pass | Attended Control Room and confirmed operation with Control Operators. Attended the Response Gate with SOG staff and tested operation of gate. Noted that thelock pins withdrew from locations, no derived from gate motor in pit. Lock pin activity confirms “Open” signal received at Gate. Requested maintenance manager refer to Marshal Beatie for action.
MSA-DCS | WA3359004 | Perimeter MDAS tamper Pole 14 in error & tamper pole 4 in error | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-23 09:10:00 | Fail | replaced faulty receivers & clear the fault from the system. parts used 2 x mdas receivers(seme stock)
MSA-DCS | WA3359005 | Gatehouse beam 15 has an unknown logic alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-11-13 09:29:00 | Fail | Parts ordered on LVM for replacement.Invoice raised for costs to date.
MSA-DCS | WA3359006 | Unit 4, Cell D2- Window not operational, keeps falling down | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-02 13:15:00 | Fail | SPIRAL BALANCES & WINDOW FEET RENEWED
MSA-DCS | WA3359033 | Pod 8, unit 3- Verandah light is not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 10:30:00 | Pass | Replaced fluorescent with led batten light
MSA-DCS | WA3359034 | Gate House - Front Entrance Lights in stairwell and Crypt faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 15:00:00 | Pass | Repaired and replaced faulty lights in gate house and crypt
MSA-DCS | WA3359077 | POD - PPTZ 3 no picture | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 08 Jun 2020 | 2020-06-08 14:21:29 | 2020-06-08 12:00:00 | Pass | closed off cost to date completed under WA3350488
MSA-DCS | WA3359080 | Maintenance Office, Power point damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 12:00:00 | Pass | Relocate damaged gpo
MSA-DCS | WA3359098 | gate house blue duress alarm light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-19 13:30:00 | Fail | Investigate duress alarm strobe. Requires replacing.Source parts and replace blue strobe.
MSA-DCS | WA3359100 | Security light at front of admin faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 10:00:00 | Pass | Investigate admin flood light. Requires replacement pe cell and ewp.
MSA-DCS | WA3359111 | Hothman, Whole unit - A wing water temperature appears hotter than B wing. | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 14:48:00 | Pass | Checked and adjusted tmv temperature to 42degs
MSA-DCS | WA3359126 | Unit 3, cell C4- personel lock not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-08 12:00:00 | Pass | repairs to lock
MSA-DCS | WA3359151 | Laundry, No 4 Wash Machine - showing AD Fault | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 11:23:13 | 2020-06-09 11:00:00 | Pass | Small Ipso AD Fault and not unlocking doorInspect & test WM. No physical faults found. Error report seen by technician. Instruct staff to monitor and log faults.
MSA-DCS | WA3359174 | Unit 2, top landing sink taps broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 13:00:00 | Pass | Remove existing damaged sink set. Supply and install new kitchen sink mixer to unit 2 top landing.
MSA-DCS | WA3359177 | Orientation centre/Office Lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 13:30:00 | Pass | Replaced fuse
MSA-DCS | WA3359179 | PDA computer is beeping | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 11:51:51 | 2020-07-02 15:30:00 | Fail | Traced bus cabling from the transponder and through the roof space of the Administration building. Found and reterminated multiple joins in the cable. Traced cabling from a telephone type connection in Admin to the receivers in the external RESET/OUTCARE BUILDING. Altered the text descriptions of the 2 receivers and MDAS transmitter 452 to indicate their correct locations. While the NO RESPONSE errors have now cleared and the area tested ok, the bus and power voltages at the receivers are less than ideal. Spoke to Security Officer Athol Van Blerk who has now requested that the RESET staff test the issued transmitter at the beginning of their shift. Security have been advised of the option of installing a fixed duress transmitter that would be secured permanently in Outcare and would always show up in Outcare when activated.
MSA-DCS | WA3359180 | WWTP no power to recirulation pump | Karnet Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 15:30:00 | Pass | Investigate wwtp pump power. Requires replacement parts
MSA-DCS | WA3359195 | Unit 2 - B Wing Grill clunky and 'jumpy' to start/ first 0.5 m teeth on drive bar sheared off | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 12:04:42 | 2020-06-10 18:30:00 | Fail | 08/06/20Inspected.Require parts.1.5m of track motor cog not aligned correctly due to bracket dropped.Returning 09/06/20.09/06/20Replaced gear track 1.5m. Aligned gear track. Motor is not adjustable due to very small tolerances10/06/20Recalibrate rack and pinion. Replace limit switches.
MSA-DCS | WA3359201 | Unit 4, B & D oven is missing the grill inside to protect the fan | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-13 10:05:00 | Fail | Replaced new Fan Guard in oven
MSA-DCS | WA3359217 | Unit 2, A9 - Cell door bottom hinge is moving on the frane side | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 12:31:05 | 2020-06-08 16:00:00 | Pass | Realigned door
MSA-DCS | WA3359218 | Unit 2, A14 - Cell Door Dragging on the Floor | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 12:34:05 | 2020-06-08 15:30:00 | Pass | Realigned door
MSA-DCS | WA3359224 | Unit 2, A wing - Grill Lock jamming when Opening | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 12:36:08 | 2020-06-08 15:00:00 | Pass | Serviced grille lock and realigned door.
MSA-DCS | WA3359227 | Unit 2, A4 - cell door dragging on the floor | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 12:39:41 | 2020-06-08 14:30:00 | Pass | Realigned door
MSA-DCS | WA3359230 | Unit 2, D3 - Cell Door jamming in the Frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 12:41:25 | 2020-06-08 14:00:00 | Pass | Realigned door
MSA-DCS | WA3359233 | Unit 2, A16 - Cell Door Top Lock Face Plate Missing Screw | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-08 13:30:00 | Pass | Rectified issue with door and realigned.
MSA-DCS | WA3359236 | Unit 2, D9 - no water to sink taps | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 12:44:58 | 2020-06-08 14:35:00 | Pass | Water to basin had been isolated explaining no water, when in isolated found cold tap to be leaking, replaced with new
MSA-DCS | WA3359238 | Unit 13 Floor peeling off in A&C wing kitchen area in between serving bench and Oven. | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-11-05 14:00:00 | Fail | DAMAGED SECTION OF FLOOR UPLIFTED & REPLACED
MSA-DCS | WA3359242 | Unit 2, B13 - Hot tap broken (¼ Turn Seized) | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 12:51:29 | 2020-06-08 15:30:00 | Pass | Basin set in duct had been pushed out of place, adjusted pipe work to fix
MSA-DCS | WA3359245 | kitchen, rational oven - Lights not coming on in Oven. Lights have been tested and are okay | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-22 14:00:00 | Fail | Replaced faulty transformer.
MSA-DCS | WA3359249 | Cabinet Shop - lock on cabinet shop door sticky | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-10 12:30:00 | Pass | Replaced bolts
MSA-DCS | WA3359251 | Unit 14, A & C - SHOWER DRAIN BLOCKED | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-15 10:00:00 | Fail | Used plunger and acid to clear blockage in shower drain.
MSA-DCS | WA3359252 | Unit 3 URGENT CONTROL AIR CON NOT WORKING | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-10 13:27:00 | Pass | Replaced controller
MSA-DCS | WA3359261 | Unit 3, Cell D6- toilet button faulty not flushing properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-22 13:00:00 | Fail | Inspected cell. Dismantled flush button. Cleaned paint and rubbish out of button to allow button to operate correctly.
MSA-DCS | WA3359266 | Unit 3, B11 - veiwing hatch taken out | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-08 15:00:00 | Pass | OBS WINDOW SLIDER RENEWED, PART FRAME REPAIRED
MSA-DCS | WA3359274 | Bakery - PROVER WAS ACTIVE THIS MORNING BUT AS OF 1040HRS THE PROVER IS NOT | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-08 15:58:00 | Pass | Start and finish times are not correct.Job started at 10.30 am and completed at 12:45pm.Was raised by the prison as we were leaving an earlier job. The WA from Programmed didn't come through for a couple of hours after.
MSA-DCS | WA3359317 | Unit 7, SCU, Cell B7- lighting circuit problem | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-18 11:30:00 | Fail | Investigated fault with b wing lighting. Removed all lights in cells and tested circuits. Found and repaired rodent damaged cables in plant room ducting.
MSA-DCS | WA3359319 | Unit 5, Cell B11- Bottom bunk light faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 08:30:00 | Pass | Repaired faulty lights in unit 5 b11
MSA-DCS | WA3359331 | Unit 2, Cell B7- top bunk light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 14:30:00 | Pass | Repaired faulty lights in b7 unit 2
MSA-DCS | WA3359333 | Unit 2 and admin MDAS no response-SEME on site | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-08 14:30:00 | Pass | Located receivers on MDAS PC map. U2 TR9.0.0 tested as faulty. Removed and replaced PCB. ADMIN 2.4.3 found to be water damaged. Removed and replaced PCB. Re-sealed. Cleared alert messages and stress tested ok. Parts used:Bosch receiver EA102A-304Consumables
MSA-DCS | WA3359342 | Unit 7, Isolation valve is faulty (whole unit) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-20 11:30:00 | Fail | 10/6/20- prep work. Marked out and cut concrete.20/6/20- Removed concrete. Isolated water. Repaired valve and pipework. One crimp conecting old pipe to new pipe failed and had to be removed and recrimped. Turned water back on. Tested. Reinstalled concrete footpath.
MSA-DCS | WA3359350 | Unit 2, staff lunch room - light needs repairs | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-23 12:00:00 | Fail | Checked damaged lights in unit 2, sources suitable replacements. Picked up and installed and tested
MSA-DCS | WA3359366 | Unit 14, D3 - cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 08:30:00 | Pass | Repaired faulty lights in unit 14 d3
MSA-DCS | WA3359372 | Unit 7, B wing - Leaking around base of tap in B Wing kitchen. Possibly washer or sealer required | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-19 15:00:00 | Fail | Retightened the lock nut on basin outlet in kitchen cupboard. Tested for leaks.
MSA-DCS | WA3359384 | Gate House- Response gate in secure area to sterile area not opening on drive unit | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 14:57:11 | 2020-06-09 12:00:00 | Pass | Adjusted clutch, tightened. Test gate operation, all okay now
MSA-DFES | WA3358857 | Room front entrance - roof leak, causing flooding and water damage to wall, roof & carpet. | DFES Regional Office - Belmont | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 08 Jun 2020 | 2020-06-08 17:00:00 | 2020-07-24 08:30:00 | Fail | Replace section of badly rusted box guttering
MSA-DFES | WA3359001 | Room near front entrance - Carpet wet and water damaged due to roof leak | DFES Regional Office - Belmont | GMP-BR | Flooring | Carpet (FL) | Facilities First Australia Pty Ltd | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 16:30:00 | Pass | Carpets dried and cleaned
MSA-DFES | WA3359039 | Room 16, Middle Dorm- Water leaking from ceiling upstairs | CFRS Fremantle | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-17 15:00:00 | Fail | Inspected roof for leaks. Cleared out all downpipes and tested, leak resolved. Applied stain block, patched and painted ceiling water damage. Job complete
MSA-DFES | WA3359067 | eradicate Red back spiders, Ants and Moth infestation | CFRS Hope Valley | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 13:00:00 | Pass | Carried out treatments to control spiders, ants and pantry moth. Gel bait appropriate spots internally to assist control of ants. Placed 2x AF pads in kitchen to assist control of pantry moth. Residual spray external areas targeting ant activity and entries to nests in lawns and paved areas.*Pantry moth is a stored product pest and will be coming from a cereal or grain product. Recommend locating open packaging in kitchen where (cereal, flour, rice or similar) infestation is originating from and dispose of.
MSA-DFES | WA3359072 | Office & Gym - Faulty Lighting | CFRS Joondalup | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-08 14:30:00 | Pass | COMPLETED
MSA-DFES | WA3359403 | Engine room roller door 1 as door is going up stop half way and comes back down-see notes | CFRS Ellen Brook | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 13:15:00 | Pass | Noted no faults whilst on site. Noted 1 safety beam out of alignment and realigned and cleaned . Tested operations all okay.
MSA-DTAG | WA3358939 | Level 11, chambers - Plaster is peeling from 1 wall & 1 column in Coroner Vicker’s Chamber | Central Law Courts | GMP-BR-HO | Building | Internal Walls (BU) | PPM Project Painting & Maintenance | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 09:00:00 | Pass | Prepare and paint
MSA-DTAG | WA3358944 | Level 6, Lift 3 is out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 14:00:00 | Pass | Requires installation before unit can be returned to service. Out of service for repair.- Not chargeble
MSA-DTAG | WA3359116 | Lvl 3, Court 33- No power to the computer at the JSO desk | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 13:30:00 | Pass | Job complete
MSA-DTAG | WA3359117 | Lvl 15, Plant Room- GPO next to the electrical switchboard has no power | Central Law Courts | WSM-BR-SITE | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 08:00:00 | Pass | Job complete
MSA-DTAG | WA3359123 | 1903 ground Outside court 6 & 7 removal of human excrement | Supreme Court | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 16:15:00 | Pass | Job carried out as per work order.
MSA-DTAG | WA3359304 | ground various Card readers on multiple doors faulty | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-10 11:45:00 | Fail | 8/6/20 - Dylan Parslow, Dean SimpsonFound 4 door controller in court 3 with burnt out components, replacement required.BRAF Submitted. 9/6/20-10/6/20 - Dean SimpsonReplaced faulty Tecom 4 door controller.Configured to the main system.Tested access cards on doors, all working.
MSA-DTAG | WA3359416 | Special Clean in cell 3 - as prisoner soiled herself | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 17:30:00 | Pass | Job carried out as per work order.
MSA-DTAG | WA3359438 | sally port and control room intermitently working - see notes | Joondalup Courthouse | GMP-BR-HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-07-13 09:30:00 | Fail | Job completed - supplied and installed push button replacement
MSA-DTWD | WA3358893 | Male toilet L Block Ground floor - The urinals in the male toilet are overflowing when flushed. | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 2 | CLOSE | 08 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 10:00:00 | Pass | Inlet valve on cistern turned down to reduce flow and drain cleaner and plunged to release some build up urinals no longer overflow.
MSA-DTWD | WA3359009 | F block, FG23 - Gas detection system fault | Carlisle Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | GASTECH AUSTRALIA PTY LTD | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-08 15:35:00 | Pass | COMPLETED
MSA-DTWD | WA3359010 | A block ground Alarm panel fault RAS dgp Fail | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 16:29:00 | Pass | 08/06/2020, 1245-1545RAS fail and DGP failFound DGP 4 offlineChecked plug pack and found that it was faulty and tested power point,Power point all okReplaced 16VAC plug pack and 7aH battery.Found RAS 4 bringing the AUX power down to 0 VDCReplaced RAS and checked AUX power all okRAS fail and DGP fail has restored.Checked Rosslare keypad not unlocking strikeTested strike all okTested cable all okElectrical strike set to power to lock.Tested single door controller and found that the relay doesnt change statewhen keypad grants them access.Single door controller 14 would need to be replaced.Also checked issue with front door not locking at the correct time found thatthe time was out by 55 minutes.Edited time and tested lock all ok
MSA-DTWD | WA3359019 | B block L1 B105 Problem with Leederville access control reporting-see notes | Leederville Campus | GMP-BR | Security | Monitoring (SE) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-08-03 08:00:00 | Fail | Attended site and spoke to John re reports for site.Tried to run reports as per site request but was unsuccessfull as the reporting tool and licences arelocated on the filemaster/Server in the 30 Aberdeen st server room.Emailed site re Windows log in but so far we have been unsuccessful with this info.Sean McGrath advised that job can be closed out.
MSA-DTWD | WA3359031 | Flickering fluro in safe room | Armadale Campus - 40 Commerce Ave | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 15:32:00 | Pass | Attended site and signed in. Located faulty light throughout site, replaced tubes and starters as required and replaced 1 x unserviceable light in safe room with led panel. Tested all okay. Job complete
MSA-DTWD | WA3359036 | Student Kitchen - Broken tap to hot water urn | Armadale Campus - 40 Commerce Ave | GMP-BR | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 1 | CLOSE | 08 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 10:15:00 | Pass | Called out for Broken RHEEM tap. Drained tank with faulty tap, took awhile. Replaced RHEEM tap, ran water and filled wall mount. Ran further tests and checked under pressure. Normal operation
MSA-DTWD | WA3359040 | Broken toilet fan cover with exposed components | Armadale Campus? 45 Commerce Ave | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 13:15:00 | Pass | Attended site and signed in. Located upstairs toilet and found fan cover fallen down. Re secured to fan and tested all okay. Job complete
MSA-DTWD | WA3359056 | Childcare 1 - flickering fluro | Armadale Campus? 45 Commerce Ave | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 13:45:00 | Pass | Attended site and signed. Located childcare room, found all lights to be on and 1 flickering. Replaced both tubes and starters and clean diffuser. tested all okay. Job complete
MSA-DTWD | WA3359159 | T block auto door not unlocking on timer is locked continuously | Munster Campus (ACEPT) | GMP-BR | Building | Automatic Doors (BU) | Securex Security Systems & Services | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 10:55:00 | Pass | 11/06/2020, 945-1000Updated door 2 programming, added Timezone 1 and relay group 32. Tested all ok.
MSA-DTWD | WA3359243 | P block G16 Broken curtains | Midland Campus | GMP-BR | Building | Windows (BU) | NEYLOR | 3 | CLOSE | 08 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-27 13:39:00 | Fail | Installation all complete & invoice & Work order attached- installed new blinds
MSA-DTWD | WA3359248 | ground E block walkways blown security and walkway lights | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 08 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-10 12:30:00 | Pass | Lights rectified as requested
MSA-DCA | WA3360556 | dressing room valve needs to be replaced and constantly running | PICA-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 13:28:00 | Pass | Replaced faulty inlet valve and ministop
MSA-DCS | WA3359651 | Cell call system has activated | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 06:38:00 | 2020-06-29 16:30:00 | Fail | Reconfigured windows firewall and cell guard settings, test cell call and check audio file log. Cell call systems back to normal operations.
MSA-DCS | WA3359668 | PTZ camera 17 & 22 not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 07:16:37 | 2020-06-09 14:30:00 | Pass | Attended site checked and found PTZ17 no picture in Control and equipment room. Checked on field in EC cabinet found signal from camera is ok. Located the problem to be the transmission problem. Reboot Fiber modems and tested all ok after. Checked PTZ 22 is working ok. Can’t see the problem.
MSA-DCS | WA3359719 | Unit 2 Control room door lock jammed | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 06:30:00 | 2020-06-10 16:15:00 | Fail | Supplied and fitted new cylinder.
MSA-DCS | WA3359760 | Sterile Zone Obs Post 1,Below Obs Post 1- Electrical Pit Lid needs reseating | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 12:00:00 | Pass | This job is for an electrician
MSA-DCS | WA3359770 | Karakin yard- damaged pole light (smashed) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-17 11:00:00 | Fail | Replaced flood light
MSA-DCS | WA3359772 | Unitt 4 L Block Cell 2 bottom bunk light is not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 10:30:00 | Pass | Replaced faulty light fitting
MSA-DCS | WA3359775 | Unitt 4 L Block Day room fan switch is broken needs a new mech | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 09:30:00 | Pass | Replaced faulty switch mech
MSA-DCS | WA3359798 | Unit 4 L Block Cell 3 main light not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 09:00:00 | Pass | Replaced light tubes
MSA-DCS | WA3359800 | CCU Unit 3 Cell CC4 bedside light not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 08:30:00 | Pass | Replaced light fitting with LED
MSA-DCS | WA3359810 | Control Room - Fire alarm in unit 7 is constantly activating | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 08:35:14 | 2020-06-10 08:34:00 | Pass | Unit 7 showing airflow fault. E Wing pipe 3 at 38%. Cleaned all sample points. Airflow back to 122% and fault cleared.
MSA-DCS | WA3359812 | Gate house lights not working in control room & above restraints locker | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-19 08:30:00 | Fail | Investigate and repair lights in Gatehouse
MSA-DCS | WA3359855 | Intensive support unit- Time stamp on monitors is 10mins in advance | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 09:02:27 | 2020-06-09 10:42:00 | Pass | Time stamp on ISU (harding) NVR changed to correct time, NVRs 2 to 6 networked to NVR1 and set to change link to NVR1s time every 24 hours.
MSA-DCS | WA3359858 | unit 4 camera 60 has no power -SEME on site | Bunbury Regional Prison | SPA-BR | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2021-06-17 11:00:00 | Fail | Recable PTZ 60 and other admin cameras. Install and program new PTZ 60 digital camera.
MSA-DCS | WA3359880 | unit 1 B wing shower keeps getting jammed shut | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-23 10:00:00 | Fail | Inspected all showers in both b and d wings. No issues found. Guards unable to specify problem.
MSA-DCS | WA3359884 | Unit 7, B Wing camera freezing on an off throughout the day. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-10-22 16:40:00 | Fail | Repaired camera comms issue in Unit 7.If fault reoccurs, B Wing Camera will need to be recabled with underground Cat6 as it is currently cabled with RG59 and Baluns.Job Complete
MSA-DCS | WA3359976 | Unit 3 POD 9 Cell 9 - faulty power to amplifier | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-11 14:00:00 | Pass | Replaced faulty power point
MSA-DCS | WA3359985 | gate house comand microphone faulty | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-09 11:47:00 | Pass | Microphone removed and soldered joints. Checked microphone now operating correctly (area between key issue and airlock)
MSA-DCS | WA3360038 | Kitchen, hallway door- door closer damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-12 12:30:00 | Pass | New door closer installed
MSA-DCS | WA3360256 | Unit 5, Cell B14- Cell window cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 10:59:14 | 2020-06-22 13:30:00 | Fail | REGLAZE CELL WINDOW
MSA-DCS | WA3360303 | Kitchen - Brat pan faulty | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 11:13:52 | 2020-06-09 13:30:00 | Pass | Kitchen Brat Pan no.2 faulty. Check pan & controls. Dismantle, check for gas leaks. Clean ignition probe. Dry water off connection. Assemble & test. All working correctly.
MSA-DCS | WA3360358 | ground Reception and Hallway Area Replace faulty lights with LED (old ones exploding)-see notes | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-09 15:00:00 | Pass | Replace faulty lights
MSA-DCS | WA3360422 | Assessments, Room 27- Ballast is damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-11 09:00:00 | Pass | Replaced light
MSA-DCS | WA3360458 | master control room, eastern outer sally port not working | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 09 Jun 2020 | 2020-06-09 16:03:36 | 2020-06-11 12:00:00 | Fail | JOb completed - Two technicians return to site with scissor lift. Traced fault to the lock motor. removed motor. Stripped, clean and renew/rebuild brushes. Re-build and test. Re-install motor and test, all okay. Changed two (2) batteries. Doors back in full operation.
MSA-DCS | WA3360579 | Unit 2 D3 Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2021-01-11 10:00:00 | Fail | Replaced damaged floor tiles in shower recess and resealed.
MSA-DCS | WA3360583 | Unit 2 D9 Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-12-10 09:30:00 | Fail | Replaced damaged floor tiles in shower recess and resealed.
MSA-DCS | WA3360611 | Eyre, kitchen- Sink is leaking around tap | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-10 12:42:00 | Pass | Replaced kitchen mixer tap
MSA-DCS | WA3360620 | Unit 8, A & B Wing- Prisoners receiving shocks off taps when turned on | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 09 Jun 2020 | 2020-06-09 17:18:39 | 2020-06-10 09:00:00 | Fail | Electric shock test and report.
MSA-DCS | WA3360632 | Vegetable Prep- disconnect electrical supply to potato peeler for replacement | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-11 07:00:00 | Pass | Disconnected and reconnected potato rumbler in veggie prep
MSA-DCS | WA3360647 | SITE COST rear patio door leading out patio will not open with fob | Hakea Prison | WSM-BR-SITE | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 09 Jun 2020 | 2020-06-09 17:30:31 | 2020-06-10 07:30:00 | Fail | Job completed - Copier door offline. Traced cable, found damaged core in panel. Re-terminated and tested.
MSA-DCS | WA3360651 | Unit 2 A16 Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-07-17 14:30:00 | Fail | Attended site and assessed required works.Re Attended site and removed all cracked and damaged floor tiles.Sourced and replaced floor tiles, regrouted and sealed.
MSA-DCS | WA3360653 | Unit 2 D5 Toilet Leaking From Under Base Of Pan When Flushed | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 13:39:33 | 2020-06-15 08:05:00 | Fail | No sign off water leaking from toilet seems to be wet from shower so silcone around bottom off toilet to try prevent water gathering around toilet
MSA-DCS | WA3360659 | Unit 2 A15 Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-07-21 10:30:00 | Fail | Attended site and assessed what repairs where required, removed sharp dangerous floor tiles.Reattended site and replaced all damaged and broken floor tiles in shower recess. Regrouted and sealed new tiles.
MSA-DCS | WA3360669 | Unit 1 D14 Loose Tiles Around Shower Drain | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-07-21 14:00:00 | Fail | Attended site and assessed what repairs where required.Sourced and picked up new floor tiles.Reattended site and replaced damaged and cracked floor tiles in shower recess.
MSA-DCS | WA3360754 | Door control screen is freezing | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Jun 2020 | 2020-06-09 18:59:00 | 2020-06-09 16:00:00 | Pass | Intermittent fault.Investigated workstation, repaired software faults.Tested OKMonitored for correct operation.Job Complete
MSA-DCS | WA3360761 | Unit 4 B12 Cell Call Faulty. A lot of static, unable to hear prisoner | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 14:59:16 | 2020-06-09 17:30:00 | Pass | Attended site checked and found U4 B12 cell call point faulty, it is hard to hear in office. Replaced the faulty cell call point and tested all ok.
MSA-DCS | WA3360871 | Bravo-1 Charlie -4 Outside perimeter lights are not working behind unit 13-14 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Jun 2020 | 2020-06-09 22:31:37 | 2020-06-09 19:30:00 | Pass | Electrician required.
MSA-DCS | WA3360874 | B-1 C-4 Outside perimeter lights are not working behind unit 13-14 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 09 Jun 2020 | 2020-06-09 23:27:10 | 2020-06-10 14:30:00 | Fail | Reset perimeter lights
MSA-DFES | WA3359755 | Swipe access system is not working | DFES Education and Heritage Centre | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-11 15:00:00 | Fail | 9/6/20 - Dylan Parslow, Ryan VestyInvestigated issues with Pacom System.Found all devices offline.Found faulty 2 door controller shorting out LAN.Authorized by Steve Cassie to replace door controller.All devices working excluding the theatre door, revisit required.11/6/20 - Dylan Parslow, Ryan VestyInvestigated issues with theatre door not working.Found 2 door controller not communicating to main controller. Probably caused by other door controller shorting lAN.Authorized by Brendan Ryan to replace door controller.Replaced and tested all onsite equipment. All working ok.
MSA-DFES | WA3359944 | 2 flouro's out and flexi cords damaged | CFRS Duncraig-Main Building | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 08:00:00 | Pass | Collected Scissor from East Perth at 0600Arrived onsite and signed in at 0700, we located 2 faulty lights, 1 in tunic room and 1 in engine room and repaired them both. We also investigated reported damaged roller door cables connected to roller doors, 2,3 and 4. I have notified staff to call it through as another fault through Assa Abloy who look after and service the auto doors. Notified staff of works completed and signed out and left site at 0800
MSA-DFES | WA3359956 | Dorm 1 Shower head is loose | CFRS Duncraig-Main Building | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-25 09:00:00 | Fail | Fit new riser rail and shower head
MSA-DFES | WA3360596 | main admin door keeps slams shut-see additional notes | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-07-06 09:45:00 | Fail | Replaced faulty door closer with new door closer. Painted face of door to cover patch where old door closer was removed
MSA-DFES | WA3360826 | RETROSPECTIVE WORK ORDER DO NOT ATTEND-STAFF ONSITE. NO OFFENCE DETECTED. | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-09 15:30:00 | Pass | Despatch Comments:ZONE 22 - REAR DOOR -Patrol Resolution:STAFF ONSITE. NO OFFENCE DETECTED.Site Inspection / Departure: Initial Site Inspection:EXTERNAL CHECK, INTERNAL & EXTERNALSystem Status on Arrival:SYSTEM DISARMED ON ARRIVALVisual Appraisal:NO SIGN OF FORCED ENTRYSystem Status on Departure:SYSTEM DISARMED
MSA-DTAG | WA3359706 | Level 10 Alarm sounding in communications room | Westralia Square | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jun 2020 | 2020-06-09 17:00:00 | 2020-06-09 10:22:00 | Pass | Found UPS in Rack 3 has battery alarm. System warning is "batteries at end of life". Will require replacement. Customer requested to close off job and submit recommendation for replacement.
MSA-DTAG | WA3359894 | Court 37 flickering light | Central Law Courts-Main Building-Level 3 | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-09 12:45:00 | Pass | Job complete
MSA-DTAG | WA3359942 | L23-32 Bookable Area & L23-01 Lift Lobby West lift lobby west opened won't close-see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-09 11:30:00 | Pass | Attended site. No fault found with Access Control. Reset both auto door motors and checked, all OK.Job completed.
MSA-DTWD | WA3359717 | Workshop - 3 high bay lights are out | Naval Base | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 09 Jun 2020 | 2020-06-11 17:00:00 | 2020-07-02 09:00:00 | Fail | Attended site and signed in. Located scissor on site, located faulty lights in workshops. Removed old hi bay lights and replaced with new Led hi bays. Re attached some hanging cabling to cable tray outside. Tested all okay. Job complete
MSA-DTWD | WA3359759 | E Block E30 SSK – Tap at station 2/3 leaking badly | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-09 09:23:00 | Pass | Replace spout
MSA-DTWD | WA3359842 | T-Block ,Room T005- the walkway Hagar light timer is not working. | Joondalup McLarty Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-10 14:00:00 | Pass | Timer replaced with new
MSA-DTWD | WA3359867 | A block L1 West male urinal continuously running | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-09 13:58:00 | Pass | Attended site,Locate cistern to male urinal running constantly. Sourced parts from local supplier for repair, return to site. Supply and install service kit to inlet and outlet valves to achieve repair. Tested works on completion
MSA-DTWD | WA3359906 | G block ground outside courtyard Drink fountain repair to Lever | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-11 12:15:00 | Pass | Arrived on site 11.40 long wait to sign in - attended to fountain to repair - faucet was working well and was not broken (perhaps repaired already?) checked unit no issues.Tech could not reset password or log on to Promap.
MSA-DTWD | WA3359935 | A Block, AF20 exit/entry door- Electronic keypad lock not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 14:00:00 | Pass | 15/06/2020, 1030-1400Tested rosslare keypad and found that the relay was switching from NO to NC and the relay was getting stuck into NCstatePower cycled rosslare keypad and tested again had same fault which showed intermittently.Also found single door controller not switching state when needed. Power cycled single door controller and tested againfound the same issueReplaced both devices single door controller and rosslare keypad AC-Q41SBTested keypad, egress and lock all ok
MSA-DTWD | WA3360392 | canteen Rear security sensor light faulty | Rockingham Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-12 14:45:00 | Pass | Attended site, replaced faulty sensor light out the back of canteen. Job complete.
MSA-DTWD | WA3360525 | A Block, Male toilet urinal is blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 17:30:00 | Pass | Unblocked urinal and fix cistern so would flush correctly
MSA-DTWD | WA3360637 | L Block, Air Conditioning wont adjust to warm, blowing out cold air | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-18 14:33:00 | Fail | Adjusted the temperature on the bms these temps revert back to old setting . Work being carried out by storm a contractor on site on the chillers. if Tafe require bms people to come out the college will get them to look at this problem to . Awaited for any problems, no issues from the Tafe closed off. Advised by the Tafe to close out the job as contractor was on site. please note circled no - due to awaiting confirmation on no further issues. This job is now complete. 1 hour labour charged only.
MSA-DTWD | WA3360644 | B Block, G Floor, Corridor- Door locks are faulty on the two exit doors – West End. | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-08-28 14:35:00 | Fail | B Block - G Floor - Door locks faulty on two exit doors.See Nathan.Door locks repaired and replaced.
MSA-DTWD | WA3360727 | Room B3- Rodent in ceiling space, may require baits | Rockingham Campus | GMP-BR | Pest Control | General Pest (PC) | JODAN PEST CONTROL | 2 | CLOSE | 09 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-10 09:25:00 | Pass | indoor rodent control
MSA-DTWD | WA3360740 | E Block, Delivery Loading Bay – Faulty tap | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 09 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-23 14:54:00 | Fail | Serviced leaking taps for loading dock wash down station.
MSA-DTWD | WA3360762 | E Block, G Floor, restaurant - Air con is not working – A/C 4 calling for cooling | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-17 09:00:00 | Fail | Found BMS showing room temperature at 43 deg C. Checked and found no issues with unit. Client informs that external BMS technician to attend.Found a return air ducting box in ceiling is not correctly installed over grill and was asked to rectify. Returned with assistance and re installed ducting. Checked operation. All ok. Cleaned up work area. Emailed signature slip to client for signature and return.
MSA-MRWA | WA3360432 | L2 211 & 295 Adjacent office lights issue mirrored, -see notes | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | LYNX INTEGRATED SYSTEMS | 1 | CLOSE | 09 Jun 2020 | 2020-06-10 17:00:00 | 2020-06-09 17:00:00 | Pass | Field Completed, no further details provided
MSA-MRWA | WA3360820 | front gate exit gate not closing | Jandakot Depot | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 0 | CLOSE | 09 Jun 2020 | 2020-06-09 20:29:17 | 2020-06-09 18:00:00 | Pass | 9/6/20 - Dylan Parslow, Ryan VestyInvestigated issues with exit gate.Determined fault at ground loop controller.Tested all fuctions, all ok.Updated integritti and pc time.
MSA-DCA | WA3361062 | Level 1, Doors leading to Function Room Foyer - Glass door is slamming shut very fast | Maritime Museum Victoria Quay | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 10 Jun 2020 | 2020-06-10 17:00:00 | 2020-07-17 11:45:00 | Fail | Door closer has no more adjustement in it and will need to be replaced. Materials on order . Concealed pivot door closer to large glass entry door replaced with new and surrounding plaster board patched and painted
MSA-DCA | WA3361378 | Roof - extractor fan on the roof cable has been vandalised | King Street Arts Centre | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-10 16:05:00 | Pass | During maintenance identified power cable on the lift motor room exhaust fan has been cut from vandals.Reported to pfm and raised job. Isllated power and tagged out.Replaced damaged wiring and conduit.Secured conduit to fan deck with saddles.Confirmed correct operation of fan motor.
MSA-DCA | WA3361594 | Public area faulty air sensors | State Library of WA-Main Building-Level 3 | GMP-BR | Electrical | Lighting, Internal (EL) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-10 16:30:00 | Pass | Attended call-out. Unable to access Promap on device. Contacted Programmed tech support and logged issue. Programmed FM approved works to proceed u til Promap functioning again.Isolated and disconnected 3 decommissioned pneumatic sensors and 2 decommissioned CSI voltage temp sensors.
MSA-DCA | WA3361818 | Green room emergency light not working-photo to follow in email | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-WC - In Front of Green Room | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | Techworks Electrical | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-01 10:26:00 | Fail | 1/7/20209:30am-10:30amReturned to site and decommissioned the old fitting off the nexus system, then went out to the field and replaced the faulty exit light with the new one, once this awesome inreturned to the pc and re-commissioned the new fitting in the appropriate place.
MSA-DCS | WA3361021 | Remove and repair pump #1 | Hakea Prison | SPA-GR | Mechanical Services | Pumps (MS) | WESTERN IRRIGATION PTY LTD | 3 | CLOSE | 10 Jun 2020 | 2020-06-16 17:00:00 | 2020-10-14 13:00:00 | Fail | 12-6-2020 - Remove pump for offsite assessment.14/10/20 - Installed new Grundfos pump, replaced faulty indicator lights and corroded discharge, test and commissioned the new pump.
MSA-DCS | WA3361023 | dairy lunch room zip autoboil not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 10 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-12 16:35:00 | Pass | on arrival no power to unit. A40165207E Zip AutoboilThermal overload tripped.checked unit allowed up to temp 3 times and all working ok. unit is agedappeared to be running well.customer to monitor moving forward if fault reoccurs perhaps replace due to age.Tech could not get on to promap could not reset password
MSA-DCS | WA3361054 | Unit 4, A wing, cell A1 - sink leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-18 16:00:00 | Fail | Replaced leaking spindle in basin tap
MSA-DCS | WA3361086 | Education 1, Class 3- report of gas smell for heaters | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 11:25:00 | Pass | Inspected gas heater. No leaks found.
MSA-DCS | WA3361123 | Unit 1, B & D - Basin tap leaking in cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-18 08:00:00 | Fail | Replaced leaking spindle in basin tap.
MSA-DCS | WA3361143 | Admin, Corridor - Welded hinge on safe snapped off | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 14:30:00 | Pass | HINGE RE WELDED ON SAFE DOOR
MSA-DCS | WA3361166 | Unit 1, Cell B5- Main lock Faulty, cannot lock door | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 08:48:06 | 2020-06-10 11:00:00 | Pass | serviced main lock on door
MSA-DCS | WA3361213 | Unit 3, Office- hot water urn faulty | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 09:15:40 | 2020-06-11 09:30:00 | Fail | Replaced solenoid and cleaned tap
MSA-DCS | WA3361216 | Unit 3, bathroom near cell 38- window frame is damaged | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-08-17 14:00:00 | Fail | INSTALL NEW WINDOW AND FRAME
MSA-DCS | WA3361217 | CRIPT, gate - maxpro slave computer with no power | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 09:15:40 | 2020-06-23 09:30:00 | Fail | Replaced power supply in. slave PC. Slave machine back on-line .
MSA-DCS | WA3361218 | CRIPT, gate - NVR 1 - shu disk failed | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 09:18:45 | 2020-07-01 15:30:00 | Fail | Loaded patch into NVR for replacement HDD, removed failed HDD caddy and installed new HDD and returned to NVR. Rebooted NVR, installed new drive and instructed NVR to rebuild RAID configuration. Alarms showing clear.
MSA-DCS | WA3361240 | perimeter tamper alarm zone H2 MW high TX-SEME on site | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 09:26:45 | 2020-06-10 12:00:00 | Pass | Traced fault to warped cover on ULTRAWAVE unit transmitter side. Replaced with van stock and tested ok to control. Checked multiple IR beam/microwave sets for insect infestation. Recommend pest control contractor to spray perimeter posts.
MSA-DCS | WA3361286 | Hotham, Office toilet- Rear seal has perished and is leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-10 13:45:00 | Pass | Removed cistern replacing key seal then reinstalled
MSA-DCS | WA3361289 | Unit 13, A & C - Fire alarm going off in duct between A15 & 16 | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 10 Jun 2020 | 2020-06-10 13:52:41 | 2020-06-10 13:38:00 | Pass | Unit 13 VESDA cell AC & BD 15/16Attended site and found cell 16 sample pipe 1 blocked with tooth paste.Cleaned & Cleared sample point cell 16 OK.Cleaned & Cleared sample point cell 15 OK.
MSA-DCS | WA3361293 | unit 6 lunch room carpet damaged and worn/to be replaced/trip hazard | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-22 11:03:00 | Fail | SUPPLIED AND INSTALLED NEW CARPET TILES AND THRESHOLD TRIM IN DOORWAY
MSA-DCS | WA3361297 | Unit 14, A & C - A/C 3/4 sensor displaying fault. Main panel showing 'isolate faulty | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 09:57:00 | 2020-06-11 08:02:00 | Pass | Unit 14 vesda cell 3/4 not resetting.Attended site & utilising blower vac cleared sample pipe 2.No access at time of attendance into the cell.Revisit required.
MSA-DCS | WA3361346 | Unit 7, Burst pipe S wing SITE COST | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 10 Jun 2020 | 2020-06-10 14:24:23 | 2020-06-10 15:40:00 | Fail | Didn’t receive work order until 12:30 pm had been onsite since 9:00 am repairing shower taps and burst pipe
MSA-DCS | WA3361383 | Unit 7, G Wing cleaning cupboard- Ballast is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-11 13:00:00 | Pass | Repaired light
MSA-DCS | WA3361388 | Orientation, PSO office - Lights flickering (requires high ladder) | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-22 13:30:00 | Fail | Repaired lights
MSA-DCS | WA3361406 | Unit 4, B Wing, Cell B6 - Toilet is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-19 12:00:00 | Fail | Replaced inlet valve and outlet rubber inside cistern.
MSA-DCS | WA3361408 | Unit 3, Cell D11- Window not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-07-01 14:30:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3361413 | Unit 1, A7 - Cell doorlocking, jamming in frame. | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 11:06:55 | 2020-06-10 14:45:00 | Pass | realigned door to rectify issue
MSA-DCS | WA3361428 | Bakery - Berto mixer making a machanical/grinding noise | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 11:18:37 | 2020-06-11 15:30:00 | Fail | 11.06.2020Arrived at site liaise with kitchen and reception, walk to the bakery, identify faulty mixer, remove panels, test/fault find diagnose and found a slight noise coming from the top motor bearing would recommend replacing at some point but okay for use at the moment, advised to keep using until fault gets worse or happens again.
MSA-DCS | WA3361494 | Level 1 - no access to parts of the building using swipe card access | East Perth | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jun 2020 | 2020-06-10 15:49:36 | 2020-06-10 15:45:00 | Pass | Found c6000 dead and not responding reset and still no response checked power c6000 replaced and tested ok
MSA-DCS | WA3361503 | Unit 14, A & C - leaking water fountain, leaking all over the floor towards A winf office | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 03:52:56 | Pass
MSA-DCS | WA3361516 | Unit 3 CONSOLE DISPLAYS NETWORK ERROR MESSAGE ON PANEL. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 11:53:00 | 2020-06-10 13:30:00 | Pass | Unit control console showing Network area on following nodes: 122, 121, 21, 133. All these nodes are associated with new build site. NOTE: Error messages have been showing on all consoles in this Prison from the last six weeks originating from new installation work.
MSA-DCS | WA3361519 | Unit 7, S Wing- Tiles cracked & grout missing from numerous joints causing water to seep | Hakea Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-10-28 12:06:00 | Fail | RE NEW SILICON JOINT ON FLOORING - RE NEW GROUTING TO ALL WET AREAS
MSA-DCS | WA3361641 | entry building - faulty light, wire that goes to the globe snapped | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 13:00:53 | 2020-06-12 10:00:00 | Fail | Replaced faulty downlights
MSA-DCS | WA3361643 | Kitchen - Meat slicer failed test and tag, faulty | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-01 10:30:00 | Fail | Tested meat slicer, no fault found
MSA-DCS | WA3361647 | Kitchen - up right freezer, failed test and tag, electrical fault | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-01 11:00:00 | Fail | Tested freezer, no fault found
MSA-DCS | WA3361648 | Unit 2, C10 - officer lock is sticking | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 13:06:06 | 2020-06-11 10:30:00 | Pass | Repair/adjust cell lock on Cell C10 Unit 2
MSA-DCS | WA3361649 | Entry Pod - on duress system - 5.1 low battery | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 13:07:26 | 2020-06-11 09:51:00 | Pass | Removed cabling from transponder to battery found corroded in cavity, replaced and tested good. System restored
MSA-DCS | WA3361674 | Gate Control - mutiple camera down. | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 13:22:44 | 2020-06-11 20:12:00 | Fail | Sourced mean well 24vdc PSU, Removed ant infestation and installed new power supply Checked cameras and confirmed operational
MSA-DCS | WA3361680 | MPC, Cell 1 - cell call system is faulty | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 13:30:00 | Pass | MPC cell 1 failing to communicate correctly, replaced cell call point for new, tested cell call fully operational, internal connection replaced from old to new type.
MSA-DCS | WA3361712 | Visits POD CCTV workstation to be brought online | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-19 16:25:00 | Fail | Visits workstation not working. Sourced parts required to reinstate workstation after sodexo disassembled. Reinstalled parts and operating system, configured and tested OK.Security requested additional displays for social visits monitoring. Investigated hardware requirements and system compatibility.Require Desktop/Tower i7, 16-32GB RAM, Nvidia Performance Graphics Adaptor, 3 displays, Wired keyboard and mouse (not wireless).
MSA-DCS | WA3361734 | INF (10) - Freezer in the kitchen is leaking water from the freezer into the light of the fridge | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-10 15:30:00 | Pass | Site to replace with spare on site
MSA-DCS | WA3361742 | INF (10) - Light switch in the infirmary kitchen near the fridges has been pushed in | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 08:30:00 | Pass | Repaired damaged light switch in infirmary kitchen
MSA-DCS | WA3361767 | Stores, Yard- Entry & Exit Gate Lock Striker Plates Broken | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-17 12:30:00 | Pass | Supplied and installed strike
MSA-DCS | WA3361785 | Replace boiler house faulty compressor | Hakea Prison | WSM-BR-SITE | Mechanical Services | Boilers (MS) | CLEVELAND COMPRESSED AIR SERVICES | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-07-07 12:30:00 | Fail | Installed new compressor
MSA-DCS | WA3361820 | Kitchen- Wash down hose has split & unable to use | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 09:30:00 | Pass | Kitchen Washdown hose split, unable to use. Check hose, remove for repair. Make up new hose as requested. Return & install.
MSA-DCS | WA3361835 | CCU- all cameras not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jun 2020 | 2020-06-10 19:16:24 | 2020-07-01 15:28:00 | Fail | Investigated CCTV fault. Traced to workstation overheating.CPU fan requires replacement. Sourced temporary spare and installed as temporary measure until correct fan unit arrives.Tested OKWill return with parts.Attended site, installed replacement CPU fan and tested ok
MSA-DCS | WA3361847 | Unit 4, B Wing- Fluorescent Light Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 11:30:00 | Pass | Repaired light
MSA-DCS | WA3361850 | west admin dinning room Fluorescent Light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 15:00:00 | Pass | Replaced lights
MSA-DCS | WA3361851 | kitchen Brat Pan Not Switching Off. Possibly Thermostat Faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 12:45:00 | Pass | Filled bratt pan with water and heated to max temp and tested ok. Cooled down with more water and repeated process a couple of times. Bratt pan has tested ok. Has not switched off and heats to max temp.
MSA-DCS | WA3361857 | gate house inferred beem at rear of gate house constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-23 08:00:00 | Fail | Located and repaired cabling issues. All 3 beam sets tested back to the gatehouse ok.
MSA-DCS | WA3361867 | Pump house - booster fault. | Hakea Prison-Sewer pump house, generator, transformers | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 10 Jun 2020 | 2020-06-10 21:22:26 | 2020-06-18 08:33:00 | Fail | nil
MSA-DCS | WA3365159 | Unit 13, B & D Wing- Constantly alarming | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 10 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-17 14:52:00 | Fail | Unit 13 BD cell 15/16 VESDA scan fault due to to many scans during a set period due to high smoke levels.Adjusted & increased smoke thresholds limits between alert/Action & Fire.Checked all other Vesda units for faults - no faults at time of attendance
MSA-DFES | WA3361420 | Staff entry and Exit door - Latch to door not engaging- latching correctly. | DFES Education and Heritage Centre | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 15:30:00 | Pass | Fit new handle to entry/exit staff door, lubricated lock and hinges - Door now engaging and latching correctly
MSA-DFES | WA3361442 | Ground floor, appliance room - Arcing of the drop lights in the appliance room | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 14:00:00 | Pass | Collected EWP from East Perth at 1215.Arrived onsite at 1245 and located with heather the reported fault. I tested for 240v at the fitting and that was all good. I then tested from a known earth terminal, to the frame, the suspension wire and the tin ceiling and I received 0 volts. I also did an a Fault loop and a Insulation resistance and they passed. Also tested the RCD for function.
MSA-DFES | WA3361468 | Driveway fence area - the fencing on the Southern edge of the drive has had all the sand wash away | VFRS Kwinana | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 10:30:00 | Pass | BRAF prepared and submitted - DECLINED by client - progress to LVM
MSA-DFES | WA3361549 | SO ensuite tap at front of station cannot be turned off may need new washer | CFRS Claremont | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 14:15:00 | Pass | Investigate leaking tap, isolate main water supply, dismantle garden tap and replace tap washer,print and body washerRe lube spindle and reseat tap seat Re assemble spindle and turn water mains back on flush out brass shaving and check for leaks Pack up and clean up worksite 1xtap washer 1xbpdy washer 1xoring Tap lubricant
MSA-DFES | WA3361557 | ground work shop drain clogged in sth west corner -needs cleaned and checked | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 11:32:00 | Pass | 50mm sink waste run into storm water gully pit is solid unable to lift lid due to new tarmac being laid
MSA-DFES | WA3361558 | Station officers ensuite- Toilet cistern operates intermittently | CFRS Claremont | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 14:44:00 | Pass | Investigate faulty cistern located ensuite bathroom Isolate water mains at mini stop,remove old inlet valve and outlet washer Supply and install a new inlet valve and outlet washer, turn water mains back on and set water levelTest cistern operationPack up and clean up worksite 1xinlet valve 1xoutlet washer
MSA-DFES | WA3361565 | Numerous in CL&D area- doors jamming, see below further info | DFES Regional Office - Belmont | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-12 08:00:00 | Pass | Door x 3 make good from stickingDoor lock x 2 remove trim as required and adjust striker plate
MSA-DFES | WA3361596 | Ground -- communication pit lid is rusted | DFES Regional Office - Belmont | GMP-BR | Building | External Walls (BU) | AWB Co. | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-09-03 13:45:00 | Fail | Removed old put kid and installed 2 x new pits, sealed in pits and cemented flush with surround. All safe now job completed.
MSA-DFES | WA3361691 | Engine bay doors #4 – the doors will not come down, door will go up but wont come down | CFRS Perth | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 12:30:00 | Pass | Technician attended the site of Perth Fire Station Engine bay bi-fold doors #4 on 10/06/2020. Following full test and inspection of door components identified fault was the switch mode. Needed to return to replace power supply. Returned on site on 11/06/2020 and replaced switch mode. All tests ok.Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3361795 | rear door zone 22 faulty | VFRS Mandurah | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-12 08:45:00 | Pass | 12/06/2020, 830-845Zone 22 ok it was zone 23 that is constantly unsealed. Reed switch corroded so replaced all ok
MSA-DFES | WA3361831 | lower dam pump replace damaged mechanical protection to power supply | FESA RHQ - Forrestfield | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-11 11:45:00 | Pass | Complete
MSA-DTAG | WA3361137 | Lvl 6, Secure Area, Prisoners Review Board- Flickering light | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 11:15:00 | Pass | Job complete
MSA-DTAG | WA3361183 | 1987 sheriff's office-Communications door lock is jamming – outside entrance to new Sheriff’s Office | Supreme Court | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 23:15:00 | Fail | Attended site to view bi-lock cylinder - requires replacement.Date on site: 10/06/2020Time on site: 01:00pm - 01:15pm Returned to site to supply and install new 570 bilock barrel and service mortice lock.Date on site: 15/06/2020Time on site: 11:45am - 12:15pm
MSA-DTAG | WA3361195 | Level 1, staff room - hot water unit is not regulating | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 14:10:00 | Pass | A40202101% Rheem Bwu L1 Crib Room not heatingstaff advised it had been turned off... tested refilledworking ok may have not had time to heat up.
MSA-DTAG | WA3361202 | Level 15, Plant room - Check operations of boilers after power outage Saturday 13/6/20 | Central Law Courts | GMP-BR-HO | Mechanical Services | Boilers (MS) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 09:00:00 | Pass | Check bms and L15 boilers
MSA-DTAG | WA3361207 | All Levels, Swithcboards - Check all electrical circuits after power outage Saturday 13/6/20 | Central Law Courts | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 08:30:00 | Pass | Job complete
MSA-DTAG | WA3361210 | lift rooms Check lift operations after power outage Saturday 13/6/20 -see notes | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 15:00:00 | Pass | Technical comment: Checked over lifts at clc after gen testing from weekend, found 6 out of 8 lifts not responding. Set controllers andlifts went back into service, tested each lift.
MSA-DTAG | WA3361259 | The carpet in the Information Centre is badly worn and poses a trip hazard | Joondalup Courthouse | GMP-BR-HO | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-12 13:11:00 | Pass | BRAF submitted, approved and works carried out.
MSA-DTAG | WA3361283 | L1 near magistrates lift water leak from ceiling possibly from air con | Rockingham Justice Complex | GMP-BR-HO | Building | Ceiling (BU) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-12 09:14:00 | Fail | Fixed leak on chilled water pipe
MSA-DTAG | WA3361702 | Level 1 - the men’s bathroom - toilet clogged | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 09:27:00 | Pass | unblocked toilet
MSA-DTAG | WA3361798 | Fire Panel needs to be isolated as HVAC need to do welding to repair major water leakage in ceiling | Rockingham Justice Complex | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 17:00:00 | Pass | Conduct Fire panel isolation on zone 8&9 due to HVAC works being conducted in roof space. Travel back to site and de isolate fire panel zones 8&9. Check panel is reset and contact security that panel is back to normal operating
MSA-DTAG | WA3361825 | Court 6, Judicial Corridor, Secretary coffee table - 3x lights not working | Perth Children's Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 09:15:00 | Pass | Job complete
MSA-DTAG | WA3361856 | L9 court 92 Too hot in court 92. Querying if air-con is on | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 15:00:00 | Pass | Return to site. Access BMS and check temps in court 92. Found room temp to be 22.5. Found temps accross lev 9 to have improved from yesterday. Access court 92 and check temps, found to be 22.5. Sensor is reading correctly. Check vav boxes accross lev 9 and found VAV 9.06 to still have a temp reading of 23.6, box is reading 0 airflow. Further investigation found this box is waiting approval for further testing. Count 92 AC now working as normal.
MSA-DTWD | WA3361096 | Male toilets, opposite A236 – urinal blocked | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Jun 2020 | 2020-06-11 17:00:00 | 2020-06-11 12:00:00 | Pass | Complete
MSA-DTWD | WA3361103 | F Block, FG11- Plumbing pipes leaking at drinking fountain | Carlisle Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-17 12:00:00 | Fail | Replaced pressure relief valve and adjusted flow
MSA-DTWD | WA3361107 | R Block , R001 & R007 - Faulty door locks | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 13:45:00 | Pass | Serviced tools
MSA-DTWD | WA3361121 | E Block, E008 & E009- External lighting is not working | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-25 15:30:00 | Fail | Replaced faulty lamps to E block security lights E007-E009, all working. Job complete.
MSA-DTWD | WA3361126 | Q Block, Q009- roof leaking onto overhead projector | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-16 12:30:00 | Fail | 1st attendance - Q009 leaking from sky lights - Due to age will need to replace 4x 2.4m long span Picked up materials/removed skylights once vent was disassembled - fitted new skylights and re-installed vents. Sealed all joints and replaced fixings
MSA-DTWD | WA3361203 | Block 3, 1st Floor - 3CF3 and 3CF29 (Fitting and Machining), A/C’s on but not working | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 14:00:00 | Pass | AC units reset due to power loss causing communication error
MSA-DTWD | WA3361304 | Level 2, A 207 - door lock sticking, This is an electric lock. | Leederville Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 14:42:00 | Pass | replace handle and service lock on door to room A207
MSA-DTWD | WA3361329 | Block 1 Security panel showing low battery signal | Thornlie Campus | GMP-BR | Security | Monitoring (SE) | CONNECT SECURITY SYSTEMS | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 12:00:00 | Pass | Changed 8 x batteries
MSA-DTWD | WA3361330 | A Block, A307 Corridor- 3x light fittings are not working | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 14:45:00 | Pass | Replaced faulty lamp holders , tubes , starters to light in corridor . Job completed
MSA-DTWD | WA3361339 | Block 3 Water damaged LED panel outside Fitting and Machining | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-17 15:30:00 | Pass | Locate faulty light fittings. Isolate power. Replace old faulty fluro fittings with new square led panel’s. Renergise circuit. All ok.
MSA-DTWD | WA3361342 | BLD 875, Pens- Faulty tap and copper pipe leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-17 14:00:00 | Fail | job completed - Repair leaking copper water pipe and replace 6 full flow ball valves
MSA-DTWD | WA3361371 | A block auto door keeps opening by itself | Munster Campus (ACEPT) | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-10 12:51:00 | Pass | Checked and found a big spider in the external sensor, cleaned both external and internal sensors. Adjusted range to both , checked safety’s, batteries etc all ok.
MSA-DTWD | WA3361372 | A block staff area sensor light staying on | Munster Campus (ACEPT) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-23 14:00:00 | Fail | Attended site and signed in. Installed switch in office in place of sensor. Replaced 2x 360 sensors in office. Tested all okay. Job complete
MSA-DTWD | WA3361514 | H block, HG06 - Cant plug anything into the power points, something seems to be blocking it | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 11:45:00 | Pass | Attended site and signed in. Located h6 and tested power. No fault were found with power points but located bent plug. Straightened plug and tested. Showed lecture. Happy to close off job.
MSA-DTWD | WA3361610 | T block G/I passages L1-replace all blown passage way and wall light bulbs ( Fluro's) | Joondalup McLarty Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 15:30:00 | Pass | Replaced all faulty components to passage way lights
MSA-DTWD | WA3361636 | E block, Restaurant Kitchen - broken faucet to potato peeler, please replace with metal not plastic | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 07:54:00 | Pass | Water filter cartridge leaking in executive kitchen
MSA-DTWD | WA3361658 | U001 - faulty lock, | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-10 14:15:00 | Pass | Service to lock
MSA-DTWD | WA3361670 | D-Block 1st Floor library leak from pipe in ceiling space near kitchen area | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-11 13:00:00 | Pass | Water leaking through slab, from filter cartridge on the union between the filter cartridges,Kitchen cupboard is damaged water logged needs to be repaired
MSA-DTWD | WA3361685 | D Block, ladies staff toilet is leaking | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-16 11:30:00 | Fail | Replaced leaking seals underneath toielt
MSA-DTWD | WA3361782 | S block, Level 2, S209 - Replace lights not working in Library | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 10 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 08:43:00 | Pass | Repalced faulty fluro and control gear to light in library.job completed
MSA-DTWD | WA3361844 | E block ground restaurant Air con is not working – A/C 4 calling for cooling – BMS Issue-see notes | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Building Automation & Electrical Services Pty Ltd | 2 | COMPFIN | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 00:00:00 | Pass | Works completed. Work order to be closed out at $0 cost
MSA-DTWD | WA3361848 | R Block, R021 - Air Con wont turn off | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 10 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-01 15:00:00 | Fail | Unit accessed. Pressure test successfully. New oil put into compressor to correct level. Unit evacuated and charged 427a. Found thermostat , high and low pressure switches out of settings. Rectified and tested. Superheat adjusted to suit. Compressor mounting to unit frame modified to suit with new fittings. Unit test run to set temps and adjusted to physically suit. Fans ok contactors and relays ok. Adjusted overloads to suit. Mech ok
MSA-DCA | WA3365469 | Lower level, Kitchen Lift - doors of kitchen lift are not opening/closing properly | Art Gallery of WA - James St-Main Building (Block B)-Level 2-Kitchen | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-11 14:53:00 | Pass | Lift 1 Art-Geared :Found rope brake tripped , checked oil levels, cleaned and tightened sensor roller, reset brake unit tested and left lift running
MSA-DCA | WA3365806 | Aircon - Chilled water system - fault - high temp. | Art Gallery of WA - James St-Main Building (Block B)-Level 5 - Roof-Rooftop Plant - External Area | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 11 Jun 2020 | 2020-06-11 21:46:59 | 2020-06-18 21:30:00 | Fail | Onsite at 6:30pm (WA) Job completed at 9:20pm (WA)
MSA-DCS | WA3364803 | Mechanical w/s paint booth light switch faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 08:30:00 | Pass | Investigate and repair mechanical workshop spray booth light switch.
MSA-DCS | WA3364806 | Perimeter light not working x4 | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 15:00:00 | Pass | Investigate and repair perimeter lights
MSA-DCS | WA3364807 | Rear security flood light to Mechanical W/S not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 11:30:00 | Pass | Investigate and repair flood light at rear of mechanical workshop
MSA-DCS | WA3364836 | Unit 2, B wing dayroom door - viewing window smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 07:37:18 | 2020-06-11 17:15:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3364849 | Unit 2, B wing dayroom door - 2x windows smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 07:47:38 | 2020-06-11 15:30:00 | Pass | RE GLAZED WINDOWS
MSA-DCS | WA3364890 | Security Area, Control Room - download footage for security/cell calls | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 08:05:20 | 2020-06-11 15:30:00 | Pass | Report to security manager, obtain details of recordings required (Cell call audio from 6B3 09/06-11/06). Located audio required and downloaded to supplied memory stick. Delivered to Security manager.
MSA-DCS | WA3364912 | MPU (8), M4 - faulty light at bed head of Cell M4 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 10:00:00 | Pass | Investigate and repair faulty light in MPU M4
MSA-DCS | WA3364917 | Unit 5, A wing, cell A06 - prisoner key is no longer working after lock was repaired | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-11 09:45:00 | Pass | repairs to faulty key
MSA-DCS | WA3364933 | Unit 4, Cell C4- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 13:00:00 | Fail | Plunged basin to clear blockage. Adjusted water pressure.
MSA-DCS | WA3364948 | Unit 1, C wing, C12 - window broken | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 15:30:00 | Pass | REPLACE/REPAIR AND RE GLAZED CELL WINDOW
MSA-DCS | WA3364956 | Unit 3, Cell A4- Sink is leaking creating a smell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-22 11:00:00 | Fail | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3364991 | Unit 7, G Wing Corridor lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-11 14:00:00 | Pass | Replaced fuse
MSA-DCS | WA3365021 | Kitchen - small freezer not working correclty & turned off (according to kitchen supervisor) | Banksia Hill Detention Centre | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-07-20 15:23:00 | Fail | BRA declined. Invoicing CTD.
MSA-DCS | WA3365034 | Unit 3, Hot water urn tap is broken & no water coming out | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-11 10:20:00 | Pass | Replaced broken top with commercial tap fixture
MSA-DCS | WA3365132 | Unit 3 - D Wing drain in cleaning cupboard not working. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-22 12:00:00 | Fail | Used acid and plunger to clear blockage in fwg under cleaners sink.
MSA-DCS | WA3365150 | Outcare- Visitors Kitchen- Light blown | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-12 15:00:00 | Pass | Investigate and repair faulty lights in outcare kitchen
MSA-DCS | WA3365166 | gate house key issue - Air-con/heating not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-12 18:36:00 | Pass | System is running.
MSA-DCS | WA3365170 | Control - cardax generated cctv alarm sequences | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 10:09:15 | 2020-08-19 19:46:00 | Fail | Reprogrammed Gallagher and Indigo HLI, Modified Indigo users and alarm monitorsControl 3 monitor 1 and 2 display external alarms and tampers.Control 1 monitor 2 displays internal alarms
MSA-DCS | WA3365340 | Cleaning Workshop Store Room Drain blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 11:37:12 | 2020-06-11 15:30:00 | Pass | Drain machine used to unblock drain 10meters drain rod used
MSA-DCS | WA3365343 | Camera system in MPU not working | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 19:30:00 | Pass | Checked workstation network settings, all appears ok.No conenction to network switch.Traced cable under desk and found damaged cable. Removed damaged section and terminated into RJ45 connector. Ran new 5m Cat5e patch lead into workstation.Workstation reconnected to network, checked indigo system all functional
MSA-DCS | WA3365348 | Murchison, office, toilet wash room - light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-17 13:00:00 | Fail | Replaced light fitting
MSA-DCS | WA3365364 | Unit 4, A/C dayroom - inside door handle of wing door is loose | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-16 14:45:00 | Pass | NEW DOOR HANDLE INSTALLED
MSA-DCS | WA3365368 | Unit 13, cell B2 - personal lock barrel not working properly | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-22 10:30:00 | Fail | replaced mortise lock and barrel.
MSA-DCS | WA3365370 | Unit 2, D12 - window wont stay open | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-07-02 12:00:00 | Fail | SPIRAL BALANCES & FEET REPLACED
MSA-DCS | WA3365374 | Unit 6, Cell B13- Personal door latch not working correctly, further info below | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-17 12:00:00 | Fail | Replaced hinges, door plate, lock and weld on strike plate
MSA-DCS | WA3365381 | U6 D11 leaking toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 10:58:00 | Pass | Replaced outlet washer
MSA-DCS | WA3365402 | Unit 2, D wing shower - window wont stay open | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-07-02 10:45:00 | Fail | NEW SPIRAL BALANCES & FEET FITTED
MSA-DCS | WA3365403 | North lobby door is not closing | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 11 Jun 2020 | 2020-06-11 15:58:19 | 2020-06-11 13:00:00 | Pass | Not electrical job
MSA-DCS | WA3365406 | Unit 6, A15 - toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 11:48:00 | Pass | Replaced outlet washer
MSA-DCS | WA3365407 | upstairs kitchen, rain coming through top of shut window | Midland (North East Metro) | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-09-24 11:47:00 | Fail | no charges - closed off compfin.
MSA-DCS | WA3365410 | Unit 6, A wing showers - sink spout requires resecuring to basin | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-12 12:25:00 | Pass | Removed basin surround tighten outlet reinstalled surround
MSA-DCS | WA3365414 | Unit 2, Door to cell C4 has dropped & damaging floor of C wing , door scrapes on he floor | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-18 09:45:00 | Fail | Replaced barrel and retaining screws.
MSA-DCS | WA3365416 | MPU (8) - PA system cant be used due to bad feedback over the speakers | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 12:11:07 | 2020-06-26 14:00:00 | Fail | Replaced failed EWIS cabinet mounted Amp with Rack mount Amp installed in Rack 9 in Gate House Equipment room. Installed new Rack mount power distribution board, no spare outlets available.
MSA-DCS | WA3365425 | Unit 3, office- Fluro lights are missing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-23 13:30:00 | Fail | Checked damaged lights in unit 3. Sourced suitable replacements. Picked up and installed and tested
MSA-DCS | WA3365429 | water leak in the men’s toilet ceiling level 4 near light fitting | East Perth-Main Building-Level 4 | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-23 13:30:00 | Fail | Attended site and carried out inspection. Waited for dry weather to seal roof leaks
MSA-DCS | WA3365434 | 1.Repair door lock on rear entry door-lock has loosened. 2.Repair door lock on stationery room | Nyandi Training Academy | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-12 14:15:00 | Pass | Attended site, bore out strike for storage room. Re-tightened and supplied new screws for 002 rear entry door.Date on site: 12/06/2020Time on site: 01:45pm - 02:15pm
MSA-DCS | WA3365441 | Unit 6, Cell A6- Toilet is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 12:40:00 | Pass | Replaced inlet valve
MSA-DCS | WA3365443 | main ground-Repair PA system - evacuation alert is ON when making announcement via PA system. | Nyandi Training Academy | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 12:23:35 | 2020-06-12 12:09:00 | Pass | Attended site for alert tone activating when using microphone. After further investigation found relay stuck on red back system reset and all back to normal working condition when left. Tested and all fine
MSA-DCS | WA3365477 | gate house nth lobby door in air lock not closing | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Jun 2020 | 2020-06-11 16:50:01 | 2020-06-11 17:45:00 | Fail | Picked up custodial lock after being informed requires replacement / damaged. Found existing lock operational but not aligned, door under repair by ability locksmiths ( new barrel / housing being cut into frame, adjusted lock operating And closing but pressure required.
MSA-DCS | WA3365535 | Unoit 1, end of A&B wing & Kitchen - lights not working x7 | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 10:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3365539 | Unit 1, Staff toilets- Light has broken ballast | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 09:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3365550 | Hakea perimter - Infer red beam 12 internal is in constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 13:34:11 | 2020-06-12 15:22:00 | Fail | Investigated infrared beam set intermittently alarming, checked all connections, cleaned lenses, checked power supply, monitored for correct operation. Noticed some branches / foliage interrupt beam when wind gusts. Advised site to request gardener to prune.Job Complete
MSA-DCS | WA3365568 | Boardroom- roof leak water coming through light | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 13:44:53 | 2020-06-12 09:12:00 | Pass | ROOF LEAK COMING THROUGH LIGHT REPAIRED
MSA-DCS | WA3365781 | external perimeter zone A03 not activating after check | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 16:30:02 | 2020-06-12 08:30:00 | Pass | 12/96/2020 06:45. Attended outer perimeter and visually inspected fence zone. Confirmed with test meter voltage on each of the two circuits (6.0-6.8kv). Contacted Gate Control. Tested fence alarms A->Eth, B->Eth, A->B. All alarms received in control.
MSA-DCS | WA3365788 | gate house senstar node side B supervision constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-17 15:15:00 | Fail | Located and repaired Comms issue around EC4. Tested ok.
MSA-DCS | WA3365833 | Wooroloo Prison Farm - Duress alarm going off - Transponder 06, AC loss for Unit 4A | Wooroloo Prison Farm-Prisoner Accommodation Unit 4a Block 1 | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Jun 2020 | 2020-06-12 02:29:03 | 2020-06-12 16:15:00 | Fail | Attended site to replace faulty power supply. Tested ALL OK.
MSA-DFES | WA3365141 | Stairwell- water coming through light fitting | CFRS Perth | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-11 12:30:00 | Pass | Complete
MSA-DFES | WA3365503 | engine room, door 1 is intermittent, will open but when closes comes half way | CFRS Midland | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 17:00:00 | 2020-07-22 16:00:00 | Fail | Technician attended the site of Midland Fire Station to the Door 1 no. W20748 on 11/06/2020. Following a full test and inspection of door components found fault to be PE Beam. Technician has bypassed for the meanwhile so that door operates, and don't believe this will be a safety issue as there are 3 other sets of PE Beams on door. Quote was submitted. Technician returned on site on 12/10/2020 to replace faulty PE Beams to engine room door 1.Tested operation. Door is now working as should. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3365571 | both Tunric rooms - roof leak | CFRS Osborne Park | GMP-BR | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 17:00:00 | 2020-07-09 15:30:00 | Fail | Supply and install new dry pan flashings around motorised vent unitSupply all accessories required for installationRemove all waste from site on completion of work
MSA-DFES | WA3365608 | Stairwell- water coming through light fitting | CFRS Perth | GMP-BR | Roofing | Rooflights and Skylights (RF) | AWB Co. | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-12 08:05:00 | Pass | investigated leak above stairs and found split dektite on an anchor point. cleaned back and sealed
MSA-DFES | WA3365747 | SIMCEN Bunker AIRCON fails to turn on | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-22 11:30:00 | Fail | Sump heaters replaced.
MSA-DFES | WA3365766 | Office various parts water leaks coming from ceiling-see notes | Armadale Regional Office | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-07-25 09:00:00 | Fail | Attended to roof leaks as requested and repaired Anticon below roof leaks . Have advised site that Anticon under the tiles is in poor condition generally
MSA-DTAG | WA3364978 | There is a leak coming from the roof in the Public Female toilets on the ground floor. | Joondalup Courthouse | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-26 13:33:00 | Fail | SOURCE OF LEAK LOCATED & REPAIRED
MSA-DTAG | WA3365015 | Custody - Plaster is peeling from the walls in Cell 1 | Joondalup Courthouse | GMP-BR-HO | Painting | Internal (PA) | PPM Project Painting & Maintenance | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 18:00:00 | Pass | patch and paint
MSA-DTAG | WA3365164 | Internal offices, rear waiting room- Roof leaking- damp tiles and dripping water in MYBS office | Perth Children's Court | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 17:00:00 | 2020-07-27 10:04:00 | Fail | MULTIPLE LEAKS REPAIRED
MSA-DTAG | WA3365420 | 1903 ground near lift 3 and court 2 roof leak | Supreme Court | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-10-05 13:28:00 | Fail | SOURCE OF LEAKING LOCATED & REPAIRED - MULTIPLE VISITS
MSA-DTAG | WA3365566 | ground Judge’s bathroom & Judicial Kitchen no hot water | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 17:00:00 | 2020-06-11 16:55:00 | Pass | No hot water in the electric hot water system. Issue not plumbing related. Unable to contact Iain
MSA-DTAG | WA3365773 | registry ground admin to barrier spray for spiders Told that white tail and red backs on premise | Mandurah Courthouse | GMP-BR-HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 16:55:00 | Fail | Waited for close of court activity. Sprayed inside airlock doors at entry to court reception area & externally to entrance & surrounds
MSA-DTWD | WA3364796 | A block, level 2, A127 - Replace broken door closer to A217 link door | East Perth Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 11 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 13:00:00 | Pass | Arrived at site, inspected closer. Required new closer, picked up materials and returned to site. Measured marked and fixed closer. Adjusted settings. Drilled out striker plate. Fixed squeaking hinges. Tidy area, packed away tools.
MSA-DTWD | WA3364862 | C block, Level 2, C207 - window seal leaking. replacement seals required | Joondalup Kendrew Campus | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 11 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 13:57:00 | Pass | ATTENDED SITE, SEALED UP WINDOWS TO A BLOCK - 2ND LEVEL ROOM 207 AS INSTRUCTED BY BARRY 2X TUBES OF SILICONE USED
MSA-DTWD | WA3364964 | Canteen - Fagor upright freezer not maintaining temperature | Rockingham Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 11 Jun 2020 | 2020-06-12 17:00:00 | 2020-07-06 14:00:00 | Fail | Travelled to site signed in. Located upright freezer. Found that fridge was at +20 degrees.client had moved food into another on-site freezer. Tested freezer and found compressor very hot and not running. Check amp draws and found compressor was seized. Unit will require a new compressor. Braf created for repairs.
MSA-DTWD | WA3365002 | B Block, B111- Gas plug in fitting welding bays faulty | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-11 13:45:00 | Pass | Complete
MSA-DTWD | WA3365012 | a block, Level 3, A412 - Replace blown lamps. High ceiling, a tall ladder is required | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-22 09:45:00 | Fail | Attended site and re tubed classroom A412.
MSA-DTWD | WA3365029 | D block L1 D106 Noisy Compressor on sample fridge | East Perth Campus | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 10:30:00 | Pass | Unit accessed and checked against manufacturer specs. Fan operating as designed re blade noise upon start up. Unit temperatures checked and ok.Unit cycling to set temps
MSA-DTWD | WA3365122 | K block, ground level, K02(kitchen) & K08(staff toilets) - Leaking taps | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-16 15:00:00 | Pass | Serviced leaking taps
MSA-DTWD | WA3365156 | Building 7, Cafeteria - leaking drain pipe to wash up area of kitchen | Thornlie Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-11 14:00:00 | Pass | Modify new teap
MSA-DTWD | WA3365194 | U022.1 - 3x roof leaks and 1x in U022 | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 14:00:00 | Pass | U block - multiple leaks to vent systems, exhaust flues, evap units and penetrations. cleaned and sealed.
MSA-DTWD | WA3365206 | Q block Q014 roof leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 12:00:00 | Pass | Sealed around a vent system if problem persists may need to replace skylights
MSA-DTWD | WA3365346 | A block L2 A277 AirCon not working. | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-07-01 08:30:00 | Fail | Picked up required part,attended site with eletrician,located site manager to access switchboard,isolated switch board and replaced faulty circuit breaker with new.tested airconditoner system and left operational.
MSA-DTWD | WA3365404 | E Block, ET06 Classroon- Leak from roof into classroom | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-07-09 11:00:00 | Fail | Gutters cleaned and Guard installed. Site confirmed leak resolved.
MSA-DTWD | WA3365409 | E Block, ET03 Classroon- Leak from roof into classroom | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-07-09 11:30:00 | Fail | Cleaned gutter and installed gutter guard. Site confirmed no further leaks reported
MSA-DTWD | WA3365411 | E block ET14 female toilet Plumbing pipes leaking at 3rd basin tap | Carlisle Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 13:11:00 | Pass | Replaced leaking taps
MSA-DTWD | WA3365412 | Lvl 3 - L2 walkway & room A269- Roof leaks | Perth Campus B5 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 09:30:00 | Pass | Blocked rainhead and box gutter - cleared both. please note blockages were caused by bird waste
MSA-DTWD | WA3365430 | F Block, FG23 Workshop- Roof leak near gas detection alarm panel | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-16 15:45:00 | Pass | Carried out repairs to roof, sealed with roof and gutter sealer
MSA-DTWD | WA3365435 | F Block, FG11-1 Mezzanine Workshop- Roof leak near around AC penetration just in front of stairs | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-08-26 13:15:00 | Fail | Removed old silicone around A/C penetration and applied new silicone to reseal. Frank Femia confirmed leak seems to be fixed. Job complete
MSA-DTWD | WA3365436 | F Block, FG31 Workshop- Roof leak above welding bays | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-08-10 14:00:00 | Fail | Applied roof and gutter sealer to areas suspected to be causing the leak
MSA-DTWD | WA3365444 | E Block, E25 Store Room – Roof Leak | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-12 13:09:00 | Pass | Located roof leak and carried out repairs
MSA-DTWD | WA3365446 | A Block, Walkway, outside AG26 female toilets- Roof leak down wall | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-07-03 14:15:00 | Fail | Installed new flashing to replace old corroded flashings
MSA-DTWD | WA3365451 | B Block, B2436- Water leaking through ceiling | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-08-10 08:15:00 | Fail | Site requested we create a temp access hole in the ceiling that will allow assessment from below during rain in an effort to identify the source of the leak. 3/8/20 Water appears to be coming through masonry wall- Site asked us to close off the work order
MSA-DTWD | WA3365454 | A Block, A30 - Water leaking through ceiling | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-22 14:30:00 | Fail | Sealed roof leak - no additional works required to ceiling
MSA-DTWD | WA3365517 | F Block, FT15 AC Plant Room- Leaks through AC penetrations | Carlisle Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-10-12 11:15:00 | Fail | Have sealed a number of areas on the roof. No further leaks reported. Frank requested to close the work order off - will review when we have more rain and issue a new work order if more leaks present
MSA-DTWD | WA3365533 | West Block, W101 - Blocked toilet | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-11 15:15:00 | Pass | Complete
MSA-DTWD | WA3365619 | A Block, Room A48 (staff office 3)- Multiple lights not working | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-16 16:16:00 | Pass | Attended site and signed in. Located a48 and all lights out. Used client supplied starters and lamps and replaced all lights out. Replaced other parts with site supplied. Tested all okay. Job complete
MSA-DTWD | WA3365626 | B block, Level 2, B20 - (Urinal near conference room) buttons stuck | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 16:15:00 | Pass | Complete
MSA-DTWD | WA3365756 | R block R021 roof leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 15:00:00 | Pass | leaking out of window frame and onto window sill sealed cladding panels directly above and apron flashing
MSA-DTWD | WA3365778 | B block L4 B2428 Water leaking through ceiling | Bentley Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-12 14:00:00 | Pass | Sealed leak with roofing sealer
MSA-DTWD | WA3365783 | D block Blocked down pipes coursing roof leaks. | Bentley Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-26 08:00:00 | Fail | Attended site - safety anchor points were found to be out of date and we were not able to access the roof. Will need to return once anchor points have been tested. Site advised anchor points had been retested . We attended and completed the works
MSA-MRWA | WA3365709 | L1 Asphalt lab Safety shower / eye wash station activation alarm not working-see notes | Materials Engineering Branch | GMP-BR | Security | Monitoring (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 11 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 14:45:00 | Pass | 18/6/20 - Dylan Parslow, Ryan VestyInvestigated issues with shower alarm.Found build up of lime scale blocking flow switch.Cleaned out and tested.All working.
MSA-DCA | WA3371404 | Kitchen Lift - people stuck in lift | Art Gallery of WA - James St | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 12 Jun 2020 | 2020-06-12 18:13:29 | 2020-06-12 15:15:00 | Pass | Lift 1 Art-Geared :Released swp, emergency power rope tripped, after discussing with swp, it trip at start up, reset and tested tripped again, after inform supervisors, left lift shut down
MSA-DCS | WA3370754 | Investigate and identify any used fire hose reels | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 15:30:00 | Fail | nil
MSA-DCS | WA3370786 | hallway / chaplains office - air con unit constantly trips | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 12 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-12 18:39:00 | Pass | Found cables damaged due to rodents repaired damaged section.If fault reoccurs Tech and apprentice will be required to crawl through out the roof space to find new damaged section.
MSA-DCS | WA3370799 | Unit 2, Security flood light not working facing the oval | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 13:00:00 | Pass | Investigate and repair Unit 2 Security flood light
MSA-DCS | WA3370805 | Video link - Light switches making crackling noise when operated | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 12 Jun 2020 | 2020-06-12 11:38:17 | 2020-06-12 09:30:00 | Pass | Replaced switch
MSA-DCS | WA3370815 | Store area internal - numerous fluros damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 11:30:00 | Pass | Replaced damaged lights
MSA-DCS | WA3370821 | Skills Workshop - 5x electrical GPOs damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 12:00:00 | Pass | Replaced 5 damaged gpos
MSA-DCS | WA3370859 | All cell lighting on the northern side of unit 12 wing has tripped out at RCD. RCD can not be reset | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 12 Jun 2020 | 2020-06-13 08:10:54 | 2020-06-12 13:30:00 | Pass | Investigated and repaired faulty lights in unit 12
MSA-DCS | WA3370863 | Unit 1, Cell B6- GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 12 Jun 2020 | 2020-06-13 08:18:24 | 2020-06-12 09:30:00 | Pass | Replaced gpo
MSA-DCS | WA3370869 | Zone 8, IPR office - alarm activated in alarm | Riverbank | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jun 2020 | 2020-06-13 08:20:40 | 2020-06-12 18:00:00 | Pass | Attend site reset alarm. Armed system and tested it working ok.
MSA-DCS | WA3370882 | Unit 3, A Wing- Cell A5 sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-22 10:00:00 | Fail | Plunged basin to clear blockage.
MSA-DCS | WA3370890 | Medical, Kitchen/passage - passage door is not opening with swipe needs key to open | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 11:30:00 | Pass | Tested multiple times electronic door medical area with different key fobs, working as normal. Job completed.
MSA-DCS | WA3370981 | Tele comm room- cell call system alarm activating constantly | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Jun 2020 | 2020-06-12 13:54:49 | 2020-06-12 15:00:00 | Fail | Buzzing sound coming from the CI-switch. No error messages on the Officer station or PC. Restarted CI switch (node 2) via site configuration program. No error messages in log. Intercoms tested ok.
MSA-DCS | WA3370983 | Unit 4, Faucet has broken off in the b wing cleaning closet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-18 15:00:00 | Fail | Located dismantled tap. Repaired and reinstalled tap and tested.
MSA-DCS | WA3370985 | Unit 14 - D Wing cell D6 faulty lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 12 Jun 2020 | 2020-06-13 10:01:14 | 2020-06-15 10:30:00 | Fail | replaced mortise lock and installed oversized strike
MSA-DCS | WA3371032 | Demountable room 7 Computer Room No 7 water leak-see notes | Nyandi Training Academy | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 12 Jun 2020 | 2020-06-13 10:16:12 | 2020-06-16 08:30:00 | Fail | SOURCE OF LEAK LOCATED & REPAIRED
MSA-DCS | WA3371062 | Unit 5, Control Room- Camera monitor intermittently going black | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-13 11:00:00 | Pass | Attended two seperate occasions as fault repeated. Loose cables were resecured and extender devices reset.
MSA-DCS | WA3371071 | unit 2D oven not working properly | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-12 13:30:00 | Pass | Unit 2D Oven Faulty. Check oven controls & wiring. Test oven, fan & switches. All working correctly. Auto timer had been operated incorrectly.
MSA-DCS | WA3371137 | Entry Building - keywatcher door lock fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | AAA Ability Locksmiths | 1 | CLOSE | 12 Jun 2020 | 2020-06-13 11:15:49 | 2020-06-15 14:30:00 | Fail | No fault found. Lock and Strike serviced to try and fix any intermittent fault that may have caused initial issues
MSA-DCS | WA3371148 | Paintshop- prisoners toilet blocked is over flowing with water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 16:00:00 | Pass | Plunged toilet to clear blockage.
MSA-DCS | WA3371149 | Unit 13 - B10-toilet and shower blocked and shower floods cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 17:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3371161 | Front gate, Master Control room - cell call panel microphone button not working | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Jun 2020 | 2020-06-12 15:42:27 | 2020-06-12 15:00:00 | Pass | Removed CI-3210 console, found connection on bottom of push to talk button loose. Soldered cabling after tightening clamp. (Comms boards required removal for access) checked multiple times fully operational.
MSA-DCS | WA3371163 | Unit 1, Staff lunch Room- Hyrdo Tap not working | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-15 08:58:00 | Pass | Reset hydro unit couldn’t get to work had password I don’t have contacted zip Australia to repair
MSA-DCS | WA3371170 | Unit 1, A-B Common areas- 1x Drink Fountains have Broken Taps | Melaleuca Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-15 09:48:00 | Pass | Ordered new tap
MSA-DCS | WA3371171 | Unit 1, C-D Common areas- 1x Drink Fountains have Broken Taps | Melaleuca Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 15:31:00 | Pass | Order new tap Installed new tap
MSA-DCS | WA3371177 | ground Reception & Office Area contractor to visit site with a view to providing quotation-see notes | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-23 15:30:00 | Fail | Replaced faulty lights
MSA-DCS | WA3371196 | reception and kitchen 1x fluro and bulb light out | Rockingham | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 09:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3371278 | recreation/gym roof leak through central of gym heavy onto mez | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-09-04 13:59:00 | Fail | MULTIPLE VISITS TO REPAIR LEAK AND INSTALL NEW FLASHINGS
MSA-DCS | WA3371283 | unit 2 cells C7 and C10 bed light flickering | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-01 14:30:00 | Fail | Replaced bed light fittings
MSA-DCS | WA3371286 | Unit 2 D13 night light flickering | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-01 15:00:00 | Fail | Replaced bed lamps
MSA-DCS | WA3371289 | unit 2 C11 toilet pan leaking at base | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-07-30 14:45:00 | Fail | COMPLETED
MSA-DCS | WA3371305 | Unit 7, F wing window Day room - broken window to repalce | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 12 Jun 2020 | 2020-06-13 13:10:55 | 2020-06-13 10:45:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3371362 | Monitor, control room - camera 28, not moving with joy stick or when alarmed | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Jun 2020 | 2020-06-12 17:46:47 | 2020-06-19 14:41:00 | Fail | Camera 28 monitored for 5 days with no further failures, no further action is required.
MSA-DCS | WA3371378 | Tap near Cyrenian tap broken-contractor on site | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-12 16:10:00 | Pass | Replace garden to cyriian building
MSA-DCS | WA3371407 | Training Room - both heaters report strong gas smell when operating | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Electrical Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 09:00:00 | Pass | Training Room, 2 x heaters have gas smell. Dismantle heaters, check for gas leaks. Remove & clean burners. Blocked with rust causing gas to blow out air intake. Assemble & test. Report to staff.
MSA-DCS | WA3371458 | entry building sally port door lock is sticking | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 12 Jun 2020 | 2020-06-13 15:14:39 | 2020-06-13 09:45:00 | Pass | Door to Sally Port - reported as sticking Removed lock from door and checked checked function with overide key - no fault foundreinstalled lock and checked - lock functioning correctly
MSA-DCS | WA3371531 | Wooroloo Prison Farm - Unit 2C - Lights in the verandah are flickering | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 12 Jun 2020 | 2020-06-12 21:42:20 | 2020-06-12 21:00:00 | Pass | Replaced faulty cable on spot light
MSA-DCS | WA3371546 | response gate , sog bar malfunctioning, gate opens and closes immediately, also dry pins doesn't eng | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-18 12:50:00 | Fail | Sourced parts attended site, investigated faults with gate, tested communication and control systems OK.Confirmed gate is now operating correctly.Job Complete
MSA-DFES | WA3371521 | front bi fold door cord keeps breaking beam | CFRS Midland | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 20:30:00 | Pass | Technician attended the site of Midland Fire Station, Front Bi fold W21347 on 15/06/2020. Following full test and inspection of door components identified fault door closing and opening. Technician has checked Bi fold found bump edge strip bungee cord getting block safety beams. Full test and inspection of door function completed prior to leaving site.
MSA-DTAG | WA3370853 | Ground- HWU element is faulty | Perth Children's Court | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-16 07:30:00 | Fail | Job complete
MSA-DTAG | WA3370884 | Specialist services - ceiling needs repairing due to water damage | Rockingham Justice Complex | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-08 10:15:00 | Fail | CEILING REPAIRED/ REPAINTED
MSA-DTAG | WA3370924 | Level 3, court 37 - Flickering light | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 09:00:00 | Pass | Job complete
MSA-DTAG | WA3370951 | Lift 3 Lift 3 is jumping and dropping dramatically-see notes | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 14:45:00 | Pass | When responding to the callback dated 12.06.2020, the Schindler Technician found a problem with your equipment. Some componentsof the car door operator were incorrectly aligned. Following our attendance, the equipment was left in service.
MSA-DTAG | WA3370971 | Lvl 5- toilet in the judicial passage near Court 52 is not flushing | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 11:30:00 | Pass | Complete
MSA-DTAG | WA3371048 | 1903 ground Assoc to Mazza JA Most if not all light tubes are out-see notes | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 08:00:00 | Pass | Replaced blown lamps and tested working
MSA-DTAG | WA3371222 | ground public disable toiket blocked not flushing | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-16 09:30:00 | Pass | Complete
MSA-DTAG | WA3371413 | registry ground admin Automatic Entry door not safe for pinch injuries-see notes | Mandurah Courthouse | GMP-BR-HO | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-12 15:46:00 | Pass | On inspection, found pelmet not clipped in correctly causing safety sensor to not pick up people in the door way.Secured pelmet and adjusted sensitivity as required. All ok.
MSA-DTAG | WA3371425 | Lvl 4- Reports that there is currently no air con in the custody centre | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 16:00:00 | Pass | Return to site. Check operation of lev 4 AC. Found ti be working with no issues. All temps accross floor satisfactory.
MSA-DTAG | WA3371487 | court 2 corridor water damage wall is wet also have ceiling damage | Rockingham Justice Complex | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-07-08 10:15:00 | Fail | ROOF LEAK REPAIRED, WATER DAMAGE TO WALL, CEILING REPAIRED & PAINTED
MSA-DTAG | WA3419344 | **Retrospective work order** Repair access control door | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 3 | CLOSE | 12 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 11:00:00 | Pass | Attended site. Re run cable for card reader with seven core screened cable as incorrect cable in situ for DOTAG formatReader. Needed to run all new cabling as all in one door cable used by previous contractor. Fit off HID reader, lock, reedand REX. Install new Pacom 2 - door controller and terminated all door items into panel. Unable to program as issue with Pacom SQL
MSA-DTWD | WA3370963 | J-10 Female Toilet- Leaking basin tap | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 14:20:00 | Pass | Replace tap set that was leaking
MSA-DTWD | WA3371012 | covered walkway lights going up to T Block, they are not coming on at the set times. | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-17 08:00:00 | Pass | Attended site and signed in. Located walkway lights to T block. Investigated lights switching. Found set times to 6pm to 6.30am. Adjusted times to 5.30pm to 7am as per Kevin’s request. Checked operation of timers and all lights working. Advised site to check the times tonight to ensure it’s what they need. Job complete
MSA-DTWD | WA3371060 | H block, femail toilet - Faulty toilet cistern, LH cubicle; | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 14:20:00 | Pass | Replaced old broken toilet
MSA-DTWD | WA3371069 | Classroom B11 (Electrical) - roof leak on crank line | Rockingham Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-22 13:15:00 | Fail | Carried out leak repairs . Confirmed by site leak has been resolved
MSA-DTWD | WA3371073 | F block science Alarm key pad unresponsive, unable to access; | Rockingham Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-24 11:38:00 | Fail | 12/06/2020Tried using codes on the keypad, none available apart from 1 code.This appears to work ok.Builders still working in F Block so system was in alarm.Could not access the Gallagher computer, need to return Wednesday when access available.16/06/2020Keypad and codes are all ok.Codes were changed a few months ago and user didn’t realise code was different.Denis Jardine tried various codes all working.
MSA-DTWD | WA3371089 | T-Block 1st Floor hallway East has a water leak down the side of the wall | Joondalup McLarty Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 09:00:00 | Pass | wall flashings come away from wall, reattached flashings and sealed
MSA-DTWD | WA3371159 | C48, Salon 4, Red salon- Water leaks (Suspect blocked gutters or downpipe) | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 15:00:00 | Pass | cleaned out box gutter, sump, partially blocked down pipe - sealed surrounding flashing joints and sump, box gutter joint trimmed sheets, trimmed ends, if occurs again, might need works to downpipe.
MSA-DTWD | WA3371195 | - E-Block Restaurant Kitchen, two ceiling double fluro lights not working | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 17:00:00 | Pass | Replaced block E kitchen lights with new fluro tubes and electronic ballasts
MSA-DTWD | WA3371204 | E-Block Deli, GPO under counter has burnt out | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 15:00:00 | Pass | Inspected burnt out 15a single outlet. Made safe, removed and installed new ip56 weatherproof outlet and plug top. Tested and energised
MSA-DTWD | WA3371214 | D-Block Canteen Kitchen walk in freezer lights not working | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 13:00:00 | Pass | Replaced freezer fluro and starter.Replaced store room fluros and starters.Replaced bathroom fluros and starters.
MSA-DTWD | WA3371273 | T block - Lift has tripped out not working | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 12 Jun 2020 | 2020-06-12 16:55:47 | 2020-06-12 16:00:00 | Pass | power related issues
MSA-DTWD | WA3371398 | H block Repair/replace existing rusted guttering | Mandurah Campus (formerly Peel) | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-08-25 14:45:00 | Fail | Materials are on order. Will schedule when they come into stock 25/8/20 Replaced 34m of guttering as per BRAF
MSA-DTWD | WA3371443 | Customer service centre - Faulty auto door | Thornlie Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 16:33:00 | Pass | Main entry customer service ES200. Found emergency stop cable from key switch had caught in belt and pulled out causing door to just down, re terminated and re fit cable and checked over door, tested all ok.There is no charge for this call out as the door is currently under warranty
MSA-DTWD | WA3371465 | L3 roof leak | Perth Campus B6 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-13 15:30:00 | Fail | Investigated area over suspected roof leak and found crank flashing rusted out in areas measured up to replace section over area, unable to access roof sheet damage as flashing sealed up and stripping it may cause issues. Sourced materials to install 10m of custom apron/crank flashing that was previously reported Installed and sealed off all works
MSA-DTWD | WA3371473 | Lvl 2 & 3 - Rooms B329 & B244 passages- broken locks | Perth Campus B6 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-16 10:40:00 | Pass | ajdustment to strike room B329 and B224 plumbing ducts
MSA-DTWD | WA3371505 | L3 B314 roof leak | Perth Campus B6 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 12 Jun 2020 | 2020-06-19 17:00:00 | 2020-08-25 15:15:00 | Fail | water ingress caused by windowsBRAF approvedcompleted works as per quote
MSA-DTWD | WA3371524 | A block student services female blocked toilet | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 09:09:00 | Pass | Attend site finding toilet not blocked, but not flushing. (Cistern issue). Serviced toilet cistern. All flushing ok..
MSA-MRWA | WA3370896 | Lvl 2, West End Office - 3x lights not working please inspect/refurbish | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 12 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-12 14:15:00 | Pass | Attended site and signed in. Located faulty lights and replaced electronic ballasts. Tested all ok. Lights work. Informed PFM and signed out.
MSA-MRWA | WA3371467 | UPS room in basement-battery check not OK | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | General Electrical (EL) | Vertiv (Australia) | 1 | CLOSE | 12 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-12 18:30:00 | Pass | Service Call at Don Aitken Centre at East Perth. UPS has generated an alarm of Battery Fail. After checked andtested.Found It was caused by battery-20. Due to high impedance and battery test did not pass the test.1 x new battery of6FM90 must be replaced asap
MSA-DCS | WA3374802 | Tele comm room- cell call system alarm activating constantly | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Jun 2020 | 2020-06-13 13:59:03 | 2020-07-01 14:58:00 | Fail | Job has been completed through WA3359651.
MSA-DCS | WA3374816 | Monitor 5 in the gatehouse control room is not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Jun 2020 | 2020-06-13 15:10:33 | 2020-06-14 13:15:00 | Fail | Picked up power supply from supplier and attended to replace blown power supply. Restored and tested fully operational.
MSA-DCS | WA3374852 | abattoirs cardis control alarm faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jun 2020 | 2020-06-14 14:00:51 | 2020-07-13 10:38:00 | Fail | Job complete
MSA-DCS | WA3374871 | Control Room-Indigo cameras- Unit 6 & 1 cannot be selected in control room, Unit-6 is not recording | Bunbury Regional Prison-Gatehouse | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jun 2020 | 2020-06-14 16:20:19 | 2020-06-14 12:00:00 | Pass | Unit 1 and 6 cameras not showing in Gatehouse MED database. User ‘security’ permissions reset and access restored. PTZ20 and Unit-3 PTZ not showing on PRU database so errors on database were corrected. Delink both Unit 1 and control room databases to central HLI PC as they had reverted back to their local backup database.
MSA-DCS | WA3378719 | SITE COST Camera 32 at the entrance pathway has gone out | Banksia Hill Detention Centre | WSM-BR-SITE | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Jun 2020 | 2020-06-14 09:56:30 | 2020-06-14 13:45:00 | Fail | Followed by up system restored
MSA-DCS | WA3378756 | Broken lock in crisis care unit. | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | ACE LOCK & SAFE | 0 | CLOSE | 14 Jun 2020 | 2020-06-14 15:25:58 | 2020-06-14 14:30:00 | Pass | Whilst at bandyup womens Prison cell lock in CCunit cell 6 - jammed replaced lock with prison own stock cell lock
MSA-DCS | WA3378761 | SOG ERU- hot roof is leaking | Hakea Prison-Main Gatehouse | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 14 Jun 2020 | 2020-06-15 12:06:22 | 2020-06-15 07:50:00 | Pass | Roof above the gym in sog leaking(celinigs soaked).
MSA-DCS | WA3378765 | Power outage in Gatehouse unable to acesss distrubtion board containg camera control | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 14 Jun 2020 | 2020-06-14 17:01:55 | 2020-09-25 11:30:00 | Fail | Disconnected supply to camera from pole 1 to pole at rear near football oval.
MSA-DCS | WA3378775 | No hot water in unit 13 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 14 Jun 2020 | 2020-06-14 17:39:58 | 2020-06-26 10:27:00 | Fail | nil
MSA-DCS | WA3378782 | Casuarina Prison, Unit 13, Elec HWS is not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 14 Jun 2020 | 2020-06-14 19:16:19 | 2020-06-14 19:00:00 | Pass | Investigate fault on unit 13 boiler, found fire system interrupting water. Fire techs to attend
MSA-DTWD | WA3378783 | North Metro TAFE-Joondalup Kendrew Campus - D Block - Ground Floor - 1 x smashed window | Joondalup Kendrew Campus | GMP-BR-RC | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 0 | CLOSE | 14 Jun 2020 | 2020-06-14 19:30:12 | 2020-06-14 17:45:00 | Pass | ATTENDED SITE AND REPAIRED BROKEN WINDOW IN D BLOCK GYM 6.38 CLEAR LAMINATED SAFETY GLASS1 - 1705 X 828
MSA-DCA | WA3382701 | cooling tower station temp 46.18-Craig Hogan aware | Art Gallery of WA - James St-Main Building (Block B)-Level 5 - Roof-Rooftop Plant - External Area | GMP-BR | Air Conditioning | Cooling Tower (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 12:00:00 | Pass | Attended call-out Cooling Tower VSD's faulted. Tower basin 40°c plus. Reset and monitored. Arranged remote access setup via AMT and their IT dept. Adjusted Chiller CW DP switch.no further alarms. Contacted contractor to quote wiring changes required for VSD's.No further pump status' indications have been registered while being monitored and manually driven for testing.Quotation to be submitted for mains feed alterations to VSD's.
MSA-DCS | WA3382602 | Response road gate is not opening. | Casuarina Prison-Gatehouse | GMP-BR- HO | Electrical | Materials (EL) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 15 Jun 2020 | 2020-06-15 11:13:24 | 2020-06-15 10:45:00 | Pass | Job completed - Two technicians travelled to site. Inspect Response gate and found over load tripped. Reset. Test auto, all okay. Testmanual and found razor wire obstruction near full closed. Moved razor wire, now okay. Test, now okay. Motor currents0.4A, okay. Test auto operation several times, all okay.
MSA-DCS | WA3382614 | unit 2 cell 79 roof leaking throungh shower exhaust fan | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-23 11:00:00 | Fail | REPAIR ROOF AND REPLACE FLASHING
MSA-DCS | WA3382635 | Gascoyne A5 Window seal leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-22 11:00:00 | Fail | WINDOW RESEALED
MSA-DCS | WA3382644 | Hotham B2 Toilet running continually | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-18 09:12:00 | Fail | Replaced inlet valve and rewashered isolation tap
MSA-DCS | WA3382666 | U7 E19-E24 Cell lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 09:00:00 | Pass | Lights tripping reset
MSA-DCS | WA3382689 | Unit 8 D1 Call indicator light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-15 11:00:00 | Pass | Audio loud and clear in cell and control but the LED was faint. Removed and repaired LRD. Required extra long rivets to secure the intercom. Tested loud and clear in the cell and in the control room. LED tested ok. Parts used:Consumables
MSA-DCS | WA3382697 | Unit 6 B8 toilet leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 10:06:00 | Pass | Replaced outlet washer
MSA-DCS | WA3382704 | Unit 1 The toilet in cell A4 is leaking and needs fixing. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-23 09:00:00 | Fail | Cleaned sand from base of cistern and replaced outlet rubber.
MSA-DCS | WA3382719 | Unit 4 Mainly A wing but all wings in unit 4 , the windows at the end of the wings need fixing. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-10-13 14:30:00 | Fail | NEW WINDOW WINDER FITTED & PARTS RENEWED
MSA-DCS | WA3382739 | EBI 2 lost camera's an images | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Jun 2020 | 2020-06-15 12:21:41 | 2020-06-15 10:30:00 | Pass | Rectified and fixed faulty EBI WS, job completed.
MSA-DCS | WA3382741 | Unit 7 - A Wing cell call A8 is faint in volume at receiving end | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-26 11:30:00 | Fail | Tested call call, audio low, removed cell call from wall found retaining holes obstructed by concrete and inner mounting box putting pressure on side of cell call a PCB. Removed part of mount box lining to enable removal of concrete, using hammer and cold chisel & SDS Drill. Drilled out holes to enable fixing with Rivets, adjusted PCB volume pot and retested, good audio both ways, refixed box to wall, final audio test with gate control. Still good audio.
MSA-DCS | WA3382756 | Unit 5 - B Wing Regithermic oven door is jamming, can you please repair if possible. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 09:35:00 | Pass | Adjust door latch as required test ok.
MSA-DCS | WA3382759 | Unit 3 Upper Bunk personal light doesn't work Cell B04 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 11:30:00 | Pass | Investigate and repair unit 3 B4 bed light
MSA-DCS | WA3382763 | Unit 3 - D8 shower drain blocked - smells | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 14:41:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3382769 | Unit 6 - A8 blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 11:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3382781 | Unit 7 - C Wing Wires need looking at and freezer is constantly 'BEEPING" | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 14:57:00 | Pass | Unit to be replaced with spare on site
MSA-DCS | WA3382784 | Unit 6 - C6 drain under sink over running. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-02 09:54:00 | Fail | Used acid and plunger to clear blockage in drain under basin.
MSA-DCS | WA3382788 | unit 4 low water pressure | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-10-12 13:00:00 | Fail | This job has been closed long ago as it was a double up job.
MSA-DCS | WA3382792 | Unit 6 Cell A9 has a toilet bowl running water. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 12:00:00 | Pass | Replaced worn outlet rubber inside cistern.
MSA-DCS | WA3382810 | Unit 3, D Wing Fluro Light- Light Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 14:00:00 | Pass | Repaired light
MSA-DCS | WA3382813 | Unit 1, Cell A14- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 15:00:00 | Pass | Repaired light
MSA-DCS | WA3382819 | Unit 5, Cell A13- Light switch outside cell broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 14:00:00 | Pass | Replaced light switch
MSA-DCS | WA3382823 | Unit 3, Cell D11- Cell Call faulty, buzzing sound | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 09:05:06 | 2020-06-15 12:30:00 | Pass | Poor audio quality in control. Removed and replaced intercom. Tested, loud and clear in cell and in control. Parts used:Cell intercom CI-CC/270/120Consumables
MSA-DCS | WA3382826 | Kitchen, Large tilt kettle- not switching on | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 09:07:15 | 2020-06-15 15:00:00 | Pass | Resoldered wires to lights and tested kettle, tested ok.
MSA-DCS | WA3382831 | unit 6 B wing/showers, middle cubicle shower head leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 10:00:00 | Pass | Replaced leaking hot spoon shower set.
MSA-DCS | WA3382838 | Unit 6 - A12 Window runners broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-02 14:30:00 | Fail | SPIRAL BALANCES & FEET REPLACED
MSA-DCS | WA3382848 | External Reset Visits Centre toilets Entrance Door Jamming Door Frame & Damaged Door Frame Flashing | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-16 14:00:00 | Pass | Attended site and carried out repairs to the toilets entry door.Replaced closer sliding mechanism
MSA-DCS | WA3382856 | Unit 6 - D Wing showers have broken floor tiles on entering two of the cubicles. | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2021-03-09 18:00:00 | Fail | new tiles installed to damaged area
MSA-DCS | WA3382869 | Unit 1 - Cleaning Store Water leak near sink in B wing store room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-23 08:00:00 | Fail | Retightened tap outlet to wall and replaced leaking orings.
MSA-DCS | WA3382885 | Unit 14 - A Wing Cell A01 light no working from inside cell | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 08:30:00 | Pass | Investigate and repair unit 14 A1 cell light and switch
MSA-DCS | WA3382892 | Unit 2 - C Wing Door hinges cell C13 need maintenance, door is dragging./relign lock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 11:30:00 | Fail | Replaced hinges, door plate and lock. Attend site weld on strike plate, remove edge capping and main lock, service, repair and re install with new fixings
MSA-DCS | WA3382904 | gate house master control Cameras not Recording | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Jun 2020 | 2020-06-15 13:47:49 | 2020-06-15 12:45:00 | Pass | All cameras showing offline on display , rectified and fixed.job completed.
MSA-DCS | WA3382909 | Gatehouse- foyer light faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 15:00:00 | Pass | Investigate and repair faulty gatehouse foyer light
MSA-DCS | WA3382913 | kitchen bell broken winder | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 09:00:00 | Pass | Kitchen Bell broken winder. Remove broken handle. Makeup new Stainless Steel Handle. Modify mounting, fit new handle, test.
MSA-DCS | WA3382914 | kitchen meat slicer not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 13:49:00 | Pass | Kitchen Meat slicer no.2 not working. Check slicer & controls. Dismantle circuit board & relay, all wet causing short. Remove water dry out board & wiring. Assemble & test.
MSA-DCS | WA3382922 | ASO Office- Door lock jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 09:53:48 | 2020-06-17 11:30:00 | Fail | Supplied and installed replacement cylinder.
MSA-DCS | WA3382928 | gate from master control tunrstie not working | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Jun 2020 | 2020-06-15 13:55:49 | 2020-06-16 08:15:00 | Fail | Rectified and fixed the faulty turnstile entry/exit, job completed.
MSA-DCS | WA3382941 | Observation tower 2 - Air Con is not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 14:45:00 | Pass | Fault found to be user error. Remote not on correct mode for operation.
MSA-DCS | WA3382963 | Unit 4, Cell C9- Windows stays faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-29 12:30:00 | Fail | RENEW SPIRAL BALANCES TO WINDOW UNIT
MSA-DCS | WA3382965 | Unit 4, Cell C2- Window stays faulty glass also cracked . | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-01 15:00:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3382973 | Unit 14, B & D- Fridge/freeze keeps tripping out power | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 08:30:00 | Pass | Repaired faulty power circuit in unit 14
MSA-DCS | WA3382977 | Unit 4, cell C13- Window stays faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-29 13:30:00 | Fail | RENEW SPIRAL BALANCES TO WINDOW UNIT
MSA-DCS | WA3382985 | Admin, Lobby Area- Vinyl has lifted- trip hazard | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 09:00:00 | Pass | SUPPLY AND INSTALL NEW RUBBER FLOORING TO AREA
MSA-DCS | WA3382987 | Common Café/Kitchen area safety button is not working when the hot water is being used and could cau | East Perth-Main Building-Level 3 | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 10:18:43 | 2020-06-15 13:40:00 | Pass | Re program to safety button. All operating ok.
MSA-DCS | WA3383010 | Obs tower 2 PA system to be reinstated please. | Hakea Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2021-08-11 15:00:00 | Fail | Re activate PA system from OBS tower 2, tested working. Job completed.
MSA-DCS | WA3383016 | Various carpentry faults as listed in long description | East Perth-Main Building-Level 4 | GMP-BR- HO | Carpentry | Materials (CA) | Schlager Construction Group | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 15:00:00 | Pass | Attended site and carried out fit out as requested on the long description.
MSA-DCS | WA3383054 | Cyrenian passage door- Lock does not open with some keys | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 15:00:00 | Pass | Faulty lock cylinder replaced.
MSA-DCS | WA3383065 | Lenard- 2x smashed cell windows | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 12:30:00 | Fail | CELL WINDOWS REGLAZED
MSA-DCS | WA3383067 | Lenard- Cell C03- Smashed obs window & mirror | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 16:00:00 | Fail | OBS WINDOW & MIRROR REPLACED
MSA-DCS | WA3383070 | Lenard, A Wing- smashed window in laundry approx 1000x550 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-07-03 10:00:00 | Fail | WINDOW REGLAZED
MSA-DCS | WA3383074 | Turner, Cell C03- Toilet not flushing very low water pressure | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-25 10:55:00 | Fail | Replaced faulty parts in the plumbing duct
MSA-DCS | WA3383084 | Unit 14, Cell D11- Blocked shower drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 11:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3383091 | Unit 14, Cell B10- Cold water tap not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 14:00:00 | Fail | Investigated for fault. Replaced split pins. Tested all taps.
MSA-DCS | WA3383095 | Unit 6, A Wing, Cell A9 - toilet running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 10:00:00 | Fail | Replaced leaking inlet valve.
MSA-DCS | WA3383097 | Unit 2, Cell B9- Toilet button is sticking & toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-30 15:00:00 | Fail | Removed flush button. Cleaned button and housing and reassembled. Tested
MSA-DCS | WA3383102 | Unit 6, B Wing- Middle shower rose water running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-22 08:00:00 | Fail | Replaced leaking cold spindle.
MSA-DCS | WA3383106 | Unit 1, Cell D6- Metal strip loose on window | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 12:00:00 | Pass | SLIDING WINDOW REPAIRED
MSA-DCS | WA3383107 | Unit 1, Cell B10- Metal strip loose on window | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-26 13:00:00 | Fail | RENEWED SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3383122 | Unit 3, Cell D12- Window stays doesnt work | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-26 11:15:00 | Fail | RENEWED SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3383125 | Unit 3, Cell D11- window stays doesn't work | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-26 12:00:00 | Fail | SPIRAL BALANCES REPLACED
MSA-DCS | WA3383143 | Unit 3, Cell C12- window stays doesn't work | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-01 09:15:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3383146 | Unit 3, Cell C09- window stays doesn't work | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-01 10:00:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3383196 | Unit 1, Cell 14 - heater GPO faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 08:30:00 | Pass | Investigate and Repair Unit 1 Cell 14 Heater GPO
MSA-DCS | WA3383217 | Unit 1, Hut toilets floor drain blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 14:00:00 | Pass | Clear blocked floor waste drains in unit one hut toilet block.
MSA-DCS | WA3383273 | Unit 2, Control Room- CCTV monitor not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Jun 2020 | 2020-06-15 16:10:20 | 2020-06-15 16:05:00 | Pass | Rectified and fixed the frozen image on both monitors , job completed.
MSA-DCS | WA3383285 | Unit 3, Cell B9- Window stays dont work | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-26 14:30:00 | Fail | RENEWED SPIRAL BALANCES
MSA-DCS | WA3383289 | Unit 3, Cell B7- Window stays dont work | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-26 13:45:00 | Fail | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3383331 | Kitchen- Potato peeler not working | Wooroloo Prison Farm | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-09-01 13:00:00 | Fail | Kitchen Potato peeler faulty. Check peeler. Disconnect power & water, remove to workshop. Dismantle shaft & motor. Machine shaft, overhaul motor & repair mounting . Repair motor mounting frame. Install bearings, shaft, seal & motor. Fit new drive pin shaft. Return to kitchen, new switch & 3 phase wall plug. Assemble all & test.
MSA-DCS | WA3383389 | Unit 1, Pod 3- Abultions extraction fan faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 10:00:00 | Pass | Reset sensor power and tested
MSA-DCS | WA3383408 | Internal Perimeter Zone 1 Perimetertrax constantly alarming | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 13:10:31 | 2020-06-15 16:30:00 | Pass | Ran plot graph and found zone to be noisey. Reset Comms to the module via UCM program on Senstar PC. Reset power to module in sallyport aircon plant room. Ran plot graph, walk tested and tuned zone. Tested ok.
MSA-DCS | WA3383424 | Unit 6 cell D 8 bottom bunk light not working . | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 11:30:00 | Pass | Repaired faulty lights in unit 6 d8
MSA-DCS | WA3383427 | Unit 14 cell A 2 light not working . | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 10:00:00 | Pass | Repaired faulty lights in unit 14 a2
MSA-DCS | WA3383438 | gate control cardax system not allowing any acces to us eystrm | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 13:23:49 | 2020-06-15 18:24:00 | Pass | Gate house controller offline, checked connections between controller and server. Swapped 5m Cat5e cable from switch to Server.Controller online but unable to clear backlog of messages.Logged into controller and cleared buffers.Controller back online but multiple faults from inputs and outputs attached to controller. Rectified inputs. Main gate relay not working.Reprogrammed to spare relay and tested all doors and all macros. Working from server.Tested again from control and front desk. All ok
MSA-DCS | WA3383504 | Control Room - Maintenance workshop door controller is offline | Boronia Pre-release-External Area-Ground Floor | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 14:59:00 | Pass | Moved controller over to planet switch in panel came online with no issues and tested ok
MSA-DCS | WA3383505 | Gate House- Pumphouse, domestic water tank- Burst pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 09:00:00 | Pass | Repaired burst pipe on domestic water tank 20mm float line.
MSA-DCS | WA3383539 | Assessments R27 Unable to open barrel | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 14:31:31 | 2020-06-16 16:00:00 | Fail | supplied and installed new lock and cylinder
MSA-DCS | WA3383546 | Unit 1, Cell B6- Vesda burnt | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 14:29:00 | Pass | replace burnt sampling point
MSA-DCS | WA3383548 | Unit 8, C Wing- Wing grille motor constantly running | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-01 08:00:00 | Fail | Noisy grill motor
MSA-DCS | WA3383559 | Boilerhouse- Boiler No 3- Air pressure/flame scnner fault | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 14:19:00 | Pass | Travel to workshop pick up programmed book. Travel to site and sign in complete tool check with officer. Travel to boiler house. Identify faults from yesterday on Allen Bradley screen, boiler had 3 faults yesterday in 5 minutes under flame fail/air pressure fault on burner. Did not have any other faults yesterday. Tested air pressure at switch. Tested between block valves. Tested flame fail and made sure scanners were still clean. Faulted burner in other ways and made sure it could only be flame or air pressure. Could not find anything unusual everything seemed to be working as normal boiler did not fault whilst onsite or since it has been started this morning. May of been a one off fault or something temporarily playing up but very hard to diagnose without witnessing the fault happen. Customer to see how they go for the day. Boiler 2 burner motor a bit noisy possibly a bearing on its way out. there is another burner on site the same, customer wants to potentially try the motor on the
MSA-DCS | WA3383594 | Monitor Room- Camera vision returned to right hand screen | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Jun 2020 | 2020-06-15 20:24:10 | 2020-06-15 17:30:00 | Pass | Attended site checked and found right hand side monitor of monitor wall display messed up. Rearrange monitor layout as customer request.
MSA-DFES | WA3382621 | SO ensuite toilet is blocked and flowing out onto floor | CFRS Claremont | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 15 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 17:00:00 | Pass | Use plunger to clear blockage
MSA-DFES | WA3382859 | Ensuite Room 11 - Light globe & loose down light fitting needs repair | CFRS Fremantle | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 14:15:00 | Pass | Replace faulty light with new
MSA-DFES | WA3382946 | Engine Room - Exhaust fans in engine room not turning off | CFRS Belmont | GMP-BR | Electrical | General Electrical (EL) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 11:30:00 | Pass | Repaired broken and loose wires on engine room exhaust fan control panel
MSA-DFES | WA3383005 | Engine room door 1 doesn’t fully close | CFRS Belmont | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-15 16:00:00 | Pass | Technician attended the site of Belmont Fire Station Bifold door AL403522016 on 15/06/2020. Technician deactivated limits which controls 12Vdc relay for motor limit and exhaust fan to increase stop added to relay 100v capacitor 60v which increase travel time by 0.5second , enough to ensure close limit is properly activated.Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3383015 | station ground drying room 3 TILES CRACKED UNDER AIRCON | CFRS Vincent | GMP-BR | Flooring | Tiling (FL) | AWB Co. | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 15:00:00 | Pass | 6.6.20- Attended site to measure up, Sourced tiles ready for Wednesday.17.6.20-Removed old broken tiles & adhesive then cleaned up area.Installed new tiles & grouted over.Clean up.Photos & paper work.
MSA-DFES | WA3383249 | Lights in stairwell and ½ lights in gym disconnected due to water leak | CFRS Perth | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 10:15:00 | Pass | Re energised power to lights in gym and stairwell.
MSA-DFES | WA3383258 | Stairwell into gym- Walls have water damaged and need repainting | CFRS Perth | GMP-BR | Painting | Internal (PA) | AWB Co. | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 13:30:00 | Pass | prepared and painted water damaged ceiling in stairwell into gym and staircase
MSA-DFES | WA3383396 | rear yard red light on one of the ballast not working back of FS | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-26 12:30:00 | Fail | Arrived onsite and signed in at 1115We located located the faulty light and investigated, looks light weather has gained entry however to repair the light we need a specialised contractor to complete works, we are currently organising the contract to fix the lights.Signed out and left site at 1200
MSA-DFES | WA3383483 | Front House, Kitchen light blown | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-17 14:30:00 | Pass | Located faulty light and tested it, light was damaged internally sowe replaced with a new light.
MSA-DFES | WA3383525 | Fix overhead light in the front office- Further information below | O'Connor Fleet Storage | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 09:30:00 | Pass | Complete
MSA-DFES | WA3383596 | Cistern in station Officers toilet may require a new float. | CFRS Malaga | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-23 11:00:00 | Fail | 23/06/2020Attend to repair cistern in S/o toilet fitted new mini stop inlet valve and outlet washer test operation
MSA-DTAG | WA3382491 | 6 of 8 lifts are not working. Please inspect and repair. | Central Law Courts | BUG-MW | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 15 Jun 2020 | 2020-06-15 10:04:41 | 2020-06-15 08:30:00 | Pass | Not chargeable
MSA-DTAG | WA3382562 | Cannot connect to database or see Graphics maps on floors-see notes | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 10:30:00 | Pass | Reset both Hosts and turned on servers on both Hosts. Reset controller to server.
MSA-DTAG | WA3382659 | ground Magistrates HWU element has failed | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 15 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-15 15:32:00 | Pass | Replaced faulty heating element.Water coming out from the hwu(hot tap) isnt clear due to the tank being corroded.( Bottom of the tank full of the tank corroded)If the water doesn’t clear up in the next few days the hot water system will have to be replaced. Hwu can be wired up again(Iain adviced)
MSA-DTAG | WA3382939 | L1 FIP Main FIP & vesda panel on level 2A needs to be reset after power outage. | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 12:15:00 | Pass | Cleared fire panel and vesda fault. Details in tech report
MSA-DTAG | WA3382968 | Level 6 and Mezzanine unable to view any of the security cameras on our security monitors. | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-16 09:00:00 | Pass | job completed - Logged onto video wall computer and ran Milestones on Level 6 and Mezzanine Floors.Job completed
MSA-DTAG | WA3382979 | L1 custody Light in upper custody area is flickering | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-16 08:30:00 | Pass | Replaced flickering tubes
MSA-DTAG | WA3383265 | Listings Business Area- Light flickering above listings team member Mikaela Kelsall | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 11:00:00 | Pass | Job complete
MSA-DTAG | WA3383271 | Ground - Custody bail door (to Sally Port) button on controller not engaging | Midland Courthouse-Main Building | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-19 14:30:00 | Fail | Replaced broken push button, tested all buttons and replaced 3 buttons that were intermittent.Tested all doors and confirmed operational 5x bell press rocker switches supplied by semeLeft 1x spare onsite
MSA-DTAG | WA3383280 | Ground - Custody bail door exiting the building is sticking & sometimes not engaging | Midland Courthouse-Main Building | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 14:27:00 | Pass | Duplicate of WA3383271
MSA-DTAG | WA3383335 | Lvl 13, Staff Kitchen - Bill unit is displaying “level sensors wrong” | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 10:55:00 | Pass | TECH COULD NOT GET ONTO PROMAP AS EMAIL ERRORS AND HE NEEDED TO RESET PASSWORD - ARRIVED ON 17TH CHANGED PARTS LEVEL SENSOR KIT ASSY, INLET SOLENOID KIT AND HOT PUMP COULD NOT RESET AS ISSUES AS IT TURNED OUT WITH MAINS POWER HE RETURNED ON 18TH AT 10AM AND WAS ON SITE FOR AN HOUR TRYING TO RESET - ADVISED SITE THAT THEY NEED AN ELECTRICIAN TO REPAIR MAINS POWER - UNIT WAS TESTED WITH AN EXTENSION CORD WITH ANOTHER POWER OUTLET AND WAS WORKING WELL ON TESTING.
MSA-DTAG | WA3383378 | ground lift 2 out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 16:00:00 | Pass | Car door issue, not seeing KTS. Had to give the door drive multiple mans open and close runs, as was shuddering at final limit.
MSA-DTWD | WA3382572 | B40 student zone internal mold on walls | Murdoch Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 15 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 15:30:00 | Pass | Prepared and painted mould effected walls and skirting window sill
MSA-DTWD | WA3382686 | B block staff room L1 faulty card reader can only access with key | Mandurah Campus (formerly Peel) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 1 | CLOSE | 15 Jun 2020 | 2020-06-15 17:00:00 | 2020-06-17 10:15:00 | Fail | 15/06/2020, 1245-1315Took apart lock, confirmed voltage ok 12vdc also lock opens when power dropped.Reader does not trigger door, no drop when swiped. See attachments for reader type.17/06/2020, 0800-1015Looks like it was not the reader was actually the door controllerReplaced door controller for foor 7Tested ok
MSA-DTWD | WA3382750 | Unit 7 ground canteen Bug zapper not working | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 02:00:00 | Pass | Attended site and signed in. Located bug zapper and found faulty fluros and starters. Replaced fluros and starters. Tested all ok. Remounted bug zapper. All ok.
MSA-DTWD | WA3382800 | tower block L3 east air con vent has fallen out of the ceiling | West One Services | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 12:00:00 | Pass | Arrived on site, signed in and contacted facilities manager, spoke to kim and he said that a grilli had fallen out, inspected grille and found that pop rivets have snapped and worn through, we did bring this up a few months ago as a sasfety issue due to the grilles being steel and very heavy they could easily cause damage to personel and equipment .We went to lebel 3, dismantled the desk and then started the repair We then redrilled the grille and fixed off with tek screws with an anti vibration rubber to stop this happening again , we reccomend doimg this to every grille in the building as this is the second time this has happened
MSA-DTWD | WA3382938 | U Block, Rooms U009, U017 - Numerous roof leaks | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 09:00:00 | Pass | Leaks to U17 and U009- U117 Sealed around vetn systems - further leaks from flexible joint to evap systems. Advised site
MSA-DTWD | WA3383061 | M Block, Room M008- Room too cold | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-08-27 07:36:00 | Fail | 15.6.20: Arrived onsite. Gained access to M008. Found tempsnto be low. Found Main circuit breaker supplying VAV's for that wing of M block had tripped. Commenced testing VAV's for electrical faults. Further testing required. Have informed FM of fault and have scheduled to return for further testing. 18.6.20: Continued on with fault finding. Found various faults on VAV' serving classrooms north. Will submit information for repairs. M.008 heating back to normal operation.
MSA-DTWD | WA3383257 | Block Lift intermittent fault does not go to selected level at times | Joondalup Kendrew Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 15 Jun 2020 | 2020-06-16 17:00:00 | 2020-06-15 13:56:00 | Pass | CONTROLLER - LOCK BEAK - RUNNING ON ARRIVAL
MSA-DTWD | WA3383311 | Fire panel fault | Perth Campus B6 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 11:30:00 | Pass | Attended site - investigated fault - device missing L6 D116.Replaced detector with new - loop test - system normal.
MSA-DTWD | WA3383458 | Block 6 ground Spray Booth in Painting & Dec Filters appear to be blocked. Heavy back pressure | Thornlie Campus | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-02 15:00:00 | Fail | Filters replaced for intake fan, Braf for exhaust fan filtersSub contractor attended site 10/07/20 to replace filters and certify fume cupboards
MSA-DTWD | WA3383481 | A block ground A009 cleaners cupboard Electric Hot Water Unit not heating the water | Balga Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-30 15:15:00 | Fail | Replaced hot water unit
MSA-DTWD | WA3383487 | E Block, Ladies toilets, far end cubicle, the water is continuously running | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 12:15:00 | Pass | COMPLETED
MSA-DTWD | WA3383489 | E-Block Male Staff Toilet, urinal backing up when flushed | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 15 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 13:15:00 | Pass | COMPLETED
MSA-DTWD | WA3383510 | P Block, P011 Electrical Store- Vinyl floor is damaged (trip hazard) | Balga Campus | GMP-BR | Flooring | Vinyl (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-23 16:00:00 | Fail | Replace damaged section of vinyl flooring
MSA-DTWD | WA3383532 | Block 9, Plant room- Sacrificial Anodes in chiller are faulty | Thornlie Campus | GMP-BR | Refrigeration | Chiller (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 15 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 11:30:00 | Pass | Replaced chiller anodes
MSA-MRWA | WA3382452 | AC-1 Fault Basement Server Room and Server room CRAC Alarm | Don Aitken Centre MRWA Head Office-Main Building | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 15 Jun 2020 | 2020-06-15 07:01:11 | 2020-06-15 04:30:00 | Pass | System reset, comms fault cleared. System operating as required
MSA-DCA | WA3385970 | graffiti in multiple locations on southern art gallery way adjacent to carpark | Perth Cultural Centre Precinct - Urban Orchard | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-23 07:30:00 | Fail | Graffiti removal in multiple locations on southern art gallery way adjacent to carpark
MSA-DCS | WA3384950 | Yeeda Peel roof leak | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 16 Jun 2020 | 2020-06-18 17:00:00 | 2020-07-08 15:00:00 | Fail | REPAIR FLASHINGS REPAIR ROOF LEAK
MSA-DCS | WA3384961 | control camera 25 no Picture (camera issue linked with camera 32 ?) | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 16 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-16 12:00:00 | Pass | Replaced faulty fiber modem, camera back to normal operations. Job completed.
MSA-DCS | WA3384981 | unit 2 cell 76 light switch faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 15:00:00 | Pass | Investigate and repair Unit 2, Cell 76 light switch
MSA-DCS | WA3384985 | unit 1 dairy hut cells 26,27&28 gpos not working above doors | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 09:00:00 | Pass | Investigate & repair Unit1 Dairy hut's power
MSA-DCS | WA3384994 | Unit 13 B and D Regi oven has blown up sparkes came out the back may need replacing. | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 07:56:09 | 2020-06-16 14:15:00 | Pass | Found oven working ok. Apparently it was a fridge which has since been removed.
MSA-DCS | WA3385019 | Unit 4 - A Wing cell A 11 sink leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-01 08:00:00 | Fail | Installed new fibre washer on basin tap. Connected pipework and tested
MSA-DCS | WA3385022 | Unit 13 - B Wing B10 shower is blocked keeps flooding | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-02 10:00:00 | Fail | Used acid and plunger to clear blockage in shower drain
MSA-DCS | WA3385048 | Eyre, B1 - Shower head & tap spraying everywhere | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 10:03:00 | Pass | Pulled apart and cleaned shower head
MSA-DCS | WA3385074 | Visits Centre - gas Heater not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-16 12:00:00 | Fail | Supply and install new radiant space heater in visitor centre.
MSA-DCS | WA3385111 | Dairy pasturisering room - double doors faulty require replacing/repairs | Karnet Prison Farm | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-08-28 12:15:00 | Fail | DOORS REPLACED & PAINTED
MSA-DCS | WA3385133 | Back of office facing AKA Lane window leaking | Rockingham Justice Complex | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-17 11:30:00 | Pass | Attended site and carried out repairs to the windows that where leaking on the southern side of building.
MSA-DCS | WA3385207 | Unit 5, B wing - Fluorescent Light outside B7 broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 12:30:00 | Pass | Replaced lights
MSA-DCS | WA3385221 | Reception, toilets residents - Light has failed (It is an element shaped light 2 pin) | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-23 08:00:00 | Fail | Replaced faulty lamps
MSA-DCS | WA3385269 | Unit 3, Cell B4- Window stays dont work | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-01 11:45:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3385272 | Unit 3, Cell B2- Window stays dont work | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-01 12:45:00 | Fail | renewed spiral balances and feet to window units
MSA-DCS | WA3385273 | unit 1 hut ablustions blocked drain sewerage over flow | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 10:09:48 | 2020-06-17 12:00:00 | Fail | Clear blocked sewer using drain Jetter.
MSA-DCS | WA3385335 | Gate House - Pump House No Water to domestic water tanks/pumps in pump house | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 14:11:47 | 2020-06-22 15:00:00 | Fail | 16/6/20 - Investigated cause of no water supply to prison. Switched pumps of and opened main water valve to supply low pressure water to prison. Repaired burst 100 mm copper main on domestic tank quick fill line. BRAF raised to investigate faulty valves on domestic tank, repair domestic tank float valve and to repair bypassing check valve on outlet of pump 1.Pump 2 made primary pump and pump 1 isolated. Pump turned back on to pressurise prison and main bypass valve shut.22/6/20 - Replaced faulty 20mm float valve on domestic water tank, that controls tank quick fill valve.
MSA-DCS | WA3385349 | Control room - Montior # 3 not working | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 10:13:46 | 2020-06-17 12:15:00 | Fail | Attended site checked and found Monitor 3 cameras back to normal already. But Monitor 2 for alarm viewer and lagging is stuck on alarms even alarms have been cleared. Located the problem to be the Indigovision workstation problem, rectified the problem and tested all ok.
MSA-DCS | WA3385356 | Education, room 5/6 & 2 - GPO tripping, room 2 GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 10:18:44 | 2020-06-16 13:00:00 | Pass | Tripping power
MSA-DCS | WA3385361 | Unit 3, D wing Dayroom - drain pipe leaking from water tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 10:21:54 | 2020-06-17 09:15:00 | Pass | Replace sinks trap
MSA-DCS | WA3385504 | UNit 8, Cell A4- Stop tap is leaking in the service duct | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-17 14:33:00 | Pass | Turned off water to units removed and rewasherd and valved x2 taps
MSA-DCS | WA3385554 | Internal 9MX constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 15:01:07 | 2020-06-16 14:00:00 | Pass | Rectified and fixed damaged connection, job completed.
MSA-DCS | WA3385557 | Internal 20MX constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 15:02:55 | 2020-06-26 13:00:00 | Fail | Replaced damage mx cable, calibrate and test, job completed.
MSA-DCS | WA3385621 | repair burst pipe behind unit 4 west side (B/D) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-17 13:00:00 | Pass | 16/6/20 - Investigated source of leak behind unit 4.17/6/20 - Dug up and exposed pipework. Removed damaged pipe and replaced with new. Tested. Denzo wrapped. Backfilled hole.
MSA-DCS | WA3385645 | Amenities - repair ceiling in amenities next to projector due to water damage | Casuarina Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2021-03-19 15:30:00 | Fail | CEILING HAS BEEN PREPARED & PAINTED
MSA-DCS | WA3385738 | Medical Clinic, medical centre - Air con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-17 12:45:00 | Pass | Reprogrammed schedule timer and test ran units. All ok
MSA-DCS | WA3385746 | Perimeter PTZ camera 19 not activating | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 16:36:29 | 2020-06-16 15:45:00 | Pass | Checked Camera 19 Recreation PTZ working ok in Gate Control. Found problem in Security office CCTV workstation. Rectified the problem and tested PTZ function ok in security. Explain to customer that Recreation PTZ is not perimeter PTZ and it is not responding to Zone alarms.
MSA-DCS | WA3385750 | Perimeter, zone 15 activating & lagging | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 16:37:57 | 2020-06-16 16:45:00 | Fail | Checked on Indigovision Control Center for Zone 15 settings are ok. Walked test in Zone 15, confirmed with Control officer alarm activated and reset correctly, cameras are showing on monitor wall correctly.
MSA-DCS | WA3385752 | MMU - Cell MA & MB- cell call not working | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 16:38:47 | 2020-06-16 14:45:00 | Pass | Attended site checked on field and found MMU cell MA&MB cell call with unit officer and confirmed cell call functioning correctly both sides. Can’t see the problem.
MSA-DCS | WA3385756 | Unit 1, A WIng- Security grille not opening off electric lock | Bandyup Prison | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 12:39:39 | 2020-06-16 15:00:00 | Pass | job completed - Travel to site. Inspect nit 1 A wing security grill. Outer lock now working. Had issue over the weekend. Seme issue.Outer lock/pattress hanging. Refit with new fixings. Both tested, all okay.
MSA-DCS | WA3385757 | Unit 1, Control, B Wing Door- self closer faulty | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 12:41:00 | 2020-06-17 13:30:00 | Fail | Attended site and carried out repairs to the faulty door closer that was not operating correctly.
MSA-DCS | WA3385761 | Reset building outside- central heating system not working | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-17 13:30:00 | Pass | Arrived to site and signed in at entry.Accessed Reset building and spoke with RESET ladies regarding issue.Gas heater not working correctly along back wall.Unit blowing hot air but has a red light up on front panel.Can not find any information on unit online.Advising staff to book a new job in with plumbers to inspect.All air-conditioning working okay in the building.
MSA-DCS | WA3385781 | Canteen stores alarm, wont arm | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 12:53:41 | 2020-06-19 13:28:00 | Fail | Sourced parts, attended site, repaired multiple ethernet network faults, tested OK. Job Complete
MSA-DCS | WA3385823 | Unit 1 staff lunch room Hydro Tap not Working | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-30 17:54:00 | Fail | Repaired zip unit in staff lunch room.
MSA-DCS | WA3385825 | Unit 1 Electrical room Fire Panel Showing Fault Boiler Room | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 17:16:43 | 2020-06-16 15:23:00 | Pass | 2 faults present in unit 1 on time of arrival.Smoke detector loop 2 device 25 in boiler room dirty/maint fault. replaced with new.Cells C/D 15/16 showing fault. Found pipe three closed by inmate. Manually open and reset. System normal
MSA-DCS | WA3385834 | Unit 2 A-B Wing Laundry Room Lights Not Working | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 11:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3385842 | Unit 2, A1 - medical hatch cant get key into lock. cell unusable | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 13:25:29 | 2020-06-18 14:45:00 | Fail | Replaced hatch lock
MSA-DCS | WA3385872 | Recreation-Overhead dome lights not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-17 13:30:00 | Pass | Tested and reset rec area lights
MSA-DCS | WA3385878 | day stay lock not working from inside room | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 17:56:28 | 2020-06-17 13:30:00 | Fail | Day stay Lock unable to be locked from inside-this lock is not suitable for this applicationlock will be changed to free access lock from inside lock is being built.Lock fitted today 17 th June key access external , free to egress internal
MSA-DCS | WA3385977 | Main building, Front Main Entry door lock - Door lock is hard to unlock causing key to break inside. | Nyandi Training Academy | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 11:40:00 | Pass | Serviced lock and adjusted strike in fixed leaf door.
MSA-DCS | WA3386029 | Lighting rod on top of camera is faulty, not in right position | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-24 16:02:00 | Fail | Checked all lightning rods and confirmed they are now located in the correct positions.Job Complete
MSA-DFES | WA3385529 | Shed closest to the main building ground corner of shed and downpipe damaged | SESU Mundaring | GMP-BR | Building | External Walls (BU) | AWB Co. | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-08 10:45:00 | Fail | Found downpipe and corner flashing of shed badly damaged. Carried out measure up and will return Ordered material and picked up for install, install had beeen done already by other company.Followed up with WASC and was advised the works were completed by others off the back of DAS/RM and we were not made aware of this
MSA-DFES | WA3385603 | CL & D offices- Aircon too hot in most rooms.Two rooms very warm. | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-16 15:30:00 | Pass | Adjusted temps
MSA-DFES | WA3385711 | Possible fault with recirculating pump. | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-02 14:19:00 | Fail | Replaced Circulation Pump.
MSA-DFES | WA3385866 | FF Bathroom - shower screen door U/S, rollers on shower screen not working | CFRS Canning Vale | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-18 12:18:00 | Fail | Replaced shower screen with new
MSA-DTAG | WA3385132 | Lift 2 - the door closed slowly, doors started vibrating and there was a loud beep | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 13:00:00 | Pass | Repairs to lift
MSA-DTAG | WA3385143 | 1987 L2 Sheriffs Office Front door is jammed and is 6 inches open. It can’t open or close. | Supreme Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-07-23 15:31:00 | Fail | Found that the old door keeps coming off the tracks, refit door and adjusted anti rise, this has been an ongoing problem. Quotation required to upgrade the unit to an es200 locking unit with new carriage bars 800mm long, use existing sensors and switches. Braf raisedRemoved existing faulty door equipment and replaced with new es200 operator, carriage bar and safety sensor. Setup and tested operation upon completion and left in good working order.
MSA-DTAG | WA3385265 | Level 7, Kitchen - No cold water coming out of zip tap | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Drainage (PD) | Water2water Pty Ltd | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 15:40:00 | Pass | New unit installed, tested and commissioned. All INSTALLED MAXIFLOW SCALE SYSTEM A40190468L - WILSON BOIL/CHILL TAP WB90 R2789901 A40190467K AND IC8 UNDERSINK CHILLER 19090264 A40190469M REMOVED OLD UNIT TO TIP
MSA-DTAG | WA3385593 | Registry door stop in overhead track needs tightened | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 14:45:00 | Pass | SECURED DOOR STOP - OVERHEAD TRACK
MSA-DTAG | WA3385627 | ground - lift 3 out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 13:52:00 | Pass | Lift occasionally going into fault, issue with new skate installed. Further work required, unit left off will return tomorrow torectify
MSA-DTAG | WA3385638 | Level 1, female public toilets - blockage in the first cubicle | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 13:30:00 | Pass | Complete
MSA-DTAG | WA3385957 | Level 1, Mens toilet - Toilet full flush sticky | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-18 14:50:00 | Pass | Went throw pulled apart button and cisterns cleaning and reinstalled
MSA-DTAG | WA3385964 | secure and public area difficult with doors- see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 18:51:44 | 2020-06-16 15:30:00 | Pass | Job completed - Unable to access RM101. Checked Door Controller and Controller. Downloaded, programmed and checked, all OK
MSA-DTAG | WA3386003 | Lvl 4- Hot water system tap will not turn off and is pouring out boiling water | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 10:30:00 | Pass | Fault is with tea boiler under service contract with Water2water. Ian Johnston notified.
MSA-DTAG | WA3386015 | Level 1 Special Clean in Court 1 – Customer urinated on a chair in the public gallery | Midland Courthouse | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | OCS SERVICES PTY LTD | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-17 21:00:00 | Fail | Bio-Clean in court 1
MSA-DTWD | WA3385082 | L3 south block roof worn belts | Perth Campus B1 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 09:28:00 | Pass | Returned to site completed required paperwork gained access to fan and locked out isolators. Fit new drive belts tensions and checks alignment. Greased fan bearings and monitored operation. All ok air flow has been restored. Work area left tidy. Old belts disposed of.
MSA-DTWD | WA3385085 | A Block, ground, A057 female toilets - door handle faulty | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-16 11:54:00 | Pass | Job completed - replaced internal handle on A057 toilet lock
MSA-DTWD | WA3385098 | A block, Ground level, AF18, AF20 - entry keypads not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-17 07:38:00 | Pass | 16/06/2020, 1300-1330Found terminal block corroded and also copper strands on the cable corroded.Stripped cabled and re terminated with new terminal block.Tested all Rosslare keypads and locks all ok
MSA-DTWD | WA3385142 | A Blockm Ground level A021 - replace/repair damaged DGPO | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 08:00:00 | Pass | Tighten screws of loose power points around the room and replaced damaged outlets
MSA-DTWD | WA3385144 | A Block, level 2, A230 - replace/repair damaged DGPO on EAST WALL | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 09:00:00 | Pass | Gpo did not need replacing, the screws were loose which have now been tighten as well as the other gpos in the room
MSA-DTWD | WA3385208 | D Block, Room D16- 29x fluro lights are not working - EWP is needed | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-31 08:30:00 | Fail | Arrived at site, set up work area, filled gaps with gap filler Job Complete
MSA-DTWD | WA3385350 | E block hospitality stores room E58- Sink tap broken | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-16 14:30:00 | Pass | COMPLETED
MSA-DTWD | WA3385459 | West block, Level 1, Room W112 - Repair classroom door lock, unable to secure classroom | Mount Lawley Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 11:30:00 | Pass | Arrived at site, inspected faulty door. Required a new face plate. Tried modifying a spare one I had. Did not work. Picked up new materials and returned to site. Fixed new plate. Tidy area.
MSA-DTWD | WA3385551 | C block east side external roof Barge capping dislodged, another coming loose-see notes | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-07-24 11:00:00 | Fail | Reattached edge flashing to the side of the roof. Scaffold required to provide safe access
MSA-DTWD | WA3385602 | D Block Nth. Entry doors, machining workshop - Double wooden doors jamming when trying to open | Rockingham Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-17 13:45:00 | Pass | New doors required. BRAF declined and not going ahead. Charging for attendance to inspect/ measure doors
MSA-DTWD | WA3385705 | Lvl 2, Gallery- Motorised blinds not working | Perth Campus B5 | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-09-14 14:06:00 | Fail | Completed - Did not go ahead with quote
MSA-DTWD | WA3385804 | Black boundary fence is broken and needs the wire repaired (Corner Jennalup Drive & Fiona Wood Road | Murdoch Campus | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 16 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-17 14:15:00 | Fail | Replaced missing fencing rails and damaged fence mesh
MSA-DTWD | WA3385871 | Level 1, server room - alarm on chiller | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 16:19:00 | Pass | Recheck equipment operation and confirmed room maintaing set point. All ok.
MSA-DTWD | WA3385984 | Male toilets - G block, men's toilets first and last blocked. | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-16 16:20:00 | Pass | Unblocked toilets
MSA-DTWD | WA3386004 | Bad odour in roof space above the auto door at the entrance to Block 8 – possible dead rodent | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-17 09:45:00 | Pass | Carried out a treatment for bad smell coming from hallway in block 8. Upon inspection no access too roof space, rebaited existing station too storeroom and added an additional station . Installed deodoriser bag too affected area.
MSA-DTWD | WA3386007 | Block 4, Room 4G4- Faulty power outlets – possible cable damage | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-23 09:00:00 | Fail | Attended site on 22/06/20 Replaced all damaged cabling Returned on 23/06/20 to replaced outlets and tested all now working
MSA-DTWD | WA3386008 | U block, work shop - There are many other leaks behind the beam saw and installation area | Balga Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 16 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 12:00:00 | Pass | U Block11 multiple leaks sealed around sump, structural support protruding through roof the other leaks are from evap flexible joints - Site made aware mechanical required.
MSA-DTWD | WA3400043 | Retrospective workorder donot attend-external door G Block could not secure | Mandurah Campus (formerly Peel) | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 0 | CLOSE | 16 Jun 2020 | 2020-06-16 20:00:00 | 2020-06-16 19:45:00 | Pass | .
MSA-MRWA | WA3385212 | L8 north hallway Water cooler not cooling, please inspect/remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-17 11:35:00 | Pass | Assessed unit to refrigeration not working. Recommend replacement. A402020265 FRIGMAC RECESSED FOUNTAIN QUOTING TO REPLACE
MSA-MRWA | WA3385575 | basement UPS room have a persistant alarm code | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-18 14:00:00 | Fail | Battery alarm reset on UPS
MSA-MRWA | WA3385911 | Level 6, Mens Toilet LHS cubicle - Toilet Blocked, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 16 Jun 2020 | 2020-06-17 17:00:00 | 2020-06-16 17:15:00 | Pass | Unblocked toilet and replace broken rubber. I noticed that the toilet pan has a small crack inside(see phoyo attached)
MSA-DCA | WA3400463 | Lift had a power surge lift not working at all | Collection and Research Centre Welshpool-Harry Butler Centre | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 17 Jun 2020 | 2020-06-17 18:04:53 | 2020-06-17 16:00:00 | Pass | Not chargeable
MSA-DCS | WA3399857 | monitor room sent zone 7 and 8 not alarming on test | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Jun 2020 | 2020-06-17 11:13:11 | 2020-06-17 12:45:00 | Fail | Replaced faulty 6000 controller with new, job completed.
MSA-DCS | WA3400010 | Internal zone, gatehouse -B, IP2IRBRX anticlimb alarm | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 09:18:58 | 2020-06-17 15:41:00 | Pass | Rectified and fixed the faulty IRB RX anti climb , job completed.
MSA-DCS | WA3400076 | Roof sheeting is lifting near control room | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-10-05 09:00:00 | Fail | ROOF REPAIRS CARRIED OUT IN RECEPTION
MSA-DCS | WA3400077 | L2 computor room all security has gone down | East Perth | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Jun 2020 | 2020-06-17 14:02:46 | 2020-06-17 10:30:00 | Pass | Phone supported client to boot up pc and walked though passwords
MSA-DCS | WA3400097 | Unit 1 - D Wing Cell D05 window has been broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 10:10:58 | 2020-06-18 12:30:00 | Fail | SASHES REPLACED & FRAMEWORK REPAIRED
MSA-DCS | WA3400100 | Unit 1, Cell A04 - toilet continues to flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 08:00:00 | Pass | Replaced faulty leaking inlet valve in cistern.
MSA-DCS | WA3400107 | Unit 1, D Wing, Cell D05- Sink has been smashed | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-24 11:00:00 | Fail | Removed damaged basin from wall. Installed new basin and connected pipework. Tested and cleaned rubbish from cell.
MSA-DCS | WA3400111 | Gym, No TV signal in training room | Casuarina Prison | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 09:15:00 | Pass | Attended site. Ran cable for Gym TV. Installed 2 way splitter for TV leading to new antenna. Tested TV signals
MSA-DCS | WA3400121 | Prosecution office- lock on door is faulty | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 10:19:39 | 2020-06-17 14:15:00 | Pass | Rekey lock on Prosecutions office GMK & SECURITY only (keys)
MSA-DCS | WA3400139 | Control room -freeze frame not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 22:42:00 | Fail | Replaced keyboard from seme stock
MSA-DCS | WA3400140 | Family visits- Camera Monitor 18 not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 10:30:00 | Pass | WA3400140Removed and replaced faulty monitor. Tested ok. Parts used:19 inch monitor from SEME stock
MSA-DCS | WA3400186 | Unit 4, Wings A & G - No hot water | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-02 14:00:00 | Fail | Remove faulty tempering valves and install new TMV as per DAS.
MSA-DCS | WA3400191 | Unit 2 - Pipe burst behind unit 2 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 10:59:28 | 2020-06-17 15:00:00 | Pass | Investigated burst pipe. Isolated water. Dug up and exposed pipe. Repaired damaged pipe. Tested. Denzo wrapped. Backfilled hole.2 x 50 mm slip couplings1 x m of 50mm copper1 x roll denzo
MSA-DCS | WA3400238 | Industries prisoners toilet pan loose | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-23 10:30:00 | Pass | Re set loose pan in industries prisoners toilet block.
MSA-DCS | WA3400257 | PROGRAM ROOM 8 A/C not heating | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 15:00:00 | Pass | Ran up unit in heating and cooling modes, monitored. Unit producing correct temperatures, all ok.
MSA-DCS | WA3400260 | Control Room- lighting switchboard is faulty | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-20 12:00:00 | Fail | Removed temporary power supply and failed power supply. Install replacement RFI 24/05 power supply.
MSA-DCS | WA3400268 | Multiple system failure throughout the prison | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Jun 2020 | 2020-06-17 15:37:06 | 2020-06-18 12:33:00 | Fail | Investigated multiple communication faults onsite, traced fault to data link between SHU and CCU. Repaired faults and tested OK. Job Complete
MSA-DCS | WA3400290 | Unit 14, B & D Wing- Cell B16- bottom bunk light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 09:00:00 | Pass | Repaired faulty lights in unit 14 b16
MSA-DCS | WA3400291 | Unit 5, C Wing, Cell C6- Toilet water running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-01 11:00:00 | Fail | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3400299 | unit 5 house 1 range hood not working and loung gpo not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-15 18:00:00 | Fail | Replaced power outlet
MSA-DCS | WA3400308 | Rodent issue in PFM Stores beside Drug Detection Unit | Hakea Prison | GMP-BR- HO | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 11:30:00 | Pass | Carried out rodent baiting within the PFM stores next to the DDU unit. Installed 4x beta stations around the internal perimeter, will check the activity in 2 weeks time
MSA-DCS | WA3400322 | Boilerhouse, Boiler number 2 - boiler not firing up | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 12:09:29 | 2020-06-18 12:54:00 | Fail | Went to site signed in a did tool check. Went to boiler house reset boiler and it started and I could not get it to fail I ran itup to temp and kept failing it and it started each time power was off so could not see were it failed on the LFL.
MSA-DCS | WA3400365 | HR demountable - 7x fluro lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-15 11:30:00 | Fail | Replaced 7x led battens
MSA-DCS | WA3400366 | Maintenance workshop- lights are faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-30 14:30:00 | Fail | Replaced tubes and starters throughout workshop area
MSA-DCS | WA3400369 | repair damaged retic by Midolo vehicle | Wandoo Rehabilitation Facility | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | WESTERN IRRIGATION PTY LTD | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-23 09:00:00 | Pass | Located and repaired broken irrigation pipe, replace faulty solenoid coil and wiring
MSA-DCS | WA3400391 | Office compactus needs securing if pushed may fall over | East Perth | WSM-BR-SITE | Building | Internal Walls (BU) | Schlager Construction Group | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-08 13:30:00 | Fail | Attended site and carried out repairs to the unsecured compacts.
MSA-DCS | WA3400422 | kitchen potato power socket failure | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 10:30:00 | Pass | Replaced 3nphase socket outlet
MSA-DCS | WA3400424 | kitchen floor scrubber faulty | Wooroloo Prison Farm | WSM-GR-SITE | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 11:30:00 | Pass | Tested floor scrubber, not an electrical issue
MSA-DCS | WA3400428 | kitchen potato machine not working | Wooroloo Prison Farm | WSM-GR-SITE | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-25 10:00:00 | Fail | Kitchen no.2 Peeler faulty. Check peeler, tripping power. Motor seized. Dismantle, remove for repairs. Remove motor, fit new bearings, wiring. Assemble 7 test. Return to site, install on base. Fit water lines & drains.
MSA-DCS | WA3400496 | various levels faults with lights see notes- | East Perth | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-19 11:00:00 | Pass | Replace Tubes as required and inspected damaged light switches.
MSA-DCS | WA3400499 | Hallway at rear of Admin building Lights all gone out due to rain | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 14:36:53 | 2020-06-18 08:00:00 | Pass | Lights not working
MSA-DCS | WA3400501 | Bakery freezer doorframe damaged | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-09-01 14:00:00 | Fail | Repairs complete
MSA-DCS | WA3400533 | ERU Hut above gym roof leak, caused ceiling panel to fall | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-11-23 09:00:00 | Fail | REPAIRS TO ROOF COMPLETED
MSA-DCS | WA3400550 | POD - Transponder 5 gymnasium office, comms failure | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 15:15:19 | 2020-07-29 12:00:00 | Fail | Replaced Moxa at Transponder 5 Gymnasium Transponder 5 drops out Transponder 3 when brought online and vice versa. Reconfiguration of Gymnasium Moxa required
MSA-DFES | WA3400122 | admin/rec ground Door latch not retracting and strike plate surround missing | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 17:00:00 | Pass | Replaced door strike plate. Latch now working
MSA-DFES | WA3400398 | ground trainig office Light pole outside training office leaning over footing loose-see notes | FESA RHQ - Forrestfield | GMP-BR | Building | Columns (BU) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-17 12:30:00 | Fail | Complete
MSA-DFES | WA3400537 | Workshop/Stores - Roof leaks | Fleet Management Services - O'Connor Workshop | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-19 11:00:00 | Fail | Have cleared rain head and carried out minor repairs, no reports of futther leaks- job completed
MSA-DFES | WA3400648 | HWS has either ruptured or pipe has burst | CFRS Joondalup-Main Building | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 0 | CLOSE | 17 Jun 2020 | 2020-06-17 22:14:38 | 2020-06-18 09:45:00 | Fail | Repair burst
MSA-DTAG | WA3400085 | 1903, Basement - Vault 7 (back room)- Blown light tubes | Supreme Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-19 08:30:00 | Pass | Replaced 36watt fluoro’s in the back room of vault 7.
MSA-DTAG | WA3400129 | Lvl 15, Plant Room- Barrel bolt securing the double doors leading to plant room is loose | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-18 09:15:00 | Pass | BARREL BOLT RE SECURED
MSA-DTAG | WA3400279 | 1987 Level 1 Fire Panel general device fault, SIP Alarm Building 87 | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 13:30:00 | Pass | Attended site checked MFIP, found zone 19 building 87 SFIP in conventional fault. Checked SFIP, found zone 17&15 isolated on SFIP which is plantroom area and no information tags on panel or logs who did isolation.Liaised with Iain Johnston and he didn’t have any contractors working in area and advised me to de-isolate zones and leave normal.
MSA-DTAG | WA3400504 | 1903 disable toilet ground Pipe leaking between cisten and bowl-see notes | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 08:12:00 | Pass | Reinstalled flush pipe and washer
MSA-DTAG | WA3400519 | L10 Registry of Births, Deaths and Marriages front counter CCTV issues - see notes | Westralia Square | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 11:00:00 | Pass | As per Slip rewiring and reprogrammed CCTV spot monitors. Tested ok
MSA-DTWD | WA3400091 | Upper walkway North- Smoke detector faulty. L2, S34, Z9 | Clarkson Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-17 10:50:00 | Pass | L2, S34, Z9 in fault, changed over, recommend changing all smoke detectors in tiling area to thermal.
MSA-DTWD | WA3400266 | G block ground tool store Drink fountain repair. Lever-see notes | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 13:30:00 | Pass | Replaced rpz
MSA-DTWD | WA3400269 | South Block, S 106 student services - Air Con not working | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 09:00:00 | Pass | Accessed unit. Test ran and found time clock , set back , and schedule settings not as desired. Reprogrammed and tested ok Unit heating to set temp.
MSA-DTWD | WA3400276 | B block- Damaged internal door entry area between door frame and nib & repaint | Joondalup Kendrew Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 17 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-01 10:00:00 | Fail | Toby Bindon (18/06/2020) - Work NoteArrived at site inspected door frame. Requires patching. Picked up materials and returned to site. Filled gaps and applied first coat of fill.**requires x2 more return visits of 2hrs. For sand and second coat of fill and final sand/paint***Toby Bindon (29/06/2020) - Work NoteArrived at site, set up work area. Laid drop sheets, taped the door frame and sanded the walls back. Filled each side of the door for a second coat. Toby Bindon (01/07/2020) - Work NoteArrived at site, set up work area. Laid drop sheets, taped the door frame and sanded walls back. Applied final fill and paint.
MSA-DTWD | WA3400304 | Block 6, 6G polishing block - EWIS speaker wire broken | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-24 15:30:00 | Fail | Investigated catinery wire. Replace with new wire and reconnected cable. Tested all ok. Job complete.
MSA-DTWD | WA3400372 | G Block, Room G28- Roof Leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 10:45:00 | Pass | After gutter inspection site haver advised leak is resolved, not going ahead with BRAF. Job complete
MSA-DTWD | WA3400487 | Welding workshop - northern welding bay exhaust is not working | Naval Base | GMP-BR | Equipment | Electrical Equipment (EQ) | Equans Mechanical Services Australia | 1 | CLOSE | 17 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 12:00:00 | Pass | Travelled to site signed in. Located Welding Extraction fan and found unit not running. Accessed warehouse roof and located the exhaust fan. Found that belts had snapped and wrapped around the motor shaft causing it to jam up. Removed belt cowling and pulley and cut the belts off. Checked to see if the motor and fan pulley was seized. Installed new belts and test ran unit. All ok.
MSA-DTWD | WA3400539 | U Block, U022.1 machine room- Roof Leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-06 10:15:00 | Fail | U22.1 Require redundant duct work removing and box cap fitting. Also vent system flashing to rear of vent needs attentionRemoved disused ducting and installed capping to penetration sealed gaps
MSA-DTWD | WA3400559 | D Block, Room D05- Ceiling leaking in female toilets | Midland Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-02 14:00:00 | Fail | Could not access roof as plant room door faulty. Will return when can get access Returned to investigate leak. Found issue with water running from windows onto roof below which is not water tight. Measured up to waterproof area using tin and battens. Measured to replace rusted out downpipe to area(BRAF DECLINED)
MSA-DTWD | WA3400563 | F Block - Blocked toilet in Male toilets. | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 16:15:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3400574 | E Block, Room E200 - Louver panel has come loose on the southern end skylight in E200 passage. | Midland Campus | GMP-BR | Roofing | Rooflights and Skylights (RF) | AWB Co. | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 14:00:00 | Pass | Replaced broken pop rivets from lowered shade system as structure had fallen apart. refixed lock in plates.
MSA-DTWD | WA3400583 | L2 west sliding door - key lock broken | Perth Campus B1 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 13:55:00 | Pass | 18/6/20 - Requires replacement besam unislide plastic 5 position switch. Pictures attached.18/6/20 - Returned to site, Replaced the broken mode switch and checked all modes and are all working properly as normal.Have noticed shear point ( door is going pass the mullion edge and potential shear point) and requires safety device..
MSA-DTWD | WA3400588 | D Block, Meat Training Room - Hot water tap is leaking in sink | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 11:00:00 | Pass | Re fix hot water supply to soap dispenser
MSA-DTWD | WA3400589 | E Block, Plant Room- Hot water tank is leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-13 16:15:00 | Fail | Replace hot water tank and fittings
MSA-MRWA | WA3400497 | Mens Change Room - Hot water taps at vanity units running cold/warm, please inspect and remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-18 12:33:00 | Pass | Replaced and tested 2x faulty tmv’s
MSA-DCA | WA3400820 | Boilers not working in HBC-see notes | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Plant Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 18 Jun 2020 | 2020-06-18 11:54:50 | 2020-06-18 10:00:00 | Pass | Attended site 18-6-20 0800. HBC boiler to not be operational and various VSDs in fault due to excessive weather & power disturbance. Reset all controls and applicable VSDs, reset BMS control system, reset boiler and tested system operation. Checked all site applicable intrinsically safe RH and temp sensors (ok). Monitored boiler on off cycle and operation. System operating correctly. Left site 18-6-20 1000.
MSA-DCA | WA3401109 | External wall in Lane way - Section of gutter downpipe has come away from roof gutter. | Old Customs House-Main Building-External Area | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-09 10:30:00 | Fail | Repaired dislodged down pipe - and sealed around rainhead
MSA-DCA | WA3412043 | Gate supports to carpark have been tampered with and have broken/come loose. Need to be re-welded | Shipwreck Galleries-Main Building-Carpark | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 10:44:00 | Pass | Drilled and tapped new fixings to hold closed position receiver. Tested ok.
MSA-DCS | WA3400669 | Duress system going into alarm, multiple alarms that cannot clear them | Bunbury Regional Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Jun 2020 | 2020-06-18 11:41:21 | 2020-06-18 16:30:00 | Fail | Replaced damaged and faulty receivers. Rectified and fixed tamper fault on receiver. Job completed.
MSA-DCS | WA3400710 | Cowling alarm wont reset since yesterday | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Jun 2020 | 2020-06-18 10:16:29 | 2020-06-18 12:58:00 | Fail | Arrived onsite to find no alarms.Officers indicated zone 2 cowling and zone 13 fence. Checked zones and adjusted and calibrated Monitored for false alarms.All zones stable
MSA-DCS | WA3400738 | Light pole 29, 30, 31, 39 and 40 are not ramping up | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 06:35:30 | 2020-07-27 14:00:00 | Fail | Repaired light poles
MSA-DCS | WA3400776 | unit 1 dayroom 2 x lights not working in front of office | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 10:30:00 | Pass | Investigate and repair Unit 1 dayroom lights
MSA-DCS | WA3400791 | Jeelia C wing roof leak between aircon duct and light | Wandoo Rehabilitation Facility | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-22 11:56:00 | Fail | NO LEAK/DAMAGE EVIDENT - WATER BLOWING IN UNDER FLASHINGS
MSA-DCS | WA3400834 | Unit 4, C4 - Glass not secure in window frame, galss has slipped down from frame | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-18 15:00:00 | Pass | SASH & FRAMEWORK REPAIRED
MSA-DCS | WA3400842 | Unit 14, Cell C09 - sink leaking wateronto floor, requires attention | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-25 16:00:00 | Pass | Replaced hot and cold spindle in basin tap set.
MSA-DCS | WA3400845 | Unit 4, B6 - Water is constantly leaking in toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 12:00:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3400847 | SOG base Toilet FOB no longer working | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-18 12:30:00 | Pass | Job completed - Attended site. Reconfigured Toilet Door Fob 24/7 Building Access to access Zone.
MSA-DCS | WA3400850 | Unit 14, day room - regi oven in B&D day room is making a really loud buzzing noise | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-19 10:10:00 | Pass | Replaced contactor, test ok
MSA-DCS | WA3400855 | SOG base Gutter leaking above the dryers at SOG base | Hakea Prison | GMP-BR- HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-12-10 14:15:00 | Fail | gutters repaired to rectify leaking
MSA-DCS | WA3400879 | unit 4, B11 - Window will not stay up when open, constantly slamming shut | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-22 15:00:00 | Pass | RENEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3400880 | Unit 6, D wing - Vent to cell D2 requires attendtion, does not operate | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-08-06 10:30:00 | Fail | REFIT - RECONDITIONED LOUVER VENT TO WINDOW
MSA-DCS | WA3400964 | Administration area, admin kitchenette - water pipes are humming (for the last 3 days) | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-18 10:54:00 | Pass | Inspected noise located problem and fixed humming noise
MSA-DCS | WA3401041 | Gatehouse - zone 10, camera not working | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 09:30:26 | 2020-06-18 12:59:00 | Pass | Power outages overnight,Cameras in zone 10 and 2 offline.Reset cameras and encoders, cameras back online but zone 10 camera 1 has poor Image, over exposedAdjusted white balance, image now clear
MSA-DCS | WA3401077 | Unit 3, B wing showers - Showers blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-19 10:15:00 | Pass | Drain machine used to clear blockages in showersremove large clump off hair
MSA-DCS | WA3401078 | zone 7 external camera - giving an internal view | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 10:06:02 | 2020-06-23 11:14:00 | Fail | Site reported multiple cameras out of alignment. Investigated fault, found multiple cameras have gone out of alignment after cleaners cleaned windows in OBS towers.Realigned multiple cameras as per control room officers.Tested OK.Job Complete
MSA-DCS | WA3401102 | Demountable room 6 & 7- Internal door handles not working properly, possibly faulty mechanism inside | Nyandi Training Academy | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-07 14:30:00 | Fail | job completed - and install replacement lever handle sets as required.Unit
MSA-DCS | WA3401127 | Unit 10, Cell B9- Power point keeps tripping | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-19 10:30:00 | Pass | Tripping power
MSA-DCS | WA3401131 | Unit 4, Cell H29- roof leak water coming through light fitting | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 10:43:13 | 2020-06-18 14:45:00 | Pass | ROOF REPAIRED
MSA-DCS | WA3401134 | Kitchen lights outside rear double doors faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-19 12:30:00 | Pass | Investigate and repair rear kitchen lights
MSA-DCS | WA3401618 | Unit 14 polisher is just not working when turned on | Casuarina Prison | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 10:30:00 | Pass | Repaired 2x faulty floor polishers in cleaning workshop for unit 14 and 4
MSA-DCS | WA3401647 | Unit 4, Cell D9- Toilet is leaking after tank fills up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 13:00:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3401679 | Unit 14, Cell A6- Basin tap is faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-26 08:00:00 | Fail | Replaced leaking basin spindle.
MSA-DCS | WA3401693 | Video links - secuirity camera not working to monitor | Bandyup Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 11:20:17 | 2020-06-18 13:57:00 | Pass | Power not connected.Re-terminated and plugged inSystem online
MSA-DCS | WA3401724 | Unit 4, B & D Showers, not working correctly, water is trickling out | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 12:00:00 | Pass | Cleaned and from tmv’s and from shower heads.
MSA-DCS | WA3402060 | Recreation Area- Lock on Fire Emergency Door requires refixing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-31 22:30:00 | Fail | Temp. repair require parts.Replace top and bottom locking bolts keyed to GMK.
MSA-DCS | WA3402131 | Unit 6- SO office grill ,lock jammed . | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-18 13:30:00 | Pass | opened jammed lock, service and repair.
MSA-DCS | WA3402381 | Unit 10, Cell C6- Bed light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-19 10:30:00 | Pass | Repaired bed light
MSA-DCS | WA3402894 | Boilerhouse - Leak from roof above front door | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-09-15 15:00:00 | Fail | SOURCE OF LEAKS LOCATED & REPAIRED
MSA-DCS | WA3404267 | Leaking filter at Program Room 2 B-Wing | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-18 14:20:00 | Pass | Removed ap11 due to leak. Replaced with new capex asset maxiflow scale system tested.
MSA-DCS | WA3404619 | Perimeter camera 11 is down and not connecting to server | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Jun 2020 | 2020-06-18 16:54:41 | 2020-06-19 16:26:00 | Fail | Investigated fault, traced to cabling fault, traced cable and repaired fault.Tested OKJob Complete
MSA-DCS | WA3406163 | Skills development, Store room - Rheem 50 Ltr HWS trips electrical power | Boronia Pre-release-AS20 - Industries Vocational Skills Development-Ground Floor-Store Room | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-22 09:00:00 | Pass | Investigate and repair skills development hot water system
MSA-DCS | WA3407143 | Unit 1 Cell C2 - key snapped off in the lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 18 Jun 2020 | 2020-06-18 18:10:28 | 2020-06-18 16:00:00 | Pass | Replaced personnel lock cylinder
MSA-DCS | WA3408580 | Perimeter main prison B1 - pole light pole 5 - TR4B9TP1 (33) damaged housing (M-DAS) | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-19 11:30:00 | Pass | Replaced MDAS damaged receiver and housing,job completed.
MSA-DFES | WA3401088 | Front entry gate not closing correctly on the timer | CFRS Maddington | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-14 13:00:00 | Fail | Technician attended the site of Maddington Fire Station entry gate W21772 on 18/06/2020. Following full test and inspection of door components identified fault was the motor was disengaged.Re-engaged and gate seemed to be working as should. Checked timeclock and tested all keypads and could not find an issue.19/06/2020. Found gate working fine, station reports fault is intermittent. Checked all connections and PE beams . Unable to pin point fault. Recommend new logic for Icaro gate motor.14/07/2020. Fitted new limit switch assembly. Re programed keypads on site and remotes. Replaced 1 faulty remote. Replaced battery to pe unit. Re programmed logic and tested gate operations all ok.Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3401122 | Ladies toilet - door closer & vent in door is loose, both need repair | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 09:36:00 | Pass | Have attended site and carried out repairs, have replaced door closer. New door closer body is smaller than the old unit. Door painted. Job complete.
MSA-DFES | WA3401126 | O’Connor Works, upstaris Conference Room - Patch & repair wall after removal of smart board | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-29 00:30:00 | Fail | Attended site to assess works required. Will need to return with to patch and paint. Sample taken to match colour. Works Complete
MSA-DFES | WA3405076 | engine room 1 - investigate defective electrical cabling that runs from the Light Tanker battery | CFRS Fremantle | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-16 15:45:00 | Fail | Complete
MSA-DFES | WA3410594 | front side of station gate has blown off the hinges and brick work broken | CFRS Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-07-30 11:30:00 | Fail | Technician attended the site of Belmont SES Regional Office to the Gate No. 1 on 30/07/2020. Attended site and installed new heavy duty gate support / roller assembly, mounted into position, tested operation several times and tested all ok. Full test and inspection of door function completed prior to leaving site.
MSA-DTAG | WA3400936 | Court 3, waiting room - hole in floor underneath carpet | Rockingham Justice Complex | GMP-BR-HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 14:30:00 | Pass | HOLE FILLED - CARPET RE GLUED
MSA-DTAG | WA3401017 | 6x Lights are not working- locations listed below | Perth Children's Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 08:30:00 | Pass | Job complete
MSA-DTAG | WA3401052 | Workstation tubular support leg in Custody security office is loose | Joondalup Courthouse | GMP-BR-HO | Furniture | Office Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-25 08:00:00 | Pass | LEG REMOVED AS IMPINGES ON LEG ROOM OF PERSON AT DESK
MSA-DTAG | WA3401852 | Lift 3 os performing erratically | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 15:27:00 | Pass | When responding to the callback dated 18.06.2020, the Schindler Technician found a problem with your equipment. Some componentsof the car door operator were worn out. Following our attendance, the equipment was left in service.
MSA-DTAG | WA3402268 | Level 1, Sheriff's office - Airconditioning is very cold. Aircon is excessively cold in certain area | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-30 16:00:00 | Fail | Controls upgrade for AC 1 and 3 due to old control failure.
MSA-DTAG | WA3409117 | Level 1, Custody - Special Clean - Custody side of interview room 2 and cell 2 due to a person in | Midland Courthouse | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 15:28:00 | Pass | Special Clean Interview Room 2
MSA-DTAG | WA3410299 | Door is not operating correctly when swipe card is swipe, possible swipe card issue | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 11:00:00 | Pass | Attended site. Level 29 West. Found no power on Auto Door, ran an extension lead, still no power. Found issue is withPower Supply. Advised an Auto Door Contractor will need to attend urgently.Job completed.
MSA-DTAG | WA3411451 | Custody - Intercom on the bail exit door is non-operational. Intercom is button stuck on | Midland Courthouse | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 14:19:00 | Pass | Attended site, checked intercom, button working correctly and not sticking, reset cell guard system and reprogrammed time. Tested cell call multiple times and confirmed correct operation
MSA-DTWD | WA3400783 | B40 Auto sliding door will not operate | Murdoch Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-18 17:00:00 | 2020-06-18 09:40:00 | Pass | 1045219 HD200. Necked and found no power to GPO, checked electrical switchboard and all correct. Found the emergency switch had been activated, reset and tested all ok.
MSA-DTWD | WA3400803 | Ground C022 Fire door safety glass requires re sealing due to glass being loose | Clarkson Campus | GMP-BR | Building | Doors (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 18 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-20 07:56:00 | Fail | Could not find door no location said in notes. Need more info****WORKS CLOSED OFF AS REQUESTED BY BARRY FIRTH *****ATTENDED SITEGLAZIER COULD NOT FIND DOOR IN QUESTION.ALSO BARRY FIRTH WAS UNAWARE OF WORKS.ATTENDANCE AND LABOUR CHARGE ONLY
MSA-DTWD | WA3400883 | A block faulty alarm in zone 42 | Mandurah Campus (formerly Peel) | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 11:45:00 | Pass | 19/06/2020, 1115-1145Cleaned sensor of dust and spider webs
MSA-DTWD | WA3400888 | Building 12, Ground level, 12G3 - Door lock faulty | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 12:25:00 | Pass | Block 12 - door lock damaged 12G3.Lock repaired.
MSA-DTWD | WA3400929 | between A and T block under cover area leak | Munster Campus (ACEPT) | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 08:00:00 | Pass | Cleaned leaf litter out of gutter and un-blocked down pipe.
MSA-DTWD | WA3400937 | U block ceiling/roof Water leaks (multiple points) | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-06 12:15:00 | Fail | Investigated area below suspended roof leak - unable to access roof due to weather and will need to return when not raining.Show leaks to U block and sealed penetrations from evap unit and structure - dwp issue resolved, other leaks from evap flexi joints are waiting on mechanical to fix.
MSA-DTWD | WA3400947 | A Block, G,1st and 2nd floors, female toilets East and West, replace/repair broken toilet seats | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-19 09:45:00 | Pass | COMPLETED
MSA-DTWD | WA3400975 | Block 10, Ladies Toilet- Faulty light tripping RCD R9 | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-19 14:45:00 | Pass | Attended site and replaced faulty light fittings. Checked and tested all now working.
MSA-DTWD | WA3401005 | Level 2, office disability - CBUS broken | Perth Campus B2 | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-24 08:15:00 | Fail | Complete
MSA-DTWD | WA3401048 | Ground level, walkways - ball lights not working | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-22 15:18:00 | Fail | Inspect walkway pole ball lights not working. Repairs made. Various replacements needed. Order made as stock unavailable in PerthReplacement globes installedRemoved existing drivers which are not stocked Replacement globe holders S&I
MSA-DTWD | WA3401107 | A Block, A356(general office area)- Window Cracked | Leederville Campus | GMP-BR | Glazing | Window Glass (GL) | O'Brien Glass With Care | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-07 13:30:00 | Fail | repairs to window
MSA-DTWD | WA3401352 | Roof leak - G Block, IT section - roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-22 10:00:00 | Pass | Sealed suspected source of leak - site confirmed leak has been resolved
MSA-DTWD | WA3401957 | Admin, Walkway- Fire Panel showing fault again, please check all detectors | Clarkson Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 13:00:00 | Pass | Short circuit on L1, most likely from water damage. Inspected detection around site. performed loop test, fault cleared for now.
MSA-DTWD | WA3402493 | U Block, Room U022- Tap leaking in trough (may need new spindles) | Balga Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-22 15:00:00 | Pass | Replaced leaking taps
MSA-DTWD | WA3402557 | U Block, Room U023, Ceiling (high workshop) - High bay lights going on and off | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-25 13:00:00 | Pass | Replaced 2x faulty highbay lamps in U023. All working now. Job complete.
MSA-DTWD | WA3404498 | Chiller room - repair leaking roof | Mandurah Campus (formerly Peel) | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-08-20 11:00:00 | Fail | Attended site and assessed roof leak from below. Will need to return with EWP in dry weather to complete leak assessment from the roof.Leak resolved and ceiling patched. Will need to return to patch paint ceiling to complete 20/8/20
MSA-DTWD | WA3404875 | E Block, Deli - Burst hot water line to a wash basin sink | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 18 Jun 2020 | 2020-06-18 17:05:49 | 2020-06-18 14:30:00 | Pass | COMPLETED
MSA-DTWD | WA3405481 | D block, Ground floor, D19 - 3 chamber Hengel retarder prover is not working | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-01 16:00:00 | Fail | COMPLETED 1/7/20
MSA-DTWD | WA3406012 | C Block, Room C107- Fluros not working (suspect ballasts) | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-29 11:00:00 | Fail | Replaced faulty electronic ballast to c107, plus lights to variou location as requested by site. Job complete
MSA-DTWD | WA3406117 | A Block, 1st Floor, Server rack doors opposite AF2.04- Door locks stuck/faulty | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Locksmith (SE) | GRONBEK SECURITY | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 14:05:00 | Pass | Replace faulty 201 cylinder.
MSA-DTWD | WA3406208 | C Block, Undercover walkway- Sticky keypad lock | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 11:30:00 | Pass | C Block - sticky keypad lock.Lock repaired.
MSA-DTWD | WA3406749 | Ground floor, E49 - water damage to carpets | Bentley Campus | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 18 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-07 09:48:00 | Fail | Damaged carpet replaced
MSA-DTWD | WA3408374 | B block - up stairs male toilet is blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-22 11:45:00 | Pass | Used small drain machine to clear blockage
MSA-DTWD | WA3408547 | K Block, Male toilet is blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-19 16:37:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3410840 | G Block, G118 - Water is leaking from the windows directly opposite door in G118 | Midland Campus | GMP-BR | Building | Windows (BU) | AWB Co. | 2 | CLOSE | 18 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-28 09:45:00 | Fail | Works completed as per BRAF
MSA-MRWA | WA3408233 | Rear exit gate not working | Traffic Operations Centre | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 15:43:00 | Pass | Inspected exit gate and found it switched off at isolated switched on and tested all ok at time of test. Due to age of gate motor and sensors recommend upgrade to a d10 and face beams. Braf raised and waiting on approvalBraf declined
MSA-MRWA | WA3408512 | Bridge compound gate is not opening | Materials Engineering Branch | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 18 Jun 2020 | 2020-06-19 17:00:00 | 2020-06-18 16:22:00 | Pass | Found same fault as previous visit over a year ago. Very old gate controller not responding to input. After power reset, gate now operational. Requires faac e145 controller and model e enclosure. Braf raised and waiting on approvalBraf has not been approved so call out has been invoiced
MSA-DCS | WA3413293 | reception video link Camera for video link not in focus | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 19 Jun 2020 | 2020-06-20 07:33:44 | 2020-06-19 08:30:00 | Pass | Attended site no work performed as not part of security system
MSA-DCS | WA3413295 | Visits 3 camera The monitor has horizonal wavy lines through the picture | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Jun 2020 | 2020-06-20 07:39:39 | 2020-08-19 13:00:00 | Fail | Faulty camera 3 replaced with camera 2 so there are two working PTZs in the internal visits room. Further work to be quoted and completed under a different job number.
MSA-DCS | WA3413297 | Assist alarm Roebourne workcamp duress. RAS fail and fuse fail. | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Jun 2020 | 2020-06-20 07:44:10 | 2020-09-03 18:00:00 | Fail | Job complete 10m 4core beldon cable used from Seme off-site store
MSA-DCS | WA3413299 | Unit 1 - A Wing sink blocked in cell A06 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 13:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3413306 | Unit 6 - A7 Unit 6 Toilet has water running through it constantly unable to stop trickling/running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-01 16:00:00 | Fail | Replaced leaking outlet rubber in cistern
MSA-DCS | WA3413311 | Unit 3 - C Wing Copper pipe is leaking in bewtween C3 C4 service duct. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-29 14:00:00 | Fail | Investigated leak. Collected parts. Repaired burst pipe in duct. Tested.
MSA-DCS | WA3413317 | Visits Area - Room 8 Speaker not working well - hard to hear | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-22 08:30:00 | Pass | Attended and test the number 8 non contact visits intercom, ok and working. Job completed.
MSA-DCS | WA3413318 | Unit 4, C wing, Cell C9 - toilets stays running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-24 14:00:00 | Pass | Flushed and cleaned sand from inlet valve and cistern.
MSA-DCS | WA3413322 | Visits area, room 5 - speaker not working well | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-22 10:00:00 | Pass | Rectified and fixed the fault on room 5 intercom, job completed.
MSA-DCS | WA3413384 | perimeter poles 27, 33, 36, 37, and 37 lights not working | Hakea Prison | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 11:30:00 | Pass | Repaired perimeter lights
MSA-DCS | WA3413399 | kitchen large convo therm 40 tray oven water pipe leaking | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 19 Jun 2020 | 2020-06-20 09:10:47 | 2020-06-19 13:25:00 | Pass | Found copper pipe to be leaking , replaced with braided hose, tested ok.
MSA-DCS | WA3413407 | Unit 2, Door controls - door operations and screen are out in the pod | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Jun 2020 | 2020-06-19 13:18:32 | 2020-06-19 16:27:00 | Fail | Attended site, investigated door control issue. Traced fault to PLC control systems. Repaired fault and tested OKJob Complete
MSA-DCS | WA3413415 | Unit 1 A wing cell A13 fire alarm continues to go off with out being a fire | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 19 Jun 2020 | 2020-06-20 09:24:05 | 2020-06-19 12:15:00 | Pass | Attended site and found detector in unit 2 B wing cell 13 in maintenance fault removed old detector and fitted new reset and left normal.
MSA-DCS | WA3413422 | Broken electrical pit at the front of prison | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-19 13:00:00 | Pass | Replace broken pit at front entrance
MSA-DCS | WA3413491 | Garments main workshop lights keep tripping | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-21 11:30:00 | Fail | Replaced faulty hi bay lights in garments and veggie prep
MSA-DCS | WA3413525 | cabinet shop various machines faulty plug and wires | Wooroloo Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 14:30:00 | Pass | Replaced damaged plug tops on various machines
MSA-DCS | WA3413532 | Chaplins Office West Side, Office - No Power | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-19 15:00:00 | Pass | Power tripping chaplins office
MSA-DCS | WA3413552 | CCU control Carpet tiles worn and lifting in numerous places | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-08-12 11:53:00 | Fail | Carpet tiles replaced
MSA-DCS | WA3413566 | Assessments Outside SO office Carpet tiles lifting requires regluing | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-08-17 13:41:00 | Fail | re-lay carpet tiles - install new diminishing strip at door way
MSA-DCS | WA3413580 | Amenities-fluro lights faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-10 15:00:00 | Fail | Investigated faulty lights in amenities. Ordered, picked up and installed replacement parts12 foot ladder used
MSA-DCS | WA3413624 | Unit 2 MDAS fault | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Jun 2020 | 2020-06-20 12:26:27 | 2020-12-16 17:00:00 | Fail | Installed underground conduit between U2 and the education demountable. Ran new cable between Education and the last MDAS point in the U2/3 roofspace. Both receivers online and tested ok. Parts used:5 x lengths of 20mm conduit100m underground 6 core security cable2 x 20mm conduit bends3 x 20 mm couplings
MSA-DCS | WA3413638 | Unit 2, D8 - Hot Tap Not working | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Jun 2020 | 2020-06-20 12:37:17 | 2020-06-19 14:38:00 | Pass | In the duct we’re the qutar turn taps connect. the guide had come off the wall. reinstalled straighten and connected all back together
MSA-DCS | WA3413655 | Unit 13 - A & C A/C Oven not working. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 19 Jun 2020 | 2020-06-20 13:00:15 | 2020-06-19 15:55:00 | Pass | Reset Hi Limit & test operation ok. Trip likely caused by small product fire in cabinet. Smells like burnt product, repair connection at one element.
MSA-DCS | WA3413694 | kitchen GPo faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 12:00:00 | Pass | Investigate and repair kitchen gpo
MSA-DCS | WA3413696 | Maintenance metal w/s gpo faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 10:30:00 | Pass | Investigate and repair metal workshop gpo
MSA-DCS | WA3413698 | Maintenance Bench grinder GPO not working | Karnet Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 08:30:00 | Pass | Investigate and repair bench grinder not working
MSA-DCS | WA3413700 | Unit 2, flood light on Northern end outside - not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 13:30:00 | Pass | Investigate and repair unit 2 flood lights
MSA-DCS | WA3413704 | Unit 7 - D Wing-Dryer keeps tripping the power in the laundry. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 09:00:00 | Pass | Investigated dryers in scu d wing. Found was being overloaded with clothes.
MSA-DCS | WA3413720 | Stores - Front Entrance-Isolator filled with water tripping refrigeration container at stores | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 19 Jun 2020 | 2020-06-19 18:12:38 | 2020-06-22 15:00:00 | Fail | Investigate and repair tripping stores circuit.Found water in GPO, drained water.Returned, resealed, replaced outlet and reterminated.
MSA-DCS | WA3413726 | Unit 10 B10 toilet broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 12:52:00 | Pass | Removed broken toilet reinstalled and adjust pipework
MSA-DCS | WA3413728 | MPU (8) - Day Room Faulty electrics, no evidence of damage or water leaks,-see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 15:27:00 | Pass | Found cockroaches in control box
MSA-DCS | WA3413778 | Disabled toilet (in the staff area) - Lock on the door faulty, | Midland (North East Metro) | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-23 09:00:00 | Pass | Attended site to re-fit disabled toilet lock.Date on site: 23/06/2020Time on site: 08:30am - 09:00am
MSA-DFES | WA3413457 | Bollards on Irwin street - will not come back up | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 19 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 14:30:00 | Pass | Arrived onsite at 1:30Located reported faulty bollards and found no fault. Only issue is the controller is a bit temperamental in locations but either than that everything works fine, Heather will speak to LEDA when they are onsite.Left site at 2:15
MSA-DTAG | WA3413386 | Ground floor, womens public toilets - flush has stoppeed working well, | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-19 13:20:00 | Pass | Push button broken replaced with new
MSA-DTAG | WA3413420 | Lift 3 is functioning erratically again- is skipping floors, flying up & down to different floors | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-19 12:00:00 | Pass | job completed - Lift shut down till door drive had arrived and replaced
MSA-DTAG | WA3413440 | Custody Centre - hot water system in custody area has ceased working | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-19 11:15:00 | Pass | COMPLETED
MSA-DTAG | WA3413463 | Multiple lights out - Magistrate 2 Chambers 2x lights & Lights in garage 1 & 2 also out | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-30 08:00:00 | Fail | Inspected fault. Replaced blown fuse and blown tubes.
MSA-DTAG | WA3413535 | Level 5- Digilock toilets Lift Urinals in mens bathroom flushing upon entry to the toilet | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-22 08:01:00 | Pass | Complete
MSA-DTAG | WA3413546 | W24.16 - Mileston display montiors not working | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 19 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 10:00:00 | Pass | issue had been fixed by the time the contractor arrived
MSA-DTAG | WA3413558 | L1 DPP Kitchen Door handle is loose, almost falling off | Perth Children's Court | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-22 10:15:00 | Pass | NEW HANDLE INSTALLED
MSA-DTAG | WA3413585 | ground Document Production Team Light flickering above Doc Prod area | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 10:30:00 | Pass | Scissors lift required
MSA-DTAG | WA3413690 | Level 3, Judicial support - No power to Kitchen, tripped out.This seems to happen on a regular basis | Central Law Courts-Main Building-Level 3 | WSM-BR-SITE | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 19 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-11 11:00:00 | Fail | Job complete
MSA-DTAG | WA3413741 | Special Clean in Court 1 – Customer urinated on a chair in the public gallery -see notes | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 19 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-24 23:00:00 | Fail | P1 Completed
MSA-DTAG | WA3413763 | Ground Kitchen - Water leak under the sink | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 15:25:00 | Pass | Long DescriptionChecked for leaks under the kitchen sink: no leaks found. Office employees have seen leaking around the blue water filter. Advised them to keep an eye on it and report it as soon as the leak can be seen.Unable to contact Iain.
MSA-DTAG | WA3413784 | Ground floor Custody Cell 1 camera going down intermittently | Midland Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 12:00:00 | Pass | Attended site checked Custody Cell 1 Camera working ok when technician arrive. Customer report on last Friday it dropped offline intermittently. Checked footage and found camera did dropped offline a couple of time, every time last less than 20 seconds. Ping camera IP address ok. Tried to reboot the camera. Tested camera ok. Advised customer report again if camera fail and may need to replace cameras if it happens again. Camera Brand: FLIR. Model CC-3103.
MSA-DTWD | WA3413433 | B block BF20 Door not opening with swipecard | Mandurah Campus (formerly Peel) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 10:00:00 | Pass | We replaced the single door controller and did nothing so we put old one back on. Checked cable was ok.Checked lock was working ok voltage was working ok. Programing is correct and reader is ok. We believe the problem could be from the lan the controller not receiving the unlock signal from the Tecom panel. The batteries were replaced as they were 7 years old
MSA-DTWD | WA3413442 | Child care - power tripping out | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 19 Jun 2020 | 2020-06-19 13:47:04 | 2020-07-15 15:30:00 | Fail | Replaced faulty hws and replaced faulty light. All now working. Informed staff of job completion
MSA-DTWD | WA3413514 | S block wing Damage to flooring requires ACM testing | Mount Lawley Campus | GMP-BR | Flooring | Concrete (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 16:00:00 | Pass | Tested vinyl floor tiles for ACM- Asbestos detected
MSA-DTWD | WA3413544 | A block roof tool store Inspection reveals possible entry point for animals - see notes | Mandurah Campus (formerly Peel) | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 11:00:00 | Pass | Installed flashing to hole in building roof to stop possums gaining access.
MSA-DTWD | WA3413591 | F block ground F30 RDC tripping power to IT server | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 19 Jun 2020 | 2020-06-22 17:00:00 | 2020-07-06 10:45:00 | Fail | Attended site, replaced all components in switchboard in F30. Job complete
MSA-DTWD | WA3413614 | Level 3 Roof Plant rust treat & repair corrosion damage to chiller | Perth Campus B4 | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-07 12:45:00 | Fail | completed as per quote
MSA-DTWD | WA3413631 | Roof leak over laundry | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 19 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-25 13:00:00 | Fail | Down Pipe was blocked with leaves. Cleaned out leaves. Down Pipe outlet needs to be modified to ensure it doesn't reoccur. New down pipe and gutter end cap installed
MSA-DTWD | WA3413666 | W.C wash hand basins x 6 flexi hoses rusted, need replacing with new and mini stops. | Jandakot Campus - Hangar | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-17 11:28:00 | Fail | Replace fixtures had to wait for water Corp to replace main isolation
MSA-DTWD | WA3413670 | C15 Disabled toilet basin plug waste leaking and Broken need replacement | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-22 16:02:00 | Pass | Replace plug and waste and trap
MSA-DTWD | WA3413684 | Faulty lighting in Rooms 1, 2 and 3 – 6 faulty light in total-see notes | Armadale Campus - 145 Jull Street | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-25 14:00:00 | Pass | Attended site and signed in. Inspected room and got out tools needed. Replaced light fallen out of roof in room 3 with new led. Replaced all faulty fluros and starters with new. Tested all ok. Informed staff and signed out. Job complete.
MSA-DTWD | WA3413688 | Faulty lighting in student kitchen-see notes | Armadale Campus - 145 Jull Street | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 11:30:00 | Pass | Replaced faulty Fluor tubes in kitchen and hallway. All now working
MSA-DTWD | WA3413692 | Faulty external security lighting along veranda -see notes | Armadale Campus - 145 Jull Street | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 13:30:00 | Pass | Replaced blown tubes on outside security lights. All now working
MSA-DTWD | WA3413699 | Faulty emergency exit light in corridor near rooms 2 & 3-see notes | Armadale Campus - 145 Jull Street | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 11:45:00 | Pass | Replaced tube on exit light
MSA-DTWD | WA3413702 | Banks St Car Park C-Block - There’s a large crack in the concrete fascia, need to have it inspected | Carlisle Campus | GMP-BR | Roofing | Concrete Roof Construction (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-21 12:15:00 | Fail | Engineers inspection completed and report submitted to Andrew Crawford. Andrew confirmed to close off job and requested a quote - Refer to RFQ WA3413702
MSA-DTWD | WA3413743 | N/W corner of the above. roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 19 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 11:30:00 | Pass | Sealed various sections of roof. Site cofirmed no more leaks. Job completed
MSA-DTWD | WA3413766 | Lift 3 motor in plant room has leaked a significant amount of oil. | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 19 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-19 18:40:00 | Pass | The drive system was faulty. Following our attendance, the equipment was left in service.
MSA-DCA | WA3414816 | Faulty fire pane & false alarm.sj | His Majesty's Theatre-Theatre Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 20 Jun 2020 | 2020-06-20 12:41:58 | 2020-06-20 11:42:00 | Pass | Attended site - investigated FIP & EWIS - warning system activated light illuminated. Alert & evac all illuminated with FIP - further investigation proved FIP was "frozen" and would not reset. Has to rebook and monitored - all cleared except previous faults.
MSA-DCS | WA3414862 | Centrel control vehicle grill - tracks are broken under the motor | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Jun 2020 | 2020-06-20 22:19:52 | 2020-06-20 15:45:00 | Pass | Phone support to site and found the vehicle gate leading to reception track under the motor is worn out and broken and stuck the gate from opening and closing. It sounds like a door mechanical problem. Advised customer to call PFM to get the correct contractor to check the problem.
MSA-DCS | WA3414871 | Front gate Master control room- internal service gate is not closing | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 20 Jun 2020 | 2020-06-20 19:17:49 | 2020-06-23 12:30:00 | Fail | Job completed - Replace 3.6 volt lithium battery to PE. Test operation okay
MSA-DCS | WA3414873 | Karnet Prison Farm- Zone 1 Camera- 2 is not working | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Jun 2020 | 2020-06-20 20:20:08 | 2020-06-20 19:00:00 | Pass | Attended site checked and found Zone 1 Camera 2 is showing green screen on control monitor. Checked on field in EC cabinet camera signal is ok. Located the problem to be the Indigovision encoder. Reboot encoder and tested it all ok. Encoder is old. If problem happens again suggest to replace the encoder.
MSA-DCS | WA3414876 | Casuarina Prison - Unit 4 - Cell water is murky. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 20 Jun 2020 | 2020-06-20 20:45:52 | 2020-06-20 18:29:00 | Pass | nil
MSA-MRWA | WA3415355 | Ground Floor - Carpark -Gate stuck open, unable to close | Traffic Operations Centre-Main Building-Ground Floor | GMP-BR | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 20 Jun 2020 | 2020-06-20 17:54:21 | 2020-06-20 16:15:00 | Pass | Found that there was no 240v power going to the gate motor, checked the switchboard and the breaker was switched on, advised site to contact their electrical contractor. Manually secured the gate.
MSA-DCS | WA3414917 | Unit 4,Emergency sell call c9 not working | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Jun 2020 | 2020-06-21 13:55:04 | 2020-06-21 12:00:00 | Pass | Attended site checked and found Unit 4 C9 cell call not working properly. Office can hear the cell but cell hard to hear office. Found the cell call point speaker grill is full of toothpaste. Cleanup the toothpaste and tested all ok.
MSA-DCS | WA3414921 | In unit 2 cell call system not working | Bunbury Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Jun 2020 | 2020-06-21 18:27:39 | 2020-06-21 15:30:00 | Pass | Attended site checked and found Unit 1,2,3 and Control cell call consoles are showing network errors. Cleared all the network errors and tested cell call working ok. Also found Unit 6 cell call in office can hear cells but cells can’t hear office, cell call PA function not working. Tried to divert the cell call to gate control then it works. Suspected Unit 6 cell call handset problem or audio output problem. Unit 6 still under warranty, ask customer to contact with PFM to get Honeywell to look at the job.
MSA-DCS | WA3414932 | Hakea Prison-Unit 3-MCC room door lock need to be repairerd ,unable to lock | Hakea Prison-Unit 3 | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 21 Jun 2020 | 2020-06-21 15:10:56 | 2020-06-22 12:10:00 | Fail | supplied and installed refurbished lock.
MSA-DCS | WA3414943 | Kitchen -dishwasher is faulty not working | Karnet Prison Farm-Hydroponics Stores | GMP-BR- HO | Catering | Catering Services (CT) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 21 Jun 2020 | 2020-06-22 12:06:59 | 2020-06-24 11:00:00 | Fail | Dishwasher blowing power. Check washer & controls. Dismantle, remove all dead & wet cockies. Still faulty, open main isolator, full of water beyond repair. Remove faulty switch, install new switch. Repair junction box. Assemble & test.
MSA-DCS | WA3414957 | Tamper alarm is not secured in gatehouse | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Jun 2020 | 2020-06-21 17:28:57 | 2020-06-23 14:22:00 | Fail | Replaced cabling connection and reed restored, monitored for a couple hours with no further activation. Reed not replaced.
MSA-DCS | WA3415610 | Perimeter Fence 4-7 Alarm is offline | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Jun 2020 | 2020-06-21 16:00:00 | 2020-06-21 10:15:00 | Pass | Phone support to site and found Perimeter Fence Zone 4-7 alarm we’re showing offline before. It seems recoded when technician called site. Instructed control staff to conduct walk test in Zone 4-7 and confirmed alarm activated and reset correctly. Informed customer we will close the job. If any problem happens, call PFM again.
MSA-DTAG | WA3414979 | fire panel fault - level 9 return air duct | Central Law Courts-Main Building-Level 9 | WSM-BR-SITE | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 21 Jun 2020 | 2020-06-22 15:33:27 | 2020-06-22 09:30:00 | Pass | Attended site to investigate fault on level 9 exhaust. We had to gain access to the exhaust duct and physically go inside it to try and reach the faulty smoke detector. 2 techs were required. We were able to get access and change out the smoke detector. Did a fip reset and reboot and all was ok.
MSA-DCA | WA3416049 | Tap in the Green Room is leaking water - The tap in the Green Room is leaking water from the top | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Green Room | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 16:45:00 | Pass | Replaced leaking and corroded mixer
MSA-DCS | WA3415078 | Lvl 1,2,3,4-Delays with securing stairwell doors using swipe card access & beeping A/H on front door | East Perth | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-23 09:19:00 | Pass | Reduced door unlock time and fixed up red on beeping door adjusted Rex on one door
MSA-DCS | WA3415099 | Stores Yard External Gate- Lock is Jamming when Locking | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 07:07:19 | 2020-06-22 14:15:00 | Pass | Adjusted strike hole to allow proper operation of lock.
MSA-DCS | WA3415108 | House 11, Bathroom- Unable to turn light off – switch faulty | Boronia Pre-release-AP23 - Prisoner Accommodation House 10 and 11 | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-22 10:30:00 | Pass | Investigate and repair house 11 light switch
MSA-DCS | WA3415125 | Jeelia, B Wing - Dayroom tv airial playing up | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | General AV works (AV) | Sapio Pty Ltd | 3 | CLOSE | 22 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 14:00:00 | Pass | Replaced wall plate and tested.
MSA-DCS | WA3415131 | Main Kitchen, Dishwasher has water leaking | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 07:29:28 | 2020-06-22 17:00:00 | Pass | Main Kitchen Dishwasher leaking water. Agent attended, checked machine. Repaired faulty pipework. Faulted again. Agent replaced water inlet solenoid. Assembled & tested. All ok.
MSA-DCS | WA3415193 | Unit 2 B10 prisoners lock is jammed and prisoners in the cell | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 22 Jun 2020 | 2020-06-22 12:05:24 | 2020-06-22 13:45:00 | Fail | Supplied and installed new lock. Adjusted hinge to ensure proper operation of door.
MSA-DCS | WA3415222 | Unit 4 - D Wing cell D12 Toilet cistern is not filling up with water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-23 16:00:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3415226 | Unit 3 Cell B10 toilet not flushing properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-30 16:00:00 | Fail | Installed new inlet valve in cistern. Tested
MSA-DCS | WA3415236 | MPU (8), Cell M11- Observation window cracked | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-07 14:00:00 | Fail | OBS PANEL RE GLAZED
MSA-DCS | WA3415238 | INF (10), Cell C3- Toilet seat is damaged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 14:35:00 | Pass | Collected seat from supplier. Replaced broken seat and removed rubbish.
MSA-DCS | WA3415241 | Unit 13,A wing cleaning store has a hole in the wall. | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-08-18 13:09:00 | Fail | THIS JOB WAS A DOUBLE UP WITH #WA3095870INVOICED COST TO DATE ONLY FOR ATTENDANCE
MSA-DCS | WA3415244 | Unit 2, Cell A7- Cell window is broken, metal rods hanging from sides of it. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-01 13:30:00 | Fail | REPAIRED/ RESET SASHES
MSA-DCS | WA3415249 | Unit 1, D Wing, Cell D12- Door viewing hatch broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-01 11:00:00 | Fail | HATCH & FRAME REPAIRED- LOOSE GLASS RESET
MSA-DCS | WA3415250 | Unit 4 - A Wing Cell A11 toilet cistern isnt refilling. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 15:00:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3415261 | Unit 5, A Wing, Cell A7- toilet is not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-01 12:00:00 | Fail | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3415264 | Unit 3 D5 Buzzing sound when cell call activated | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 08:45:15 | 2020-06-22 12:00:00 | Pass | Poor audio quality in cell when tested. Removed and replaced intercom. New intercom tested loud and clear in cell and in control room. Parts used:Cell Guard intercomRJ45 cable adapter Consumables
MSA-DCS | WA3415267 | Kaartdijin Mia - Wash Basin in middle prisoner's toilet is leaking water. Need fixing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-23 14:00:00 | Pass | Tightened trap and replaced trap rubbers.
MSA-DCS | WA3415272 | Unit 9 A3 Vinyl lifting and in poor condition | Hakea Prison | SPA-BR | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2021-02-15 10:30:00 | Fail | DAMAGED VINYL REPLACED TO AREA
MSA-DCS | WA3415274 | Kaartdijin Mia - Day room. Lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-20 13:30:00 | Fail | Check fault, require parts.Remove frame edge capping, install floor mount bracket, secure frame to bracket, install fame capping and check lock function.
MSA-DCS | WA3415281 | Unit 1, A Wing- Grill motor appears to over heat causing unit to shut down, unable to use til cooled | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-29 16:00:00 | Fail | 25/06/20Attend site.Inspect motor, liaise with maintenance staff.28/07/20Replace grille motor - in progress29/07/20Replace grille motor - complete
MSA-DCS | WA3415285 | Unit 5 A16 GPO on wall broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 12:00:00 | Pass | Replaced gpo
MSA-DCS | WA3415307 | Unit 4, B & D Wing- Oven fan is faulty | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-08-07 10:05:00 | Fail | Adjust door, Fitted door lock spring ok but access and mount bolts for hinge are corroded. Drill out hinge mount bolts, fit new nut/threads. fit new hinge & new bolts.
MSA-DCS | WA3415318 | CCU (11), Cell D5- Cell call not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 09:02:19 | 2020-06-22 12:30:00 | Pass | Replaced damaged cell call with new, job completed.
MSA-DCS | WA3415322 | Unit 4 wings PA making a high pitched buzzing noise | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 10:30:00 | Pass | Recalibrate and adjust the amplifier due to buzzing sound, job completed.
MSA-DCS | WA3415329 | Unit 9 C4 & C9 Taps constantly dripping | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-23 09:02:00 | Pass | Replaced one tap in both cells and re oringed outlet
MSA-DCS | WA3415337 | Education 1, smashed window (approx 1750x600) | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-26 11:00:00 | Fail | WINDOW REGLAZED
MSA-DCS | WA3415338 | Unit 1 A1 Smashed viewing panal | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 09:13:47 | 2020-06-22 15:00:00 | Pass | REGLAZE OBS PANEL
MSA-DCS | WA3415345 | Zone 12, Outside fence, water leak on main line | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 22 Jun 2020 | 2020-06-22 13:18:27 | 2020-06-22 14:31:00 | Fail | Attended site,Locate 100mm burst galv main water line,Isolate water and cut it burst section of pipe,Supply and install 100mm gibolt coupling and section of galv pipe to repair the burst. Tested works on completion
MSA-DCS | WA3415349 | kitchen LGE Combi Therm Oven not working. Intermitently Cycling | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 09:20:33 | 2020-06-30 10:25:00 | Fail | Replaced door magnet & tested ok
MSA-DCS | WA3415390 | Amenities -change the timers on the site lighting, on at 1730 and off at 0730. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-29 08:30:00 | Pass | Reset time clock in amenities building for external lighting
MSA-DCS | WA3415405 | Unit 1, Cell D3- Broken floor tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-12-14 09:55:00 | Fail | door lifted and hinges re welded and tiles replaced with new
MSA-DCS | WA3415410 | Unit 1, C-12 - Broken Shelf & Bottom Bunk End Panel | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-13 14:30:00 | Fail | Attended site to investigate and organise repair works.Re attended site and carried out repairs to the damaged end panel on bunk bed.
MSA-DCS | WA3415433 | Unit 1, Cell A16- Cell door face plates missing | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-01 09:30:00 | Fail | Supply and installed new stainless steel face plates to cell door.
MSA-DCS | WA3415438 | Unit 1, Cell B10- Cell door face plates missing | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-01 10:30:00 | Fail | Supply and installed new stainless steel face plates to cell door.
MSA-DCS | WA3415443 | Unit 1, Cell D9 Cell door face plates missing | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-02 11:03:00 | Fail | Supply and installed new stainless steel face plates to cell door.
MSA-DCS | WA3415446 | Unit 1, Cell B9- Cell door face plates missing | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-01 12:30:00 | Fail | Supply and installed new stainless steel face plates to cell door.
MSA-DCS | WA3415464 | Carpark - Street light at the end of stores near cable gate is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-24 15:00:00 | Fail | Replaced damaged street lights in front car park
MSA-DCS | WA3415560 | Investigate low water pressure across site | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-23 12:29:00 | Pass | Investigate low water pressure to unit1 and shed
MSA-DCS | WA3415567 | Unit 2, Officers station- Controller offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 22:50:00 | Pass | Controller has failed completely, power and communications ok, installed new Gallagher 6000 and tested inputs.Working correctly
MSA-DCS | WA3415568 | Unit 3, Officers station- Controller offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 07:37:00 | Pass | Checked controller, still offline, unable to ping controller from server, power cycled, still offline.Replaced controller, online and operational
MSA-DCS | WA3415572 | Gatehouse- UVSS light blub is not worrking | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 08:00:00 | Pass | Re-terminated 24vac light globe connections in UVSS. all UVSS lights activate when pressure sensor is activated
MSA-DCS | WA3415604 | Unit 2, Cell A5- Reading light is broken/exposed wires | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 11:15:40 | 2020-06-26 10:00:00 | Fail | Isolated damaged cell light. Picked up replacement cover and fitting for maintenance. Installed and tested
MSA-DCS | WA3415613 | Unit 4 Cell door B5 is not shutting correctly, door will only shut when double locked | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-02 10:45:00 | Fail | On site replace hinges and lock.Attend site replace door plate and weld on strike plate.
MSA-DCS | WA3415625 | Unit 4, B & D showers have no water pressure. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 16:00:00 | Pass | Cleaned tmv’s, flushed all pipework and cleaned sand out of showerheads.
MSA-DCS | WA3415629 | WWTP air valves faulty | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-30 16:00:00 | Fail | WWTP Air Valves faulty. Check valves, beyond repair. Order new parts. Pick up & return to site to install.
MSA-DCS | WA3415630 | Kitchen floor drain near office blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-23 12:30:00 | Pass | Clear blocked floorwaste drain in kitchen near staff office.
MSA-DCS | WA3415640 | Internal Visits Centre Family Rooms & Holding Cells Cameras Not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 11:34:51 | 2020-06-24 17:30:00 | Fail | Adjust the alignment multiple cameras internal visit area. Job completed.
MSA-DCS | WA3415649 | Maintenance office, Store Room - Repair Test & Tag Birko Toaster Damaged Power Lead | Hakea Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-02 13:00:00 | Fail | Replaced damaged plug top
MSA-DCS | WA3415721 | Exit/entry to back centre cars carpack The exit sign is not lit up. | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-01 11:00:00 | Fail | Repaired flouro exit light near door to rear car park. Replaced water damaged led exit light above door to rear car park after sourcing replacement.
MSA-DCS | WA3415824 | Unit 5 C Wing Regi Area Double GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 13:00:00 | Pass | Repaired GPO
MSA-DCS | WA3415826 | Assessment, female staff toilet is blocked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 13:18:55 | 2020-06-23 10:30:00 | Pass | Attended site,Used drain machine to clear tree roots from sewer line as required. Tested works on completion
MSA-DCS | WA3415839 | Unit 5, House 2- Kitchen sink is blocked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 13:16:56 | 2020-06-23 12:33:00 | Pass | Attended site,Used drain machine to clear a grease blockage to the main sewer line. Tested on completion
MSA-DCS | WA3415854 | Unit 5 A12 & A5 Cell calls faulty | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 09:00:00 | Pass | Very low audio due to dirt inserted inside the speaker plate. Clean and test cell calls. Job completed.
MSA-DCS | WA3415884 | BatCave West Fluorescent Light Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 15:00:00 | Pass | Repaired light
MSA-DCS | WA3415886 | Education, Prisoners lunch room - Water boiler is not filling up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 10:43:00 | Pass | No water in unit on arrival. Also water not hot. Turned unit on to Heating.Main isolation to urn turned off. Waited for unit to fill and heat to temp, element took awhile to heat up. Cleaned calcium off tap. Normal operation
MSA-DCS | WA3415888 | Unit 2 B4 Judas Hatch Lock Not locking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 13:44:14 | 2020-07-15 12:00:00 | Fail | Supplied and fitted replacement hatch and lock.
MSA-DCS | WA3415914 | Remove old VSD & water pumps and store at Hakea stores | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-15 11:00:00 | Fail | Moved pumps from outside yard into programme store, to protect from elements. Removed Vsd from wall and stored with old unit inside store with pumps,until able to be transported to Hakea. Truck collected from yard. Pumps loaded at casuarina. Transported to Hakea. Car need to be moved in front of Pfm shed. Pumps unloaded and stored. Vsd boxed and stored. Keys returned to Pfm office. Truck returned.
MSA-DCS | WA3415931 | Repair commercial dishwasher- no water flowing into machine. | Nyandi Training Academy | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 14:08:52 | 2020-06-23 08:30:00 | Pass | Commercial dishwasher faulty, no water flow. Check washer & controls. Clean contacts on solenoid, still faulty, removed & replaced with new solenoid. Reconnect & test. All working correctly.
MSA-DCS | WA3415978 | Lights are not working- see locations below | South West Metro Cockburn | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-25 15:00:00 | Pass | Replaced lamps and control gear as required .
MSA-DCS | WA3415979 | Health Admin- Hot water urn in medics tea room has stopped working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 10:43:00 | Pass | No water in unit on arrival. Main isolation to urn turned off. Waited for unit to fill and heat to temp. Cleaned calcium off tap. Normal operation
MSA-DCS | WA3415991 | Kaartdijin Mia -Leak in Wash basin in Prisoner Toilet 1. Next to Day room in Kaartdijin Mia | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 15:00:00 | Pass | Tightened loose basin tap and retightened leaking trap under basin
MSA-DCS | WA3416009 | Kitchen - Main Bell faulty regulator | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-03 16:10:00 | Fail | Returned 3/07 for repairs to kettle. Replaced solid state control, calibrate as required. Test tilt kettle ok now.
MSA-DCS | WA3416057 | Gate house - X-ray machine has a burning smell coming from it | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-08 08:19:00 | Fail | Subcontractor attended and made attempt to repair X-ray - Unit beyond economical repair - X-ray was replaced by another contractorNo further works by SEME
MSA-DCS | WA3416070 | Bakery- Bread slicer #1 is faulty, see notes below | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 22 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-23 13:30:00 | Fail | 23/07/20 - Called as requested to the slicer faulty. Made repairs to the emergency stop switch and checked rear panel securing.
MSA-DCS | WA3416072 | Bakery- Bread slicer #2 is faulty, see notes below | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 22 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-23 14:30:00 | Fail | 23/07/20 - Called as requested to the slicer not working. Found the front panel not in correctly and the blades loose. Secured the panel correctly and tensioned the blades all working correctly now.
MSA-DCS | WA3416151 | The lock of the front sliding door is not working properly | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-23 11:00:00 | Pass | Checked physical door operational, tested key control functions correct, tested Gallagher control of door correct, site staff unable to advise issue occurring, door is currentl yh full y operational and was m o nitored for the day.
MSA-DCS | WA3416157 | Electronic gate between Selly Port and Reception faulty | Melaleuca Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 22 Jun 2020 | 2020-06-23 01:53:31 | 2020-06-22 23:00:00 | Pass | Travel to site. Inspect gate. Found gate open. Found PE fault. As a temporary fix, bridged out PE. Test gate operation,all okay. Will need to return with correct battery. See your work order WA3414871 for return visit to replace batteryduring normal working hours.
MSA-DFES | WA3415530 | L1 kitchen Zip Hot water boiler (Kitchen) not working | CFRS Murdoch | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 09:30:00 | Pass | Replaced hot pump on zip hydrotap A40051076C
MSA-DFES | WA3415622 | Fire fighters Bathroom - Ceramic soap holder broken (sharp edges risk of injury). | CFRS Daglish | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-08-25 10:30:00 | Fail | Complete
MSA-DFES | WA3415710 | Main building, ground, changeroom 4 - No hot water in Changeroom 4 showers. | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 13:33:00 | Pass | Repair hot water unit
MSA-DFES | WA3415988 | ladies toilet next to kitchen Leaky tap in women’s toilet.-see notes | DFES Regional Office - Belmont | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-27 09:32:00 | Pass | Attend to repair basin taps ladies toilet near kitchen un able to repair fitted new Bristol basin set ,mini stops , flexy hoses test all connections
MSA-DTAG | WA3415025 | Central Law Courts-Main Building-Magistrate Car Park L1- Alarm coming from Fire Booster | Central Law Courts-Main Building-Level 9 | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 22 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 10:30:00 | Pass | Attended to investigate fire pump fault. Jacking pump was in fault and not working. Found that there is works being done outside of building and very likely a hydrant has been used multiple times and the jacking pump has been going in and out for a while thus making it trip out in the board. I reset the switchboard and the jacking pump is all clear and working again.
MSA-DTAG | WA3415175 | Lvl 1- Sheriff’s Office- Front door is not opening | Supreme Court | WSM-BR-SITE | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 22 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 09:01:00 | Pass | Found that the lock was jamming due to the door being knocked out of alignment, re-aligned doors and tested, all ok.
MSA-DTAG | WA3415346 | Custody, control room - Duress light for pre trial room on Duress indicator panel not functioning. | Mandurah Courthouse | GMP-BR-HO | Security | Security Management System (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-22 16:00:00 | Pass | 22/6/20 - Dean Simpson, Joshua ParkConnection on the LED loose.Re-soldered connection and tested all ok.
MSA-DTAG | WA3415480 | Outside of building, Facing McIver Station - Graffitti on building in 2 places | Perth Children's Court | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-29 14:30:00 | Pass | Removed graffiti
MSA-DTAG | WA3415929 | Ground/first - Lift not working, won’t move | Perth Children's Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 13:30:00 | Pass | Not chargeable
MSA-DTAG | WA3415956 | Level 4, Adult Community Corrections Kitchen - Hot water system will not turn off and is pouring out | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 13:35:00 | Pass | Ran tests as unit off on arrival. Hot water intermittently coming out of the hot side of the tap. Very dangerous. Replaced XL tap and dual solenoid. Ran further tests and cleared fault log. Normal operationreplaced inlet solenoid kit, wiring loom /level sensor and Level Sensor Assembly + main PCB Kit. NOTE WORK ORDER CLOSED EARLY IN ERROR.
MSA-DTAG | WA3416028 | SEME to replace broken duress button located in Family violence office | Rockingham Justice Complex | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-06 08:45:00 | Fail | Pickup part and travel to siyto replace the damaged duress pendant. Tested it ok after replacement.
MSA-DTWD | WA3415324 | B Block, G Floor - Faulty door lock on south western exit door | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-08-28 14:35:00 | Fail | B Block - G Floor - Faulty door lock on SW exit door.See Nathan.Door locks repaired and replaced.
MSA-DTWD | WA3415388 | whole building Bad smell in building | Armadale Campus - 40 Commerce Ave | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 10:30:00 | Pass | Located and removed dead mouse from roof void (hallway outside room 4). Placed deodoriser bag to affected area.
MSA-DTWD | WA3415411 | block 8 ground passageway Bad smell in passageway outside 8G20 again-see notes | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 09:00:00 | Pass | Bad smell reported in block 8 , upon inspection light bad smell noted , installed deodoriser bag to affected area.
MSA-DTWD | WA3415440 | level 2 - male staff toilet running continuously | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-22 13:52:00 | Pass | Repair leaking toilet
MSA-DTWD | WA3415538 | L Block - lift stuck on first floor (Swipe card activates but wont release lift to ground level) | Mandurah Campus (formerly Peel) | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 13:15:00 | Pass | Not chargeable
MSA-DTWD | WA3415540 | E block. Restaurant/large scale kitchen. Freezer unit fan noisy | Joondalup Kendrew Campus | GMP-BR | Refrigeration | Freezers (RE) | Precise Air Group | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-23 10:00:00 | Pass | Accessed and signed in . Inspected freezer room 2 for noisey fan mtr. Found hrs evaporator fan has noisey bearings. New replacement sourced. Unit isolated and fan replaced. Unit tested ok. Ensured freezer room came down to set temps. Operation as desired.
MSA-DTWD | WA3415550 | E block. Restaurant/Large scale kitchen. Large stockpot safety valve not working | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-16 08:30:00 | Fail | 16/7 Thermostat replaced. Tested.
MSA-DTWD | WA3415554 | E Block, Mens Toilet is blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-22 12:45:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3415609 | Roof leak - NW Awning, J Block, leaking downpipe | Rockingham Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-08-19 15:30:00 | Fail | Scheduled for 19/8/20 weather permitting New section of box gutter installed 19/8/20
MSA-DTWD | WA3415674 | A block ground multiple Several fluoro tubes not working | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-25 12:00:00 | Pass | Replaced multiple lamps out throughout Ablock. Tested. All working, job completed.
MSA-DTWD | WA3415774 | E Block, E74/75 Kitchen Entrance – 7 Lights not working | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-01 08:12:00 | Fail | Repalced faulty light in kitchen canopy and light in E70 classroom .job completed
MSA-DTWD | WA3415806 | Lvl 2, Library Door- Disconnect broken sign | Perth Campus B2 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 22 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 07:30:00 | Pass | Isolate power to sign in front of library.job completed
MSA-DTWD | WA3415818 | C block - Auto door entry sensor not working on the west side of C Block. | Midland Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-22 14:42:00 | Pass | Found that the external sensor has failed, replaced faulty sensor, tested and adjusted, all ok.
MSA-DTWD | WA3415944 | Block 3, Fitting and Machining- Manual roller door hard to open and close | Thornlie Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-22 16:00:00 | Pass | 1053191. Found roller door getting tight when opening and closing, lubricated guides and door where necessary and tested all ok, advised staff that door may need replacing in near future due to age and condition
MSA-DTWD | WA3415952 | Block 6 stairwell VBB steel store Lights in stair well faulty | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-07-13 12:15:00 | Fail | Attended site and signed in. Located stair well lights. Removed old light and replaced with new led fitting. Installed new light below existing. Tested all okay. Job complete
MSA-DTWD | WA3415957 | L2 RHS auto doors from outside no power-see notes | Perth Campus B6 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-01 13:15:00 | Fail | Inspected door and found that the controller has failed and requires replacing/ upgrading ASAP. Please quote for a 301 power train, 1x Ixio, 1x pib.Returned and completed upgrade of works as per quotation, tested all ok.
MSA-DTWD | WA3416014 | L2 S218 Replace lighting as required fluro blown | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 11:15:00 | Pass | Attended site, replaced multiple fluros and starters throughout out B1. Job complete.
MSA-DTWD | WA3416023 | D block, Plant room - Repair/Replace damaged door lock to the D Block Plantroom. (lock Jammed) | Midland Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 09:15:00 | Pass | job completed - adjusted strike
MSA-DTWD | WA3416055 | ladies toilet canteen ground tower toilet is blocked and over flowing | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Jun 2020 | 2020-06-23 17:00:00 | 2020-06-23 13:46:00 | Pass | Attended site,Plunged paper blockage clear from toilet. Tested all other toilets all functioning well.
MSA-MRWA | WA3415187 | ground male toilet near kitchen Toilet blocked. | Jandakot Depot | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 22 Jun 2020 | 2020-06-22 17:00:00 | 2020-06-22 11:00:00 | Pass | unblocked toilet
MSA-DCA | WA3416355 | ground studio 15 PowerPoint is not working in Studio 15-see notes | Old Customs House-Main Building-Ground Floor-Office Studio Space | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-23 12:45:00 | Pass | Locate faulty GPO. The gpo is a RCD gpo. The rcd would some times reset and then trip again and other times it would not reset at all. Investigate if any other gpo’s were on the same circuit witch there was not. Left site to get a new rcd gpo. Replaced faulty rcd gpo with new and test. The gpo is now working advised staff of work completed.
MSA-DCA | WA3417108 | blocked urinal | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-AG.19 - Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 15:30:00 | Pass | Clear blockage to urinal
MSA-DCA | WA3417113 | Level 4 - Emergency lighting permanetly on | Art Gallery of WA - James St-Main Building (Block B)-Level 4 | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 09:45:00 | Pass | Located faulty emergency lights on level 4 found blown fuse in level 4e db. Replaced with site supplied fuse tested all ok
MSA-DCS | WA3416257 | Unit 1, Shower sets leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-07 12:30:00 | Fail | Cut in new water isolation on main supply. Re seat shower breach seats (hot & cold) and replace tired wall spindles.
MSA-DCS | WA3416323 | Kitchen, Near Office- Air Con fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 23 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 08:45:00 | Pass | Attended site and investigated AC in the kitchen. Staff wanted to see if the evap and Kitchen exhaust could be run independently of each other as they were getting cold when the evap would run. I investigated the wiring and found that they can be run independently. I showed staff how to operate the switches. I also looked at there air curtain they said was not running. I found a wall switch and run up air curtain. All ok.
MSA-DCS | WA3416333 | Unit 4, Cell B9- Toilet cistern is not working, water constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-25 11:00:00 | Pass | Replaced faulty inlet valve in cistern.
MSA-DCS | WA3416334 | Unit 7, B Wing- Hot water is not constant | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-25 15:00:00 | Pass | Investigated inconsistencies in hot water temps. No power at plant room switch board. Helwig elec called to restore power. Hot water allowed to return to temp. All tmv’s in a/b wing need to be flushed and rechecked due to complaints of cold water a requested by maintenance.
MSA-DCS | WA3416336 | Unit 6 - B Wing- End shower is continually running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-02 11:00:00 | Fail | Replaced leaking spindle in end shower tap set.
MSA-DCS | WA3416343 | Reception, Door 9- MKH lock on door does not lock as per security checks | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-01 17:00:00 | Fail | 24/06/2020. Serviced lock. New cylinder also required.On site 01/07/2020. Supplied and fitted new MKH cylinder and checked operation of lock. - job completed
MSA-DCS | WA3416349 | Reception, Behind desk of induction DO- Carpet tiles require refixing | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-03 08:00:00 | Fail | DAMAGED FLOORING REPLACED
MSA-DCS | WA3416378 | control gate house no audio on durress | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 14:27:00 | Pass | Restored audio to duress system found extender locked up, reset and restored.
MSA-DCS | WA3416445 | Gatehouse, interlock faulty | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Jun 2020 | 2020-06-23 12:48:01 | 2020-06-23 12:00:00 | Pass | Gatehouse office/reception door is under repair by locksmith( forced open) and it was ovveride through the interlocking set up which affected the function Sally port/ gate office door. Advice the SO on site with regards to the issue of interlocking for sally port area. Job completed.
MSA-DCS | WA3416446 | SITE COST Unit 2 A4 Cell Door Jammed Wont Open | Melaleuca Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 23 Jun 2020 | 2020-06-23 12:50:12 | 2020-07-15 12:00:00 | Fail | Supply and fit custom made plates and re-hang door
MSA-DCS | WA3416450 | WARRANTY- Perimeter zone 16, omnitrax constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Dataline Visual Link Pty Ltd | 0 | CLOSE | 23 Jun 2020 | 2020-06-23 12:54:22 | 2020-06-23 12:00:00 | Pass | Completed under warrantly
MSA-DCS | WA3416571 | Hydrotap isolation taps handles broken. | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-29 15:15:00 | Fail | Job complete
MSA-DCS | WA3416617 | Main gatehouse UPS in fault, please investigate | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-24 16:00:00 | Pass | Job completed - Fault apparent with Gatehouse UPS. Attend to diagnose, rectify if possible and provide report of repairs if needed
MSA-DCS | WA3416639 | gate control monitors 1.2. and 3 video feed is lagging | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 10:17:52 | 2020-06-24 17:00:00 | Fail | Travelled to site fromPerth. Attended Gatehouse Equipment room to view camera feeds from different sources, before attending Control Room. Restarted Indigo workstation feeding monitors 1, 2, 3, checked visually with cameras in and around Sally Port to confirm cameras now showing “current” live feed.
MSA-DCS | WA3416659 | Kitchen- Dishwasher faulty plug | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 11:03:00 | Pass | Double up by site. CPB already repairing
MSA-DCS | WA3416661 | Kitchen- Bun divider outlet is cracked | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 22:00:00 | Fail | Replaced cracked outlet and conduit
MSA-DCS | WA3416664 | Education corridor, far end middle light faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 11:37:00 | Pass | Repaired roof pe cell
MSA-DCS | WA3416719 | Camera 62 not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-24 14:46:00 | Pass | Sourced parts, attended site, repaired network fault and tested OK.Job CompleteParts:SEME Stock2 x SFPs2 x 1M Fibre Patch
MSA-DCS | WA3416823 | Unit 3 C11 broken tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 14:06:00 | Pass | Replaced broken pillar tap
MSA-DCS | WA3416842 | ladies toilets 2 x Toilet seats Broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 16:00:00 | Pass | Replaced x2 toilet seats
MSA-DCS | WA3416861 | Kitchen - power cord is faulty for boiler kettle | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 13:40:00 | Pass | Repaired loose cabling under kettle boiler
MSA-DCS | WA3416865 | Kitchen - power cord is faulty for bun divider | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 14:00:00 | Pass | Replaced damaged plug top on bun divider
MSA-DCS | WA3416926 | Kitchen, Prisoners toilets- Blocked & not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 15:00:00 | Pass | Adjust loose flush buttons in wall and replaced x3 outlet washers
MSA-DCS | WA3416943 | Front Gate, Control- Sallyport doors not closing fully | Melaleuca Prison | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 23 Jun 2020 | 2020-06-23 17:23:52 | 2020-06-25 15:30:00 | Fail | Replaced top PE set on outer sallyport
MSA-DCS | WA3416950 | gate house black gates internal not working correctly | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 23 Jun 2020 | 2020-06-23 17:29:18 | 2020-06-23 16:30:00 | Pass | 23/06/20Removed and replaced broken motor track.Adjusted limits to suit.
MSA-DCS | WA3417013 | Front Gate, Internal Service Road Gate- Gate Top Locking Pin Not Working | Melaleuca Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | MARSHALL BEATTIE AUTOMATION | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-23 13:45:00 | Fail | No completion notes
MSA-DCS | WA3417056 | Perimeter zone alarm 1 outer keeps activating | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 14:54:56 | 2020-06-24 11:30:00 | Pass | Adjusted sensitivity and tested operation, all OK
MSA-DCS | WA3417078 | operations office monitor is not workingt | Pardelup Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-25 12:00:00 | Pass | Phone support with Operations Control Officer we managed to resolve the issue. Monitor now showing display from quad unit.
MSA-DCS | WA3417084 | control PTZ 5 is out of focus | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 15:52:52 | 2020-06-24 10:30:00 | Pass | replace MIC IP Starlight.
MSA-DCS | WA3417085 | PTZ1 camera - Vision is puple/pinky. It's not clear. | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 15:57:59 | 2020-07-29 11:30:00 | Fail | Mark Field spoke with Mario Kovac, works to be closed off as camera replacement is a warranty item with another contractor. No further works required
MSA-DCS | WA3417117 | Unit 2, Cell B6 basin sink cracked & broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-24 14:45:00 | Pass | Removed old broken basin installed new one cleaned up and adjusted pipework
MSA-DCS | WA3417118 | Unit 5, Cell B6 Toilet Bowl Cracked and leaking when flushed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 16:48:00 | 2020-06-24 16:10:00 | Pass | Removed broken toilet replaced with new toilet concreted in and adjust flush pipe to suit
MSA-DFES | WA3416460 | Station. Appliance bay Front door of station coming off hinge. Requires attention. | VFRS Kwinana | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 16:15:00 | Pass | Carried out repairs to door hinges
MSA-DFES | WA3417016 | L1 room 3 kitchen roof leak-rainwater was leaking from skylight closest to oven | CFRS Fremantle | GMP-BR | Roofing | Rooflights and Skylights (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 17:00:00 | 2020-07-23 11:30:00 | Fail | Leak around skylight sealed and wet weather confirmation leak resolved
MSA-DFES | WA3417025 | L1 Kitchen air con not working, continues flashing red | CFRS Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-24 09:00:00 | Pass | Attend site, investigate kitchen AC unit UF fault. Power cycle unit and see if fault clears. Fault did not clear. Carry out further checks on unit and found outdoor printed circuit board to have failed. Inquire on availability of replacement board. Found that board is no longer available. Unit will have to be replaced.
MSA-DFES | WA3417046 | Ground floor - Kitchen - leak around filter (under sink) which services the wall urn | CFRS Maddington | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 09:55:00 | Pass | Replaced leaking filter and installed new Maxiflow INSTALLED NEW CAPEX ASSET MAXIFLOW SCALE FILTER SYSTEM A40191312A REMOVED OLD LEAKING SYSTEM TO TIP
MSA-DTAG | WA3416396 | Lvl 4- staff toilet behind Court 41 CLC is blocked. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-24 09:05:00 | Pass | COMPLETED
MSA-DTAG | WA3416413 | Unable to unlock key safe (batteries changed recently) | Rockingham Justice Complex | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-23 10:15:00 | Pass | Attended site, gained entry to safe. Battery compartment faulty.Key pad severely worn, mew safe required.Date on site: 23/06/2020Time on site: 09:45am - 10:15am
MSA-DTAG | WA3416462 | Lvl 4 (CBU), Kitchen- hot water tap is not working (this is separate to the Billi unit system). | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-24 09:40:00 | Pass | COMPLETED
MSA-DTAG | WA3416668 | ground kitchen Leaking tap and hot water system to kitchen | Sir Francis Burt Centre | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 10:56:00 | Pass | Rewashed kitchen taps. Water wouldn’t completely shutt off. Replaced faulty exp valve at the hwu.No tempering valve installed and I haven’t seen any drains connected to the hwu tray.
MSA-DTAG | WA3416711 | CoA Registry counter area- 5 Computers to the public counter area have no power | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Gilmour & Jooste Electrical | 0 | CLOSE | 23 Jun 2020 | 2020-06-23 15:05:13 | 2020-06-23 12:15:00 | Pass | Inspected power and found tripped rcd - reset and tested working
MSA-DTAG | WA3417123 | Special clean - Cell 2and cell 4 in custody control center & Holding dock in court 2 | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 23 Jun 2020 | 2020-06-24 17:00:00 | 2020-06-23 19:45:00 | Pass | Job carried out as per work order
MSA-DTWD | WA3416216 | B40 student support amenities - GPO next to auto door Brocken – tagged out | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 23 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-25 10:15:00 | Pass | Attended site and signed in. Located faulty/broken gpo. Fixed gpo and remounted to wall. Tested all ok. Completed paperwork got pfm to sign and signed out.
MSA-DTWD | WA3416218 | T127 corridor - Light switch in corridor Brocken tagged out | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-25 08:00:00 | Pass
MSA-DTWD | WA3416237 | T Block, Both lifts are not working | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 23 Jun 2020 | 2020-06-23 11:09:28 | 2020-06-23 10:30:00 | Pass | Lift 1 and 2 stop after power surge. Both lifts door drive haven’t started up and lift going in to fault ongoing fault reset liftand all running
MSA-DTWD | WA3416312 | Plant Room-Air drier next large air compressor, Getting a lot of water from condensation in the air | Perth Campus B5 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 23 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-21 11:23:00 | Fail | TECHNICIAN FROM AIR COMPRESSOR/AIR DRYER COMPANY WAS NO SHOW. HAS BEEN ARRANGED FOR HIM TO BE ON-SITE 17/7 AM. ANOTHER TECHNICIAN, CHRIS TO MEET HIM ON-SITE.TRAVELLED TO SITE AND SIGNED IN. GAINED ACCESS TO PLANT ROOM. CHECKED OPERATION OF AIR DRYER. SYSTEM RUNNING OK. COMPLETED REQUIRED PAPERWORKNESSCO ATTENDED SITE WITH TECHNICIAN AND REPROGRAMMED CONTROLLER.
MSA-DTWD | WA3416329 | T Block, No heating | West One Services | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 23 Jun 2020 | 2020-06-23 17:00:00 | 2020-07-06 14:00:00 | Fail | Arrived on site, found boiler on fault , reset fault and building got to temperature within 1 hour, boiler working well, went out on a flame fault , no service since 5/19 , need to get boiler tech to attend to service boiler
MSA-DTWD | WA3416437 | Lvl 1, C Block, Room C113- Worn hose reel is leaking | East Perth Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 10:30:00 | Pass | Sign inGet keysLocate c blockOutdoor yardExisting hose has come off reel and leakingUnable to repairLeft site to get new replacementGot partsReturned and remove old hose reelMark and drill holes for new bracketFit and test new hose reelClean upReturn keys and sign out
MSA-DTWD | WA3416590 | A block Level 3 Aircon to Hr not heating | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-30 10:30:00 | Pass | Attended site collected site keys,set up ladder,harness and barricades,accessed ac4 system and found system to have trpped out on hp switch,reset and adjusted to suit system,checked indoor filters indoor coil and airflows,adjusted airflows to two vents.tested system and left operational
MSA-DTWD | WA3416624 | Lunch room V7 ZIP Hydrotap is displaying filter change status light | Rockingham Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-23 13:45:00 | Pass | Filter service checked unit
MSA-DTWD | WA3416745 | Metals/Electro workshops - 12x blown high bay lights | Clarkson Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-02 15:00:00 | Fail | Replace faulty globes, found some lights beyond repair and required replacing
MSA-DTWD | WA3416812 | A Block - Gutter outside room A 30 has collapsed. | Bentley Campus | GMP-BR | Roofing | Guttering (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-08-25 13:30:00 | Fail | Cleaned roof and gutter, removed flashing and damaged gutter. Replaced new gutter and reattached flashing.
MSA-DTWD | WA3416830 | D block D04 Hot water system is not working | Midland Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 14:30:00 | Pass | Repairs to be done by electrician, fault with unit is supply to unit. No power when isolated in on and breaker is on.
MSA-DTWD | WA3416834 | Between D & G Blocks Damaged communication pit | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-09 15:30:00 | Fail | Attended site and signed in. Dug out ground and removed pit from around cabling. Installed new plastic Comms pit. Made level with slope to avoid damage again. Back filled and clean site. Replaced 2 electrical pit lids with new. All okay Job complete
MSA-DTWD | WA3416857 | M Block, Tiling and bricklaying workshops- Multiple overhead lights out | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-24 11:00:00 | Fail | Repalced 2x light fittings as per braf. All completed now
MSA-DTWD | WA3417034 | A block A313 laboratory operations roof leak | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 13:30:00 | Pass | A313 - Leaking along purlin line from extractor fan requires dry pan flashingJob not completeBRAF Declined so closed off as incomplete
MSA-DTWD | WA3417036 | A Block, Expo above security desk- Roof leak | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 09:15:00 | Pass | A block roof - Trades found there is no access available. They will require a boom lift toaccess area. Believe the joints to the curved roof are the issue and will require cleaningand re-sealing. This is only based on an assumption as they have been an issue in thepast but cannot access without boom.
MSA-DTWD | WA3417041 | A Block, Room A338- Roof leak corridor | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-27 14:00:00 | Fail | Completed works as per BRAF
MSA-DTWD | WA3417057 | Block 6, Metal Fabrication 2, Project store - Damaged lights | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-07 14:30:00 | Fail | Replaced 2x faulty damaged lights in store block 6. All now working
MSA-DTWD | WA3417060 | D block D03A White 2 RCD tripping, found HWH in cleaners store causing trip-see notes | Midland Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-15 13:00:00 | Fail | Replaced hot water unit
MSA-DTWD | WA3417076 | L2 B249 table pulled off wall-see notes | Perth Campus B6 | GMP-BR | Furniture | Domestic Furniture (FU) | AWB Co. | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 12:45:00 | Pass | Attend siteSpoke with BrettFound deskHas been removed from wallNo legs on back of deskMeasured heightsLeft and source partsReturn to siteFit ceiling panel as requested by clientSet legs and fix internally to frame workLevel feet and deskClean up
MSA-DTWD | WA3417079 | E block E23 Female staff toilets – Water damage to ceiling | Bentley Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-10-01 15:30:00 | Fail | Roof leak resolved and ceiling repaired
MSA-DTWD | WA3417093 | exhaust fan is faulty | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 12:45:00 | Pass | Attended site and signed in. Located faulty exhaust fan, and switch. Replaced fan in kitchen and switch for light and fan. Tested all okay. Job complete
MSA-DTWD | WA3417101 | External, south, above sand pit- High bay lights x2 reflector dislodged and hanging | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-07-22 13:00:00 | Fail | Resecured reflectors on 2x highbay V block sand pit.job completed
MSA-MRWA | WA3416622 | Male toilets- Bottom hinge in the 1st stall is about to fail | Materials Engineering Branch | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 14:00:00 | Pass | Sign inSpeak with GrahamMale toilets ground floor1st cubicle bottom hinge, internal spring has snapped and missing pinHinge coming away not safeRemove damaged hingeUsed van stock hinge similar styleReplaced top to match found door wasn’t closing correctlyNeed to get similar width hinge to allow door to operateClosed toilet off and taped offInformed client and explained need to return and source correct hardware to existing terrazzo toiletsOriginal buildClean upLeft site to source parts*called supplierThey may have suitable replacementsNeed to take old hinges in to match hole positions and see what’s in stockGet hardware from suppliersAttend site sign inClose access to toilets with signagePlace new hinges on terrazzo partitionsTemp fix to timber doorPre drill holesFit new threaded rodMark and cut to lengthFit hinges to doorCheck lock working and even margin around doorClean up
MSA-MRWA | WA3416686 | archive room ground Replace existing lock with new lock & issue 4 keys for Business Service staff | Heavy Vehicle Services | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-16 10:10:00 | Fail | replace 1x registered oval cylinder on an archive room and supply 4 new registered keys
MSA-MRWA | WA3416689 | Lorenzo Quijote, Ground floor- desk to be lowered, as it’s currently too high | Heavy Vehicle Services | GMP-BR | Furniture | Office Furniture (FU) | MR - Handyperson - PFM | 3 | CLOSE | 23 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 10:57:00 | Pass | Dropped desk back to normal height
MSA-MRWA | WA3417086 | Ground Floor – Men’s Toilets – 2nd toilet upon entry.-toilet blocked-see notes | Heavy Vehicle Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-25 13:55:00 | Pass | Unblocked toilwt and replaced inlet valve
MSA-DCA | WA3418152 | Plant room, Pump Room - Heating water pump 1 fault | Collection and Research Centre Welshpool | GMP-BR | Mechanical Services | Pumps (MS) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 16:30:00 | Pass | Attended site 1430. HWP1 servicing CRC to have excessive noise. Applied tests and checks to find rubbers and couplings U/S. Removed defective rubbers and couplings and replaced new rubbers and couplings. Aligned shafts to couplings and tested operation. System operating correctly. Left site 1630.
MSA-DCS | WA3417636 | Gutter at the front of stores leaking | Karnet Prison Farm | GMP-BR- HO | Roofing | Guttering (RF) | AFD Contracting | 3 | CLOSE | 24 Jun 2020 | 2020-06-30 17:00:00 | 2020-08-06 13:30:00 | Fail | 25/06/20Inspect leaking gutter.Measure for replacement.Join in gutter has broken apart due to gutter rusted out.Upon inspection, was noted that 21m of gutter is rusted out.Daryl Harries (Karnet) from maintenance was shown 21m of rusted gutter.05/08/20 to 06/08/20Remove and replace 21m of gutters to stores
MSA-DCS | WA3417639 | Unit 2, Cell 21 - light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 15:00:00 | Pass | Investigate and repair unit 2 cell light
MSA-DCS | WA3417673 | Unit 14, B & D, Cell B10- Leaking tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 09:00:00 | Pass | Replaced leaking basin spindle.
MSA-DCS | WA3417693 | Unit 14, C Wing- Cell C13- Clogged shower drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-26 10:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3417696 | Unit 14, A Wing, Cell A1- Leaking sink tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-26 11:00:00 | Pass | Replaced leaking spindle in basin tap.
MSA-DCS | WA3417705 | Kitchen - brat pan will not tilt | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 24 Jun 2020 | 2020-06-25 08:11:40 | 2020-06-24 16:30:00 | Pass | 24/06/2020Called as requested to the bratt pan not tilting. Found the up/down switch not operating correctly due to cockroaches so use the spare set of contacts on the switch tested all ok. If fault occurs again then a new switch will be required.
MSA-DCS | WA3417713 | CCU (11), D Wing, Cell D6- Toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-03 10:00:00 | Fail | Investigated toilet. Removed toilet. Cleared blockage from inside stainless pan. Reinstalled pan. Tested flushing. Sealed with sikaflex.
MSA-DCS | WA3417720 | Unit 13, D Wing, Cell D12- Toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-25 12:00:00 | Pass | Used acid and plunger to clear food scraps blockage from blocked toilet, shower and basin.
MSA-DCS | WA3417729 | Unit 6, B Wing, Cell B2- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-03 12:00:00 | Fail | Plunged basin to clear blockage caused by food scraps.
MSA-DCS | WA3417739 | Unit 2, D Wing, Cell D7- Window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-01 16:00:00 | Pass | REPAIRED / RESET SASHES
MSA-DCS | WA3417750 | Hakea Stores, female toilet- Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-25 15:00:00 | Pass | Repaired light.
MSA-DCS | WA3417756 | Unit 7, Cells E6 - E11 - Cell lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-25 12:30:00 | Pass | Replaced fuse
MSA-DCS | WA3417760 | Justice Club, No hot water in kitchen, toilets & bar | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Jun 2020 | 2020-06-25 08:40:59 | 2020-06-24 11:48:00 | Pass | Checked and tested hot water to kitchen and showers all working ok.
MSA-DCS | WA3417793 | Reception cameras 1and 2 failed | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-15 18:40:00 | Fail | installed cameras onto new ceiling, ran new 15M fig 8 cable for power.programmed cameras into Indigo system.checked live view and recorded footage.
MSA-DCS | WA3417797 | Reception - PIR failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-26 10:30:00 | Pass | PIR damaged due to water ingress. Removed and replaced with PIR from site stock.
MSA-DCS | WA3417798 | Court services PC crashed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-24 14:30:00 | Pass | WA3417798Installed new workstation and monitors. Setup to run Indigo CCTV software and Cardax access control/security software. Tested ok. Parts used:27 inch monitor from SEME stock Wireless Keyboard and mouse from SEME stockPC from SEME stock
MSA-DCS | WA3417799 | Education reed switch tampered | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-25 16:30:00 | Pass | Removed door from its hinges so the reed switch magnet could be retrieved. Secured magnet, hung door, tested ok.
MSA-DCS | WA3417906 | Unit 4, A11 - Toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-30 10:00:00 | Fail | Plunged toilet to clear blockage. Tested
MSA-DCS | WA3417911 | The Potato rumbler on the left has a leaking pipe underneath the base of the machine | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 16:00:00 | Pass | Investigated water leak. Collected parts and repaired broken drain.
MSA-DCS | WA3417927 | Unit 7, A & B Wing- Air Con heating is not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-26 15:28:00 | Pass | HVAC system is running as design
MSA-DCS | WA3417943 | Unit 7 (SCU), A&B wing plantroom , no power to switchboard . | Casuarina Prison | GMP-BR- HO | Electrical | Distribution Board (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-24 16:00:00 | Pass | Investigated and repaired power loss to unit 7 a/b switch board. Site stock switch board parts used.
MSA-DCS | WA3417947 | Boilerhouse- Boiler No 3- Air pressure/flame scanner fault | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 24 Jun 2020 | 2020-06-25 10:24:01 | 2020-06-30 10:30:00 | Fail | Supply and install new relays and bases for boiler #3.Attended site to investigate Air pressure/flame scanner fault on Boiler No 3.
MSA-DCS | WA3417949 | Yeeda, C Wing (entrance)- Air Con appears to have no power | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-06 09:30:00 | Fail | Complete
MSA-DCS | WA3417954 | Yeeda, Cell B07- Toilet solonoid constantly running | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-25 12:15:00 | Pass | Replaced faulty solenoid
MSA-DCS | WA3417965 | Adjacent to room 1 Education- Fire cupboard doorlock & hinges need repair | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-02 10:45:00 | Fail | View door require parts.Replace rusted hinges, service lock and replace bolt throw
MSA-DCS | WA3417970 | MPU camera 108 not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-15 18:41:00 | Fail | installed new Axis vandal corner mount camera, Axis PoE injector and 48vdc PSU from seme stockran new Cat6 cable from communications cupboard to OBS cell 2 (Camera 108)terminated and programmed camera. Checked cameras recording and live view.*** please note signs of rodents in MPU roofspace, coax cable for 108 has bite marks, have notifed Facilities manager at WKRP. ***
MSA-DCS | WA3417983 | Unit 4, Cell D1- Viewing hatch cover damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 13:30:00 | Pass | repair framework. replace sliding hatch cover
MSA-DCS | WA3417999 | Gatehouse, Front gate lock is faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-20 15:00:00 | Fail | Open jammed lock and replace bolt throw.Replace lock and lever pack.
MSA-DCS | WA3418019 | Unit 13, Cell D12- Toilet is blocked, overflowing & smells bad | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 12:00:00 | Pass | Removed plates from toilet. Plunged toilet to clear blockage.
MSA-DCS | WA3418104 | Front gate desk - visitors camera not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Jun 2020 | 2020-06-24 16:20:56 | 2020-06-25 08:05:00 | Fail | Front Desks box type axis camera belongs to IT Dept. not part of security systems on site.
MSA-DCS | WA3418147 | Unit 2, Day Room, A & B side over the stairs - Roof leak | Bandyup Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-08 11:30:00 | Fail | REPAIRED ROOF SHEETING AND FLASHING - SEALED
MSA-DCS | WA3418166 | Kitchen, Combitherm Oven- Oven Not Producing Steam | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 14:15:00 | Pass | Turned on main supply tap
MSA-DCS | WA3418167 | Laundry, washing machine No 4 - Won’t turn or spin | Hakea Prison | SPA-BR | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 24 Jun 2020 | 2020-06-25 13:03:02 | 2020-07-20 14:20:00 | Fail | BRAF required to complete work
MSA-DCS | WA3418206 | Zone 1 Cowling continual activation | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Jun 2020 | 2020-06-24 17:37:04 | 2020-10-09 12:04:00 | Fail | power-cycled controller and calibrated zone
MSA-DCS | WA3418244 | Front gate - locker 137 lock does not work | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 24 Jun 2020 | 2020-06-25 14:19:35 | 2020-06-25 09:00:00 | Pass | Serviced locker and ensured proper operation
MSA-DCS | WA3418304 | visits centre (inside) - broken window front south west bottom panel and | Bandyup Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 24 Jun 2020 | 2020-06-25 15:13:30 | 2020-06-25 11:00:00 | Pass | BROKEN GLASS REMOVED & REPLACED
MSA-DCS | WA3418339 | A,B,C, Wings Loss of power | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 24 Jun 2020 | 2020-06-24 19:56:18 | 2020-06-25 11:30:00 | Fail | Blown fuse
MSA-DCS | WA3418381 | Wooroloo Prison Farm | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 24 Jun 2020 | 2020-06-24 22:58:17 | 2020-06-24 22:30:00 | Pass | 24.06.20CHcalled out for fire tanks over flowingarrived onsite and flushed out infill valve and got it to stop fillingtanks still draining excess water thru over flow, will stop once at correct levelprison staff asked me to take off 003 locks on both ladders as they were not prison issue locks and they don’t have keysgot MAF signed and uploaded in documents
MSA-DCS | WA3418397 | Main Honeywell system is not recording in on the monitors. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Jun 2020 | 2020-06-25 00:20:55 | 2020-07-01 15:24:00 | Fail | CCTV issues after generator tests. Reinitialised servers, repaired synchronisation faults with DVM databases.Tested OKJob Complete
MSA-DFES | WA3417769 | G Floor - Stair 3 door not buzzing or latching properly. | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-25 11:30:00 | Pass | 25/6/20 - Dylan Parslow, Dean Simpson, Joshua ParkInvestigated issues with stairwell 3 ground door.Found lock not lining up with frame properly.Door requires adjustment.
MSA-DFES | WA3417788 | Engine Room Doors 1, 2, 3 & 4- Low voltage flexi cords damaged | CFRS Duncraig | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-08-26 13:30:00 | Fail | Following our service call on 30/06/2020 to the Engine Room Roller Shutters, W2272, and W22174 & W22173 located at the above site, it has been reported that the existing bungi cords are damaged and will require replacement to restore and maintain safe and reliable door operation.Technician attended the site of Duncraig Fire Station to the Engine Room Door on 30/06/2020. Following a full test and inspection of door components found fault to be site bungi cords to 3 doors are in poor condition. Required to quote to supply and install new bungi cords. Noted cord to door 1 has been replaced and require to source new cords the same. Technician returned on site on 26/08/2020 and completed quoted works. Full test and inspection of door function completed prior to leaving site. This quote includes:"Removal of the existing components."Supply and installation of 3 x new replacement bungi cords "Test and check door operation."The above work is to be carried out during norm
MSA-DFES | WA3418014 | Fire alarm system not working (see notes) | Fleet Management Services - O'Connor Workshop | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 24 Jun 2020 | 2020-06-24 15:20:08 | 2020-06-24 16:00:00 | Fail | investigate redback - system not operatingAppears to be hardware fault - further investigation required
MSA-DFES | WA3418280 | Rear door next to alfresco area - lock is faulty - cannot securely lock | CFRS Vincent | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 24 Jun 2020 | 2020-06-24 18:43:14 | 2020-06-24 16:25:00 | Pass | Replace broken digital code pad to rear door
MSA-DFES | WA3418348 | Toilets 1, wont flush (in double dorm) | Kensington (old) | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 24 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-25 07:45:00 | Pass | Investigate toilet not flushing located double dorm Isolate water and remove old inlet valve and old outlet washer Supply and install new performa inlet valve and caroma outlet washer Turn water main on and test operation/check for leaks Pack up and clean up worksite
MSA-DTAG | WA3417662 | Custody holdings cell 4 - holes to be patched & repainted- see below information | Joondalup Courthouse | GMP-BR-HO | Painting | Internal (PA) | PPM Project Painting & Maintenance | 3 | CLOSE | 24 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-30 16:59:00 | Pass | Patch and paint damaged walls
MSA-DTAG | WA3418054 | Hearing Room 2.02 - Faulty Paddle | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-25 12:30:00 | Pass | Job completed - Attended site. Replaced faulty egress switch on Level 2 Door 2.02 Public.
MSA-DTAG | WA3418117 | Mutiple faulty lights needing repairs/replacements (see notes) | Rockingham Justice Complex | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-01 07:45:00 | Pass | Inspected lighting and replaced faulty fittings and blown tubes and pl lamps
MSA-DTAG | WA3418298 | G, custody - Special clean for cell 1 due PIC spitting on the floor/door & also threw food around | Midland Courthouse | WSM-BR-SITE | Cleaning | Cleaning (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 24 Jun 2020 | 2020-06-25 17:00:00 | 2020-06-24 19:00:00 | Pass | P1 Completed
MSA-DTWD | WA3417844 | B Block, level 2, (Male Toilets near TIWA) - Replace/repair flush buttons | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-01 15:30:00 | Pass | COMPLETED
MSA-DTWD | WA3417862 | Block 1, ground, room 1G10 - faulty locks | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 15:45:00 | Pass | Block 1 - Room 1G-10 faulty door locks.Locks repaired.
MSA-DTWD | WA3417898 | A Block, Roof Void- Possibly possum in roof space | Mandurah Campus (formerly Peel) | GMP-BR | Pest Control | General Pest (PC) | Allpest WA | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-08 10:00:00 | Fail | removed possum from trap, applied d Ter to buildings where possums travel ie down pipes, metal grates
MSA-DTWD | WA3417909 | D Block Carpark area- Wire boundary fencing fallen down | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-29 11:00:00 | Fail | Replaced damaged wire and retensioned fence- Installed 7 spiggots to base of badly corroded posts
MSA-DTWD | WA3417980 | Graffiti needs removing from areas near A Block | Fremantle Campus (formerly WA Maritime) | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 24 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-26 14:00:00 | Pass | REMOVAL OF GRAFFITI FROM AREAS NEAR A BLOCKS
MSA-DTWD | WA3418045 | Room B1 - broken lock, the door to the retail sales area | Murdoch Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-29 14:00:00 | Pass | Repairs to handle
MSA-DTWD | WA3418178 | Francis st foyer - Repair/replace lighting as required | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-08-26 10:00:00 | Fail | Completed jsa, set up work area , changed tubes and starters (2x36w tubes 2x s10 starters 2x18w tubes 2xs2 starters ) , packed up work area , lights to staff toilets now operational, light in staff room s-216 is operational.Attended site, replaced pole top and cabling to light on museum st, also inspected fuses in switchboard for east stairwell. 26/08/20
MSA-DTWD | WA3418193 | E Block- E63 BISTRO – Possible V.S.D issue with the aircon fan | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-06 15:00:00 | Fail | sub contractor attended site and found pc board on vsd defective. replaced with new pc board from stock unit now running correctly
MSA-DTWD | WA3418286 | Tower Block, G Floor - Disabled toilet door motor is making noise | West One Services | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 15:53:00 | Pass | On inspection, found unit working in good condition.Unknown noise coming from light or ceiling.Unit all ok.
MSA-DTWD | WA3418343 | Tower block, ground floor - diable toilet - faulty buzzing light fitting | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 11:15:00 | Pass | Attended site and signed in. Located faulty lights through out, replaced and lamps as required. Isolate redundant control gear in disabled toilet light. Tested all okay. Job complete
MSA-MRWA | WA3417989 | External pedestrian gate - mag lock malfunctioning, please investigate and remediate | Traffic Operations Centre | GMP-BR | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 24 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-24 15:48:00 | Pass | Found gate opening and closing ok but maglock to not be holding gate. Checked maglock supply and found no power coming from security access system. Relay in control box switching mag power working correctly.Security tech required to resolve.
MSA-DCA | WA3419026 | Emergency door in the bottom workshop is not functioning properly, bottom pin is not dropping. | Short Street Theatre-Main Building-Mezzanine-Workshop | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 15:00:00 | Pass | Adjusted panic bar mechanism so that it latches correctly
MSA-DCA | WA3419216 | 3x roof leaks adjacent to cooling towers | Art Gallery of WA - James St-Main Building (Block B)-Level 5 - Roof-Rooftop Plant - External Area | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-26 11:30:00 | Fail | Leak repaired and confirmed with site
MSA-DCA | WA3419220 | Urinal is leaking, near recepiton | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-AG.19 - Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 13:05:00 | Pass | Unblocked badly blocked urinal. Not enough water flow coming from the solenoid valve due to the faulty control box.
MSA-DCS | WA3418498 | Unit 4, A Wing, Cell A13- Judas hatch is jammed, unable to be opened | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 25 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-25 12:00:00 | Pass | Adjusted hatch, refit new lock
MSA-DCS | WA3418499 | Unit 4, Cell C2- Window frame broken, glass is loose | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 07:31:10 | 2020-06-26 10:30:00 | Fail | RENEW SASH TO WINDOW
MSA-DCS | WA3418502 | Visits Area- Prisoner side of Non Contact Booth room 7 the light is not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-29 10:00:00 | Pass | Repaired faulty lights in visits room 7
MSA-DCS | WA3418543 | INF (10), Cell C1- Shower in cell is flooding the floor and out into the wing. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 15:00:00 | Pass | Investigated cause of blockage in shower. Water pressure too high. Parts collected and installed. Water pressure adjusted.
MSA-DCS | WA3418549 | Entry Pod- Fire alarm fault, has been isolated | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 07:54:06 | 2020-06-25 11:33:00 | Pass | Attended site and found Unit 4 K block to have low flow cleared pipes and normalised.Reset and left normal.
MSA-DCS | WA3418570 | Admin- Keywatcher laptop in both security and the front gate won't sync with the databases. | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 07:36:49 | 2020-06-25 15:58:00 | Pass | Sourced parts, attended site, investigated fault. Found database corrupt/faulty. Sourced software to unlock database. Repaired database. Performed backups and tested OK.Job CompleteParts (SEME Stock):Software Update
MSA-DCS | WA3418677 | Front gate - Xray Machine - Blue search random light faulty | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 08:36:24 | 2020-06-25 12:30:00 | Pass | Attended site to reset the random search strobe output on Maxpro. Tested it ok after.
MSA-DCS | WA3418683 | WWTP screening pit pump tripping RCD | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-17 15:00:00 | Fail | Investigate wwtp screening pit pump. Pump is faulty. Remove pump for assessment.Source new pump.Replace WWTP screening pit pump.
MSA-DCS | WA3418738 | Admissions, Hallway/chaplains office- Air Con unit constantly trips | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-21 10:15:00 | Fail | Complete
MSA-DCS | WA3418751 | Fix WKRP OT lightning protection | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-25 19:00:00 | Pass | Removed and replaced lightning arrestors in EC2, EC5 and EC7.
MSA-DCS | WA3418753 | NUR 5 disk fault | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-25 21:00:00 | Pass | Removed and replaced faulty hard drive. Tested ok.
MSA-DCS | WA3418754 | SQL server memory low | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-25 22:15:00 | Pass | SQL express server memory alarm activating every hour on the Gallagher, located source of alarm, 10GB of event data.perfromed archive of the system to events older than 90days. Database still 10GB, Contacted Gallagher technical support, attempted to use GallagherShrink.EXE. Unsuccessful.opened command prompt and cleared event data under direction of Gallagher.purged files and restarted Gallagher services.checked all systems and confirmed correct operation
MSA-DCS | WA3418756 | DCP lagging | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-26 14:48:00 | Pass | Unistalled Gallagher and re installed.Monitored workstation,Mini dump file has not reappeared
MSA-DCS | WA3418759 | MWH 3 x OT alarms | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-26 09:00:00 | Pass | Checked microwave power and alignment. Reset transmitter and receiver units. Walk tested and plotted Omnitrax zone. Tested ok.
MSA-DCS | WA3418762 | Gatehouse RS fault | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-25 22:30:00 | Pass | Replaced reed switch magnet in the door. Tested ok.
MSA-DCS | WA3418763 | Comms room alarm | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-25 22:21:00 | Pass | Audible alarm on the CellGuard system, traced fault to CI-Hub offline, found Power card not seated correctly in CI-Hub.re-seated and cleared CellGuard system, no faults on system
MSA-DCS | WA3418767 | Zone 23 false alarm | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-26 15:00:00 | Pass | Cleared away loose rubbish. Microwaves and beam sets checked for power and alignment. Tested ok.
MSA-DCS | WA3418768 | EC 3 alarming | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-26 14:50:00 | Pass | Cleared controllers clutter and buffer,Tested controller and inputs all working
MSA-DCS | WA3418816 | Unit 8, Cell D6- Ceiling light is damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 09:30:00 | Pass | Repaired light
MSA-DCS | WA3418817 | Unit 7, Cell S10- Ceiling light is damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 10:30:00 | Pass | Repaired light
MSA-DCS | WA3418827 | Unit 9, C Wing showers- Drain of shower closest to the grille require drain unblocking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 10:40:00 | Pass | Cleared blocked shower.
MSA-DCS | WA3418828 | Unit 7, Cell S6- Toilet cistern needs repair constantly running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-25 12:38:00 | Pass | Pulled apart cistern replaced outlet washer
MSA-DCS | WA3418833 | House 2, Unit 5- Water leak from mains | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 10:03:20 | 2020-06-25 14:40:00 | Pass | COMPLETED
MSA-DCS | WA3418836 | Unit 8, Cell 10- Toilet is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-25 13:29:00 | Pass | Pulled apart cistern replaced outlet washer
MSA-DCS | WA3418837 | Unit 7, Cell E3- Toilet is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-25 14:20:00 | Pass | Pulled apart cistern replaced outlet washer
MSA-DCS | WA3418847 | Unit 9, Cell D7- Sink is blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-25 15:10:00 | Pass | Unblocked basin with plunger
MSA-DCS | WA3418851 | Unit 9, Cell D12- Drain on floor near toilet overflows water to the floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 11:30:00 | Pass | Cleared blocked floor drain
MSA-DCS | WA3418867 | Unit 1, Block 3 - Ceiling fans in ablutions are not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 09:30:00 | Pass | Replaced toilet fan sensor
MSA-DCS | WA3418931 | Fault with keywatcher- Please speak with Patrick before attendance | Melaleuca Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-01 11:15:00 | Pass | removed 3 board 8 slot & replaced with 16 slot. programmed box for extra slots & moved numbering. tested operation & all ok. handed fobs & O-rings to Natasha Watterson
MSA-DCS | WA3418946 | Garments, Workshop- Prisoner toilet cistern is leaking badly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 13:00:00 | Pass | Replaced leaking section of 20mm copper pipe in plumbing duct.
MSA-DCS | WA3419036 | Kitchen - Mid Size Kettle Boiler, Tilting Mechanism faulty | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 13:50:00 | Pass | Cleaned & greased, tested ok
MSA-DCS | WA3419040 | Unit 6, A11 - GPO broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-25 14:00:00 | Pass | Replaced light switch
MSA-DCS | WA3419098 | gate house, visits internal 2 camera - not working | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 25 Jun 2020 | 2020-06-25 16:28:22 | 2020-06-25 16:30:00 | Fail | Attended site - Camera 2 Internal lost IP address, reset & reprogrammed camera. Tested OK. Job completed
MSA-DCS | WA3419122 | gate house - Zone 9 camera 1, Zone 12 camera 1 - water in camera housing | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2021-06-03 16:00:00 | Fail | Inspected both housings. Both have been replaced and there is no evidence of water ingress. Both camera appear bright and clear at the gatehouse.
MSA-DCS | WA3419186 | Unit 4, Court Yard- external lights timer faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-10 12:00:00 | Fail | Repaired multiple faulty external lights in unit 4
MSA-DCS | WA3419200 | Unit 4, Cell B10- Window spirals not working | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 11:30:00 | Pass | REPAIRED FRAMEWORK, BALANCES AND REPLACED PARTS
MSA-DCS | WA3419201 | Unit 4 - D Wing- Shower door broken off hinges. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-28 15:00:00 | Fail | NEW HINGES FITTED
MSA-DCS | WA3419243 | Unit 9, A Wing- Grille lock broken | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | AAA Ability Locksmiths | 0 | CLOSE | 25 Jun 2020 | 2020-06-25 17:40:03 | 2020-06-25 14:45:00 | Pass | Repaired lock on grille as required.
MSA-DCS | WA3419332 | waste water chlorine plant not dosing correctly | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 11:13:00 | Pass | Changed out 2 x empty 70kg chlorine bottles. Recalibrated Analyser
MSA-DCS | WA3423073 | Unit 1 A Wing Assess damage & make safe - retrospective work order | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Jun 2020 | 2020-06-25 20:45:00 | 2020-06-30 16:15:00 | Fail | Checked wiring configuration at the CI8 in U2 store room. Repair the backing box in cell A01. Installed new intercom. Tested loud and clear in the cell and in control. Parts used:Cell Guard CI-CC/270/120Wiring adapter Consumables
MSA-DCS | WA3423081 | Unit 1 A Wing Assess damage & make safe - retrospective work order | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 25 Jun 2020 | 2020-06-25 20:45:00 | 2020-06-25 18:30:00 | Pass | Made safe vandalised basin and toilet
MSA-DCS | WA3423133 | Unit 1 A Wing Assess damage & make safe - retrospective work order | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 25 Jun 2020 | 2020-06-25 20:45:00 | 2020-06-25 21:00:00 | Fail | 23.06.2020Hakea PrisonArrived on site for call out due to riotsWas informed we could not enter due to the area being a crime sceneChecked fire pumps before we left all fine they hadn’t been running24.06.2020 Unit 1Attended site for fire alarm check vesda all working fine. Will need to return Monday with 16 vesda sampling points and go through and swap burnt ones out and clean pipe in a wing unit 1. All sitting normal when left29/6/20 KS JNReturned to site to replace all sample points in unit 1 A wing after many damaged during riots.Replaced all 16 sample points with new and checked airflow ok.
MSA-DCS | WA3423145 | Unit 1 A Wing Assess damage & make safe - retrospective work order | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 25 Jun 2020 | 2020-06-25 20:45:00 | 2020-06-29 10:30:00 | Fail | Repaired U1 damaged
MSA-DCS | WA3425882 | Retrospective work order-Unit 1 A Wing asses damage, make safe and repair once access allowed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 25 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-03 15:35:00 | Fail | Reinstalled new stainless steel basin and adjust waste/ pipework in duct
MSA-DCS | WA3425902 | Unit 1, A Wing assess damage, make safe and repair once access allowed | Hakea Prison | GMP-BR-RC | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 25 Jun 2020 | 2020-07-01 17:00:00 | 2020-10-19 13:56:00 | Fail | MAJOR WORKS COMPLETED FOR MINI RIOT. INCLUDING CLEANING, REPAIRS TO CELLS DOORS
MSA-DFES | WA3418477 | Security system does not automatically switch to away when the DDL status is switched to off station | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 25 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 08:20:00 | Pass | Reenabled keyswitch remote arming
MSA-DFES | WA3418651 | Main sliding door, between room 15 & outside ares 52- not functioning | CFRS Perth | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-25 11:00:00 | Pass | Attend and sign inKitchen sliding doorsPelmet and rollers systemLHS door has dropped and not able to slide correctlyRemoved pelmet coverPack up doorAdjust roller tighten bolt and nutDoor working correctlyCheck and test other doorRe fit cover pieceClean up
MSA-DFES | WA3418739 | Ground Floor - Repair/replace faulty external security & walkway lights, approx 6 not working | CFRS Duncraig | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-22 16:45:00 | Fail | Arrived onsite and signed in at 1330Located 7 faulty lights, will need to get approval to swap for new leds as site has requested them.Notified staff of works and signed out and left site at 1400Complete
MSA-DFES | WA3418746 | FF 1 dorm ensuite- Broken wall tiles & missing grout around base of shower recess | CFRS Duncraig | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-08-06 13:30:00 | Fail | Broken wall tiles & missing grout around base of shower and re tile and regrout Assessed job Picked up gear for job 25/7/20Back to site removed tiles also cracked grout.Cut tiles to size, Glued in place & grouted off. Cleaned up.
MSA-DFES | WA3419371 | Front N/E #2 Sectional Door it comes half way down and then goes back up | CFRS Wangara | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 11:00:00 | Pass | 26/06/2020. Following full test and inspection of door components identified fault was a set of safety beams was set to be out of alignment.Adjusted these & tested operation a few times without an issue before station. The issue has been resolved.
MSA-DTAG | WA3418707 | Main Foyer & by security desk - Switches for light switch fallen in, light switch shocking people | Perth Children's Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 08:30:00 | Pass | Job complete
MSA-DTAG | WA3418951 | Level 1, Female staff toilet - Blockage in the female staff toilet | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 11:00:00 | Pass | cleared blockage in main sewer line.
MSA-DTAG | WA3418978 | Ground level kitchen - Water leak under water to water filter | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-25 15:05:00 | Pass | Single filter housing was leaking on arrival. Replaced leaking housing with a new Capex Asset SN A402011579 Maxi flow system and fittings inc new PLV .Removed old housing and Flushed filter. Checked under pressure. Normal operation
MSA-DTAG | WA3418986 | Staff on Lvl 22 have lost 24/7 access & plus certain doors on level 23 and other outstanding issues | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-25 13:45:00 | Pass | Job completed - Attended site. Saw Corbin on Level 31. Went through Door Groups and Access Level.
MSA-DTAG | WA3419083 | rear car park - Rear Gate sagging as if the hinges aren’t in line anymore | Perth Children's Court | GMP-BR-HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 12:15:00 | Pass | Realigned rear car park gate
MSA-DTWD | WA3418508 | A Block , Room A338 repair small damaged entry wall from shelving removal,patch & paint | East Perth Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 25 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-26 15:30:00 | Pass | Repaired and painted walls
MSA-DTWD | WA3418530 | A Block, A338 - Air Con vent is damaged | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 25 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-15 14:01:00 | Fail | Found grilles damaged due to age and wear and tear.Ordered new grilles to replace old grilles as per request.Replaced grilles onsite.
MSA-DTWD | WA3418579 | A block East- Male toilet A028 right hand basin requires repairs to waste pipe | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 10:03:00 | Pass | COMPLETED
MSA-DTWD | WA3418832 | K block, Canteen - MID-Leaking hot water pipe at the rear of the Canteen | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 25 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 09:30:00 | Pass | Replaced corroded and leaking pipework
MSA-DTWD | WA3418887 | Admin block - Staff office block. Smell coming from floor waste, possible broken pipe below ground | Clarkson Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 15:30:00 | Pass | COMPLETED
MSA-DTWD | WA3418892 | C block. Second floor female toilet. First stool on left is leaking | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-30 10:02:00 | Pass | COMPLETED
MSA-DTWD | WA3418968 | Q block, Level 1- Area is cold | Joondalup McLarty Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-01 15:15:00 | Fail | Disconnected the old actuator from the housing and installed the new one, tightened accordingly on the shaft. Rewired the new actuator the same as the existing one and checked for correct operation. Found that both heating water valves were opening and closing together. Both CHWV's were operating OK, both were closed whilist the HWV's were open in heating mode. Pump 2 and reverse cycle chiller both ran up OK.
MSA-DTWD | WA3419058 | Centre Block - Lift car 5 - Front panel not working, side panel ok | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | CLOSE | 25 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-25 14:54:00 | Pass | JOB COMPLETED - On arrival lift 5 COP wasn’t responding and wasn’t transmitting calls to lift. Removed cover and disconnected card and cycled the power to reset the card. Reconnected card and put lift back in service.
MSA-DTWD | WA3419146 | E Block, Room E617- men's toilet, 4th cubicle blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 13:15:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3419265 | A block, A12 - kitchen sink is blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 12:00:00 | Pass | Cleared blockage using plunger and drain machine
MSA-DTWD | WA3419321 | N Block, Room N108 - drain is flooding back into lab | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 25 Jun 2020 | 2020-06-25 18:23:23 | 2020-06-26 12:45:00 | Fail | COMPLETED
MSA-MRWA | WA3419104 | Eastern carpark adjacent motorcycle bays - 2x new LED carpark lights not working | Don Aitken Centre MRWA Head Office | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 25 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 15:45:00 | Pass | Switched on breaker and relabelled
MSA-DCS | WA3422792 | Dining Room- bain marie - light not dimming | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 11:00:00 | Pass | Steam rising from under the trays is causing the utensils to get hot , not the lights .Kitchen staff are aware of this and will address the situation.
MSA-DCS | WA3422823 | Jeelia, Cell B6- Bedside light not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 10:00:00 | Pass | Replaced push button switch and lamp in bedside light. Test ran ok.
MSA-DCS | WA3422840 | Front Gate, Front Door- Intercom muffled | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-26 14:30:00 | Pass | Attended site. Found Front Gate House Door intercom muffled. Reset Intercom and turned down microphone levels.Tested intercom, all OK. Tested other intercoms, call OK. Job completed.
MSA-DCS | WA3422850 | CCU (11), Cell D8- toilet float sticking & constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-03 15:00:00 | Pass | Replaced worn outlet rubber in cistern.
MSA-DCS | WA3422863 | O D P - Control Room Door leading into Education cannot be opened. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 26 Jun 2020 | 2020-06-27 10:13:46 | 2020-08-07 10:00:00 | Fail | Open jammed lock, attempt repair, unable to repair due to wear. Obtain spare lock from Security, install lock, adjust strike and escutcheon.Supply replacement lock to Security.
MSA-DCS | WA3422867 | Unit 1, C wing the middle shower doesn’t receive any warm and/or hot warm water.- | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-06-29 15:00:00 | Pass | Realigned tap set and installed new connector pin.
MSA-DCS | WA3422870 | Lines running through visits 3 display, need to change with the visits 2 camera | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Jun 2020 | 2020-06-27 09:00:00 | 2020-06-26 13:00:00 | Pass | Job complete
MSA-DCS | WA3422873 | Unit 1, C6 - main lock broken, prison locked in | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 26 Jun 2020 | 2020-06-26 13:50:00 | 2020-07-01 14:30:00 | Fail | Job completed - attended site urgently and gained entry to cell locked shit with prisoner inside, 01/07/2020 - supplied and installed new main cell lock
MSA-DCS | WA3422908 | Kitchen Fire Hose Leaking Above Coldroom | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-01 11:15:00 | Pass | COMPLETED
MSA-DCS | WA3422909 | Abattoir - Broken light in boning room | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-03 11:30:00 | Fail | Investigate abattoir boning room light. Light requires replacement.Replace broken light in abattoir.
MSA-DCS | WA3422915 | Transfer pump line leaking | Wooroloo Prison Farm | SPA-BR | Mechanical Services | Pumps (MS) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-08-14 12:00:00 | Fail | Transfer pump line leaking. Check pump & discharging line. Found leak from valve & inground below Sewerage plant. Dig up, leak found, pipe had been cut in two places by contractors. Repair cut pipe. Run pump, water not flowing to tank. Found more leaks under Control room in new Sewerage plant. Pick up pipe, connect to existing pipework outside fence, run new line around plant fence. Locate existing line on other side & connect. Run pump, still not reaching tank. Connect Orchard pump & test. Overhaul Transfer pump, fit new stator & pressure gauge. Replace leaking pipe between water meter & pumps shed. Test, pump water to inspection valve by gardens drain. Clear rubbish & dig to locate pipe from drain to fence line. Found leak in ground below oval. Run new pipe above ground to tennis court tank. Run pump, all working. Bury pipe where required. Transfer pump, check pipe and paint with sewerage pipe purple. Report to staff.APPROVED TO CARRY OUT ALL NECESSARY WORKS AS PER GRANT BYRNE
MSA-DCS | WA3422964 | Yeeda, large pole night light - broken on/off switch | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-01 10:00:00 | Pass | Replaced broken rotary switch with a new one . Note- this switch has been replaced with control from inside the office and now serves only to prevent access to the pole cabling.
MSA-DCS | WA3422966 | medical centre raw sewerage coming from toilets and sink and smell | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 26 Jun 2020 | 2020-06-27 10:55:49 | 2020-06-26 15:15:00 | Pass | COMPLETED
MSA-DCS | WA3422973 | ladies staff end toilet water on floor does not seem to come out of the toilet | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 08:30:00 | Pass | replaced rubber seal in flush pipe, which was causing water to run onto the floor
MSA-DCS | WA3422978 | Staff disable toilet taps often doesn’t turn off properly and drips or leaks. | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 08:45:00 | Pass | was talking to a staff member who said one of her collueges reported the issue but then realised she hadnt actually fully turned the lever tap off.
MSA-DCS | WA3422993 | conference room light not working | Midland (North East Metro) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 16:45:00 | Pass | Fitted new tubes to dull and failed lights , cleaned diffusers. Test ran ok.
MSA-DCS | WA3422998 | reception light cover near toilets is coming down | Midland (North East Metro) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 16:00:00 | Pass | Refitted diffuser to ceiling and realined the troffer light above so it is sitting on the frame correctly.
MSA-DCS | WA3423070 | Control Room - Cell call system- server and back up has failed | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jun 2020 | 2020-06-26 15:44:57 | 2020-07-10 15:48:00 | Fail | job to be invoiced at cost, new work order will be released.
MSA-DCS | WA3423141 | SOG base-Check rusted camera pole and bollard | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 17:00:00 | Pass | Supplied and installed new single head bollard. Cable damage apparent onexisting cabling within bollard. Removed old cable and installed new HBUS cable for reader, and trigger cable for gateand reed. Reterminated reed, trigger, and reader. Tested in full. Tested ok. Works Complete.
MSA-DCS | WA3423194 | Gate house, Keywatcher east box 1 - door tounge/latch is slightly loose and falling into recess | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 26 Jun 2020 | 2020-06-27 12:58:20 | 2020-07-14 12:00:00 | Fail | Remove lock, weld lock in workshop, install temp repaired lock.Replace lock.
MSA-DCS | WA3423209 | Kitchen, Oven 3 - part has fallen from the back | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 26 Jun 2020 | 2020-06-27 13:06:41 | 2020-06-26 16:10:00 | Pass | Reattach fan cover assy as required
MSA-DCS | WA3423225 | U6,7 & assessments - Exhaust fans not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-01 09:00:00 | Pass | Found several fans tripped on units due to electrical fault where building had lost 1 phase reset fan overloads once phase was fixed. Could not access unit 6 board due to operations in unit 6. Will reset on next attendance.Also found assessments aircon indoor fan tripped. Reset fan and tested operation. All ok.Reset all fans in unit 6 and tested ran operation. All ok.
MSA-DCS | WA3423232 | Unit 10, Cell A15- Taps continuously running water turned off in duct | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-08 08:12:00 | Fail | Replaced quarter turn tap
MSA-DCS | WA3423240 | U9 A10 leaking tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-08 09:14:00 | Fail | Pulled apart plug and waste Re-silicon
MSA-DCS | WA3423254 | Gatehouse Perimeter senstar Node 9 on perimeter in constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-02 08:45:00 | Fail | Removed faulty batteries in EC 2 and EC9Installed new 6v5.7Ahr battery in EC 2 and EC 9.load tested and confirmed alarm on EBI and Senstar.Alarm has cleared.
MSA-DCS | WA3423274 | control visits area CCTV monitor not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jun 2020 | 2020-06-26 17:27:19 | 2020-06-26 15:00:00 | Pass | Rectified and fixed cctv monitor, job completed.
MSA-DCS | WA3423340 | Clerical Area - Door relase push button onte working (However the door swipe is working.) | Walcott Centre (Central West Metro ) | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 14:15:00 | Pass | Clerical area door release intermittent. Replace button with new and test. ALL OK. Also test lock but OK. Advised to monitor but test OK at time of testing.
MSA-DCS | WA3423365 | West Admin - Superintendents office - air con not working in boardroom & supers end | Hakea Prison | GMP-BR- HO | Air Conditioning | Ducted Split System (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-30 12:30:00 | Pass | Found heater serving superintendents area not operating. Inspected inside roof and located heater. Found temp switch has tripped. Reset heater and tested operation. Monitored running current. All ok at time of departure.
MSA-DCS | WA3423369 | Unit 6, B Wing - Shower keeps running /cannot turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-03 13:00:00 | Pass | Replaced leaking spindle.
MSA-DCS | WA3423588 | unit 1 A1 Remove main lock from damaged cell door situated in cabinet shop | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-01 14:15:00 | Pass | job completed - removed lock from damaged cell door situated in cabinet shop, as requested
MSA-DCS | WA3423738 | rear sally port for industries - roller door has been hit by a truck. not operational | Hakea Prison | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 0 | CLOSE | 26 Jun 2020 | 2020-06-26 19:23:59 | 2020-06-30 08:00:00 | Fail | 26/06/20Unjammed door off wall, checked for damage. 6 roller door panels to be replaced. 1 weather strip to be replaced. R/H track to be reattached to wall.29/06/20Inspect roller door. Door was not as left on 26/06/20. Persons have tried to operate door and jammed braces under. Too unsafe to raise so repairs will be done as arranged tomorrow.30/06/20Raised roller door to safe height / isolated. Measured for manufacture of replacement of damaged section.
MSA-DCS | WA3423747 | Unit 9 network error on main intercom system | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jun 2020 | 2020-06-26 19:36:51 | 2020-06-26 18:45:00 | Pass | Investigated cell intercom network fault, repaired network faults, performed server backup, tested OK.Job CompleteParts (SEME Stock):Backup Hard Drive
MSA-DCS | WA3423756 | master control room fire monitor constant alarm-please call site asap | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 26 Jun 2020 | 2020-06-26 19:50:29 | 2020-06-26 19:19:00 | Pass | On attendance POD graphics displaying 118 faults relating to the Infirmary & visits area.Inspected both DGP’s in the Infirmary & visits(reception) area.Both panels operating correctly but it appears that cabling issues reside in both areas within the builders work space.No access to these areas at this point in time.Advised prison officers in the POD.Recommend corrective services engage the builder with ARA input for further fault finding to resolve issues.
MSA-DCS | WA3423779 | UNIT 16 - HOT WATER BOILERS ARE NOT IGNITING - RHEEM SYSTEM. | Casuarina Prison-Gatehouse | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 26 Jun 2020 | 2020-06-26 22:04:10 | 2020-06-26 21:20:00 | Pass | COMPLETED
MSA-DCS | WA3423788 | Fire alarm fault - Unit 1 - keeps beeping | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 26 Jun 2020 | 2020-06-27 22:06:08 | 2020-06-27 09:30:00 | Pass | System status displaying normal on departure
MSA-DCS | WA3423789 | Unit 1 Control room staff toilet - water leaking into light fitting. | Karnet Prison Farm-Prisoner Accommodation Huts Unit 1 | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 Jun 2020 | 2020-06-27 22:20:53 | 2020-07-17 12:30:00 | Fail | Investigate unit 1 control room staff toilet light. Remove light. Water leak needs to be repaired and ceiling assessed for replacement.Replace light in unit 1 staff toilet
MSA-DFES | WA3422740 | Drink fountain in engine bay leaking from spout | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 26 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-30 10:45:00 | Pass | Replaced peeking faucet installed new one
MSA-DFES | WA3422744 | Block 1, Room 21- Zip HydroTap | CFRS Wangara | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 26 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-03 10:36:00 | Fail | Replaced main power board and loom. Replaced John Guest fittings and tubing. replaced Zip Element , replaced probe hot tank kit, replaced 15amp fuse, replaced Zip Overload Kit
MSA-DFES | WA3422761 | Room 22 - Door locking mechanism in west Hygiene Showers broken. | CFRS Wangara | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 26 Jun 2020 | 2020-07-02 17:00:00 | 2020-08-19 13:02:00 | Fail | Arrived at site, inspected faulty door mech. Mortise was missing, station had spares. The lock system had a low voltage cable that linked multiple doors together so when one was locked the other door also locked automatically. When re-installing the mortise I copied the opposite door hoping they would sync together. But they did not, I was only getting a red flashing light and could not lock the door.**Door hardware is fitted and works but will not lock. Need an electric door type trade (automation/control). They will have to sync the doors up from a control panel***Engaged specialists - works as per docs attached
MSA-DFES | WA3422902 | Key FOB & Key pad controls are not working for the front automatic security gate | O'Connor Fleet Storage | GMP-BR | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 26 Jun 2020 | 2020-06-26 17:00:00 | 2020-06-26 15:45:00 | Pass | No Cost associated with this Job.It was not for Assa abloy and has now been passed to back to programmed to reissue it to the gate motor installers to repair the ground cable
MSA-DFES | WA3423103 | Ants on the floor at Female change room | DFES Cockburn Emergency Services Complex | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-03 11:15:00 | Pass | Carried out a service for ants at Cockburn Emergency Services Centre. There were reports of ants located in the female change rooms. Upon further inspection no active ants could be located. Residually Sprayed attrathor at ground level to the internal perimeter. As well as applying ant gel to cracks and crevices.
MSA-DFES | WA3423204 | L1 whole office Attend Office and inspect all Fluoro lights and replace where necessary | South Metro Regional Office | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-29 09:15:00 | Fail | Investigated all faulty light fittings on First floor at Dfes office. Will be compiling a quote and submitting for approval. Will return once approval is complete. There are 1 faulty in public room, 5 faulty in meeting room, 2 x faulty in hallway, 1 faulty in operations room, 2 faulty in staff room and 1 faulty in toilet entrance.
MSA-DTAG | WA3423015 | Ground level, Court 3 - Time delay lock is again faulty and not opening | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 26 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 15:30:00 | Pass | Attended site. Removed switch plate, reterminated, tested successfully multiple times.Whilst on site discovered Camera 123 Sally Port North not working. Tried to power with POE injector, failed to power up.Recommend replacing.Job completed.
MSA-DTAG | WA3423754 | 1987 building - Level 4 or Level 1 Plant room or FIB fire panel fault | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 26 Jun 2020 | 2020-06-26 19:37:55 | 2020-06-26 17:19:00 | Pass | Attended site & replaced dirty smoke detector in plant rm 3 zone 18 L1S93 sheriffs office.System status displaying normal on departure
MSA-DTAG | WA3423765 | Ground level - there is a water leak in cleaners room . | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 26 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-29 09:25:00 | Pass | COMPLETED
MSA-DTWD | WA3422758 | A Block, Room AG26 Female toilets- Blocked toilet | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 26 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-26 14:04:00 | Pass | Unblock toilet
MSA-DTWD | WA3422875 | G block ground G129 male toilets 2nd and 3rd cubicles blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 26 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 14:00:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3422876 | Block 6 - 2 x 32amp faulty power points in Polishing Room | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-06-30 14:33:00 | Pass | Repalced faulty 3phase outlet in polishing room as shown by site. Job completed
MSA-DTWD | WA3422879 | Block 6, Metal Fab 2- Faulty suspended power point over Plasma Cutter | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-15 12:05:00 | Fail | Relocated faulty 3phase gpo .job completed
MSA-DTWD | WA3422883 | E block male toilets 2 cubicles blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 26 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 12:30:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3422885 | Block 6, Metal Fab 2- 3 x 32amp faulty plugs for welders | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-06-30 12:00:00 | Pass | Replaced 3x faulty 3phase plugs as shown by site. Job completed
MSA-DTWD | WA3422887 | Block 1, Alarm panel reading fault (advised by Education Security) | Thornlie Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 1 | CLOSE | 26 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 14:22:00 | Pass | Reset alarm system dialler & reprogrammed in Education Security receiver numbers
MSA-DTWD | WA3422894 | Block 3- Toilet leaking water onto floor in disabled male cubical | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-06-29 11:14:00 | Pass | Fixed leaking toilet
MSA-DTWD | WA3422898 | Block 10 - Faulty lights from Block 10 to carpark near staircase | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 26 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-26 16:15:00 | Pass | Attended site and signed in. Located block 10 lights and tested. Found timer 1 hour out. Tested function of on and off. All okay. Reset timer and checked all lights all okay. Job complete
MSA-DTWD | WA3422919 | E block, E300 Automotive - Hoist No3 (Molnar) has broken the right rear locking mechanism on the arm | Midland Campus | GMP-BR | Lifts | Vehicle hoists (LI) | SPECIALISED LIFTING SERVICE | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-01 10:00:00 | Pass | NEW WORK ORDER ISSUED FOR REPAIR AS WAS OVER LIMIT
MSA-DTWD | WA3422947 | A Block, Ground West End Female 2nd cubicle leaking | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 16:30:00 | Pass | replaced faulty inlet valve in cistern
MSA-DTWD | WA3422981 | P block, P003, level 1 - Dead rodent in room. Issue with copious amounts of flies | Joondalup McLarty Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 1 | CLOSE | 26 Jun 2020 | 2020-06-29 17:00:00 | 2020-07-02 09:15:00 | Fail | 29/6 - REMOVED DEAD RODENT2/7 - PLUGGED HOLES AROUND P BLOCK WITH 500GMS STEEL WOOL AND 2 TUBES OF EXPANSION FOAM
MSA-DTWD | WA3423118 | E block, G level - Lino flooring lifting in main hallway, stores area, entry to walk in cool rooms | Joondalup Kendrew Campus | GMP-BR | Flooring | Vinyl (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-26 14:20:00 | Fail | Repair vinyl as per client request
MSA-DTWD | WA3423132 | E block, restaurant kitchen - Spray hose, handle and faucet for dishwasher leaking | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 10:40:00 | Pass | COMPLETED
MSA-DTWD | WA3423404 | E block ground E003 (S/W demountable Security door latch pushed in-see notes | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-06-29 13:15:00 | Pass | Repairs to latch
MSA-DTWD | WA3423451 | U block U019 Emergency exit door lock jammed (won't lock) | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-29 12:45:00 | Pass | repairs to lock
MSA-DTWD | WA3423554 | N Block, Room N117- Cupboard door near sink is falling off | Mount Lawley Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-03 09:30:00 | Pass | Arrived at site, inspected faulty cupboard. Required new screws into both hinges. Drilled out the holes and installed new fixings. Adjusted the magnet catches and tested. Works fine. Tidy area, packed away tools.
MSA-DTWD | WA3423589 | N Block, N119A & N119B- lights not dimming correctly | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 26 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 14:00:00 | Pass | Attended site, replaced 1x dimmer and 12x es lamps in room N119a and N119b. Tested all working. Job complete.
MSA-DTWD | WA3423605 | C block C45 Washing machine drain in hairdressing is overflowing | Midland Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-03 11:10:00 | Fail | Increased height to stand pipe of washing machine drain.
MSA-DTWD | WA3423735 | D block Mid-D04 Check power to HWH. | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-02 15:01:00 | Fail | Repalced faulty contactor and timeclock .tetsed hwu all Working fine .
MSA-DTWD | WA3423764 | E block, E313 wash bay - The drain in the wash bay has blocked ( over flowed/ blocked and stinks) | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 26 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-23 10:00:00 | Fail | Had pit cleaned out and jetted inlet and outlet of pit.
MSA-DCS | WA3423792 | No water pressure to all building, power failure | Casuarina Prison | GMP-BR- HO | Equipment | Building Equipment (EQ) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 06:09:01 | 2020-06-27 06:08:00 | Pass | Attended site . Tried to reset alarm on pump control panel. Pump continually goes into high pressure shut down. Isolated pump and switched to mains pressure. Inspected prison for any visible leaks. No visible leaks found. Water is now available throughout prison. Spoke with P. Ackland regarding issue. He was going to contact Broad supervisors, to contact there site plumber who installed the pump, regarding repairs and reinstating prison water back to pumped not mains.
MSA-DCS | WA3423810 | Unit 16 : No hot water and no electricity | Casuarina Prison-Recovery Office | GMP-BR- HO | Electrical | Materials (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 11:41:54 | 2020-06-27 13:00:00 | Fail | Reset gas boilers and kitchen emergency stops in unit 15 and 16
MSA-DCS | WA3423821 | B wing - unit 1 - cell 14-15 toilet is blocked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 12:56:59 | 2020-06-27 11:40:00 | Pass | COMPLETED
MSA-DCS | WA3423825 | Albany regional Prison -Gate control - monitor No 2 in the indigo is faulty | Albany Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-16 15:00:00 | Fail | Removed existing failed monitor from wall. Obtained new wall mount bracket screws (8mm x 40 mm) different size to old monitor, spacers and washers. Mounted brackets on rear of monitor and hung monitor on wall. Connected cables, Programed monitor and installed as Monitor no 2 on Indigo system.
MSA-DCS | WA3423826 | In gate control ,preset on the cameras requires resetting | Albany Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-02 14:30:00 | Pass | Checked PTZ Camera Preset locations on all Site PTZ Cameras, corrected Preset location wher incorrect views were showing. Confirmed views with control staff.
MSA-DCS | WA3423827 | In gate control cameras PTZ 3 and 4 keep dropping out | Albany Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jun 2020 | 2020-07-03 17:00:00 | 2020-08-19 19:44:00 | Fail | Programmed and installed new network switches,Integrated into existing system
MSA-DCS | WA3423830 | Internal visit prison camera faulty.SJ | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 17:46:28 | 2020-08-26 12:00:00 | Fail | All 3 cameras tested. Images and all PTZ functions tested ok.
MSA-DCS | WA3423832 | Unit 2 PIR out side of the 17 faulty & unit 3 PIR out side of the 21 faulty.SJ | Greenough Regional Prison | GMP-BR- HO | Building | General Building (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 17:48:42 | 2020-07-01 15:00:00 | Fail | Replaced PIR sensor behind riveted cage in unit 2 outside room 17 which had been physically damaged.Replaced PIR sensor behind riveted cage in unit 3 outside room 21 which had been physically damaged. Both tested fully operational.
MSA-DCS | WA3423846 | Uniy1 Control monitor is not working . | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 15:53:41 | 2020-06-27 14:45:00 | Pass | Unit 1 Control Monitor not working. Door Control monitor is ok just CCTV monitors with no synch to cameras. Rebooted CCTV workstation and all is ok. Recommend replacing workstation as resources are running high also live view is lagging.
MSA-DCS | WA3423853 | Hakea Prison - in visit main monitor not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 17:08:55 | 2020-06-27 15:00:00 | Pass | Attended site, investigated CCTV cameras in visits, repaired KVM link and tested all displays OK.Job Complete
MSA-DCS | WA3423857 | Cell SHU has leaking pipe from the ceiling | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 17:57:08 | 2020-06-29 10:00:00 | Fail | Collected materials. Isolated water to pipework.. repaired pipework in roof space. Turned water back on and tested. Removed rubbish.
MSA-DCS | WA3423898 | Karnet Prison Farm - Front gate - Display planel to the door control screen has no signal. | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jun 2020 | 2020-06-27 20:36:27 | 2020-06-27 20:30:00 | Pass | Attended site and investigated the fault.Checked power and connections on KVM extenders.Restarted Gallagher workstation in control room.Conducted test.All back to normal and operational.
MSA-DCS | WA3423927 | In front gate doors not operating properly | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Jun 2020 | 2020-06-29 07:01:41 | 2020-06-29 14:30:00 | Fail | Reconfigured faulty sally port door and sliding door, job completed.
MSA-DCS | WA3423952 | Between units 15 and 16 - Support building - Computers are not working. | Casuarina Prison-Prisoner Accommodation Unit 14 | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Jun 2020 | 2020-06-28 13:18:08 | 2020-06-28 12:00:00 | Pass | Contacted site and monitors are down in Unit 15 & 16. Software has logged out and requires password. Site and PFM notified to contact 3rd party contractor as its part of new build.
MSA-DCS | WA3423991 | MCC -Ampac fire panel system -general fault -GND Cell D-16 -faulty alarm. | Casuarina Prison-Gatehouse | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 28 Jun 2020 | 2020-06-28 16:13:27 | 2020-06-28 14:30:00 | Pass | Ampac FIP under Honeywell DLP.PFM to engage Honeywell to resolve issues
MSA-DCA | WA3424760 | Chiller 2 fault | Collection and Research Centre Welshpool-External Area-Ground Floor-Plant Room | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-14 16:30:00 | Fail | Attended site. Chiller 2 in fault. Raised a PO for Airvison to attend. During attendance it was identified that the oil pressure transducer for the applicable refrigerant circuit was defective. Quotation submitted via Airvison. Quotation approved with a seperate job raised. Current job to be closed out.
MSA-DCA | WA3424783 | L1 external balcony External gates leading to balcony have come loose and detached from fittings | Maritime Museum Victoria Quay | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-30 15:00:00 | Pass | Re-installed broken door threshold and installed sliding bolt to secure.
MSA-DCA | WA3424829 | External front fence Damage to front wire fence. Please repair and make secure. -see notes | State Archives Repository Dianella-Main Building-Ground Floor | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-30 09:30:00 | Pass | Replaced damaged section of chain mesh fence
MSA-DCA | WA3424891 | Dark Room - No lighting is working | State Library of WA-Main Building-Level 3-3.41 - Preservation Services - North | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 15:11:00 | Pass | Investigated lights not working level 3, found 2x circuits tripped crossed neutrals, repaired and tested all ok
MSA-DCA | WA3424900 | Lift 5 is not working | State Library of WA-Main Building-Level 5-Lift Motor Room | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-30 09:30:00 | Pass | Some of the car components were faulty. Following our attendance, the equipment was left in service
MSA-DCA | WA3425220 | roof over stage area fire detector in fault due to water damage-zone 75 loop 6 unit 86 | His Majesty's Theatre-Theatre Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 12:30:00 | Pass | Water damaged detector - Z75L6 D86 - replaced base and protection. Fault with transponder - requires further investigation.
MSA-DCS | WA3424100 | Unit 2, Cell C6 - Fire alarm wont reset, active alarm. | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 29 Jun 2020 | 2020-06-29 11:04:37 | 2020-06-29 10:30:00 | Pass | System status displaying normal on departure
MSA-DCS | WA3424108 | Montior room - Camera 28 & 30 are uable to move joy stick. | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Jun 2020 | 2020-06-29 11:12:06 | 2020-06-29 12:10:00 | Fail | Cameras not working with keyboard but ok when moving via workstation.Configured new operator for Video wall, keyboard fully operational
MSA-DCS | WA3424119 | Unit 10, Plant room - burst water pipe | Hakea Prison | SPA-GR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 29 Jun 2020 | 2020-06-29 11:19:51 | 2020-06-30 15:20:00 | Fail | Replaced hot water system in u10(lhs unit)
MSA-DCS | WA3424125 | Montior room - camera 36 not moving with joy stick or on alarm | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Senior Officer Security | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Jun 2020 | 2020-06-29 11:23:02 | 2020-07-13 12:02:00 | Fail | Attended site, checked all PTZ function from indigo keyboard.Camera 36 working correctly.Checked indigo errors, all ok.Staff had reported no CCTV faults since last attendance
MSA-DCS | WA3424132 | Gate hose - fire alarm panel showing an earth fault, unable to reset | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 07:26:49 | 2020-06-30 07:26:00 | Pass | detector faulty - replaced
MSA-DCS | WA3424168 | Active terminates in the Bathroom vanity unit | Boronia Pre-release-AP08 - Prisoner Accommodation House 16-Ground Floor | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 29 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-15 13:10:00 | Fail | multiple visits required to monitor bait box installed 2.7.20 until termite activity is ceased. invoice 9863
MSA-DCS | WA3424230 | Unit 14, B WIng, Cell B16- Electrical plug socket is bcracked & broken | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 08:30:00 | Pass | Replaced gpos in b16 unit 14
MSA-DCS | WA3424232 | U7, E16 - Button pushed in light switch | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 14:00:00 | Pass | Replace light and antenna point
MSA-DCS | WA3424239 | Assessments, cleaners store - light switch needs replacing/repairs as damaged | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 08:00:00 | Pass | Replaced light switch
MSA-DCS | WA3424244 | U9, C7 - Fuse tripping out unable to reset, Plug socket damaged blackening from terminal points | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 08:25:04 | 2020-06-29 12:00:00 | Pass | Repaired tripping gpos
MSA-DCS | WA3424271 | Unit 5, B wing - flickering ceiling light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-29 15:30:00 | Pass | Repaired faulty lights in unit 5 b wing
MSA-DCS | WA3424295 | Unit 5, B & D wing dayroom - ceiling light flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-29 14:00:00 | Pass | Repaired faulty lights in unit 5 b/d wings
MSA-DCS | WA3424301 | Unit 6, B Wing- Windows at the end of the landing, runners broken. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-29 09:30:00 | Fail | WINDOWS REPAIRED
MSA-DCS | WA3424304 | Unit 6, A Wing, Cell A8- toilet constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-02 14:00:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3424305 | ISU, A & C wing - roof leak both around living areas | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-12-04 11:41:00 | Fail | minor/temp repairs made while waiting for BRAF to be approved. Major works still need to be carried out to make sure roof does not leak again.new job 2 be issued...???
MSA-DCS | WA3424309 | Unit 3, Cell D4 very low water pressure in toiley & continually smelly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-01 13:00:00 | Pass | Adjusted copper connector in flush button assembly. Replaced leaking outlet rubber.
MSA-DCS | WA3424325 | Unit 3, Cell C5- sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 09:00:00 | Pass | Used plunger to clear blockage in basin.
MSA-DCS | WA3424330 | Unit 5, A Wing- Cleaning storeroom, Tap leaking water cannot turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-01 14:00:00 | Pass | Replaced 2 x leaking spindles in tapset in cleaners room.
MSA-DCS | WA3424333 | Unit 14, A Wing, Cell A5- Hot water not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-03 14:00:00 | Pass | Investigated hot water issue. Hot water tested and at 45 degrees. No issues found.
MSA-DCS | WA3424335 | Unit 14, B Wing, Cell B10- Toilet is blocked, has been plunged by not clearing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-02 15:00:00 | Pass | Plunged blocked toilet to clear rubbish blockage. Tested.
MSA-DCS | WA3424340 | INF (10)- Cold water pressure not correct | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 12:00:00 | Pass | Repiped hand basin into tempered water line to make hot water to a safe level.
MSA-DCS | WA3424345 | Unit 6, B & D, Cell B2- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-02 16:00:00 | Pass | Used plunger to clear blockage in basin
MSA-DCS | WA3424349 | Door from the main foyer area into the car park is not closing properly | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 12:00:00 | Pass | Attended site and carried out repairs to the hydraulic closer on the foyer door leading to the car park.
MSA-DCS | WA3424351 | Unit 6, A Wing, Cell A7- Flushing issue, water running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-02 16:00:00 | Pass | Replace outlet rubber and cleaned cistern.
MSA-DCS | WA3424384 | Unit 1, Cell C7- Prisoners sink is loose from wall | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 09:09:19 | 2020-06-29 12:00:00 | Pass | Removed cistern to access mounting bolts. Removed basin. Straightened bracket. Remounted basin and connected pipework. Reinstalled cistern and tested
MSA-DCS | WA3424387 | Unit 5, C Wing, Cell C6- Toilet is running constantly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-02 08:00:00 | Pass | Replaced leaking outlet rubber in cistern
MSA-DCS | WA3424392 | Unit 14, Cell A4- Sink water is only dribbling out of tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 14:00:00 | Pass | Replaced blocked spindle.
MSA-DCS | WA3424398 | Unit 3, C WIng, Cell C5- Tap drips & sink blocked, doesnt drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 17:00:00 | Pass | Replaced leaking spindle in basin tap.
MSA-DCS | WA3424404 | Unit 14 Cell alarm fault A12 - alarms keeps going off, different sounding alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 09:20:02 | 2020-07-01 09:00:00 | Fail | Cell call for 14-A-12 showing “Tamper” on Control console, hence the different sound. Drilled out Rivets and removed cell call. Installed new cell call unit. Tested cell call and confirmed Tamper Alarm cleared and good audio both ways. Riveted Cell call to wall.
MSA-DCS | WA3424410 | SHU (9) - East-East wing grille not closing properly and when closed whole grille vibrates. | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 09:25:43 | 2020-07-15 10:30:00 | Fail | 10/07/20Inspect, add washers behind rack, inspect broken limit switch15/07/20Replace rack and limit switch
MSA-DCS | WA3424412 | unit 1, Cell D13 - the judas hatch can be opened from the inside by pushing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-08 13:30:00 | Fail | On site remove jammed object from hatch.Attend site replace lock and adjust strike.
MSA-DCS | WA3424417 | SHU (9)-Lights in yards not working, yards having to be closed at 1700hrs due to insufficient light | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-08-03 15:00:00 | Fail | Repaired multiple faulty lights in SHU yard
MSA-DCS | WA3424421 | Unit 1, D07 & B01 - have dropped on the hinges causing it to bind with the door frame. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-08 12:00:00 | Fail | Replace hinges on B1.Replace hinges, door plate and lock on D7
MSA-DCS | WA3424423 | Admin -On entrance to admin tea room donga, the light cover has been broken. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 10:00:00 | Pass | Checked damaged lights. Picked up replacement and installed
MSA-DCS | WA3424429 | Unit 14, Cell A7- Cell Call alarm is constantly alarming | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 09:36:36 | 2020-07-01 12:30:00 | Fail | Attended unit. Checked with unit staff who advised that they hadn’t had any false activations from this cell call in last two days. Attended cell and noted that the cell call grill was completely obstructed by a clear adhesive material. Cleared the plastic-like substance cover speakergrill and tested to Unit Control. Good audio both ways. NOTE: This Wing has a significant problem with cockroach infestation.
MSA-DCS | WA3424430 | Unit 6, A wing, A12 - window will not stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-08 14:15:00 | Fail | SPIRAL BALANCES RENEWED
MSA-DCS | WA3424435 | Unit 5 having issues with grills.- further information below | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 09:38:11 | 2020-06-29 12:30:00 | Pass | On arrival at unit, found all Grills open, with drive motors disengaged. No control panel buttons would work. Tested button operation at Interface cabinet in roof space, no power to drive control relays. Found supply fuse had failed, replaced fuse (4 amp) and tested load, 1.2 amp max. Unable initially to get C wing grill to operate, until I realised that the Grills on A & C landings had been locked in the Open position. Released the key locks and tested Grills. All Grills operating correctly.
MSA-DCS | WA3424437 | Crisis Care - camera broken | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 09:38:32 | 2020-07-01 15:29:00 | Fail | Sourced parts, attended site, investigated multiple intermittent camera faults in CCU. Repaired communication faults and camera faults.Monitored for correct operation.Tested OKJob Complete
MSA-DCS | WA3424447 | Unit 3, Cell C10- toilet not flushing correctly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-29 16:00:00 | Pass | Inspected cistern and toilet multiple times. Cistern flushes okay.
MSA-DCS | WA3424451 | kitchen Rational over not working (says reset gas)(code from weeked 34-30 34-31 34-27 | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 10:30:00 | Pass | Rational oven faulty (reset gas). Check oven, control modules faulty. Lower ignition module that is not sparking. Replace module ignition. Assemble all & test.
MSA-DCS | WA3424456 | Gatehouse, reception - Roof leak above reception desk | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-10-08 13:27:00 | Fail | SEALED SARKING - CLEANED BOX GUTTER - PUSHED UP FLASHING - FLUSHED OUT PIPES TO SOAK WELL
MSA-DCS | WA3424457 | Unit 3, Cell C13 -Sink tap turns 360 degrees and very hard to stop water flow | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 17:00:00 | Pass | Installed new spindle in basin.
MSA-DCS | WA3424460 | Unit 3 - B7 Unit 3, Cell B07 the top door hinge faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-01 11:15:00 | Pass | Replace hinges, door plate and lock.
MSA-DCS | WA3424464 | CCU (11), Cell C6, D Wing - Water pressure too high. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 13:00:00 | Pass | Installed control valve in shower outlet to restrict water volume.
MSA-DCS | WA3424469 | Unit 13, C WIng. Cell C15- No water pressure & drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 12:00:00 | Pass | Inspected. Cleaned corrosion and blockage from restrictor and tap.
MSA-DCS | WA3424473 | Unit 5, B Wing, Cell B7- Door has dropped | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Lock It Locksmiths | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-15 10:30:00 | Fail | No staff in unit to commence work.Replace hinges and screws.Replace door plate and lock.
MSA-DCS | WA3424475 | unit 1 A wing roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-09-04 14:10:00 | Fail | SEALED RIDGE CAPPING, TURNED UP ENDS OF VALLEY FLASHING.
MSA-DCS | WA3424505 | unit 2 top landing water pipe leaking under sinks | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-01 11:00:00 | Pass | Supply and install new basin set in hand basin unit 2 top landing.
MSA-DCS | WA3424508 | Kitchen - bun divider faulty (sticking) | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-10-02 16:00:00 | Fail | 06/07/2020Called as requested to the BDR not working correctly. Found the the head need to be lubricated so lubricated tested ok. Also the oscillating shaft is very noisey and requires replacement. Parts required 1 x Crossbearing Assembly1 x Bearing Housing1 x Ball Bearing2 x Draw Spring1 x Retaining Ring1 x Bearing2 x V belt1 x Angular Contact Bearing02/10/2020Called as requested to fit parts required fitted tested all working correctly now.
MSA-DCS | WA3424513 | Unit 7, C Wing, Cell extractor fan & switch are broken | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-29 12:30:00 | Pass | Investigated unit 7 extraction system. Found work as intended
MSA-DCS | WA3424515 | MEDICAL CENTRE CLEANING STORE HOT WATER PIPE LEAKING | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-01 10:00:00 | Pass | Replace washing machine taps in medical centre cleaners store..
MSA-DCS | WA3424518 | Kitchen 3 stack pizza oven elements not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-08-19 17:30:00 | Fail | 06/07/20Called as requested to the oven not working correctly. Found the bottom energy regs faulty so replaced with new and indicator lights. Also top deck and middle require the same. 19/08/20Returned to site with the parts required fitted tested all working correctly now.
MSA-DCS | WA3424524 | whole building check RCD function | Maddington (South East Metro) | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 10:05:17 | 2020-06-29 14:30:00 | Pass | Perform rcd injection tests, and emergency and exit light test.
MSA-DCS | WA3424527 | SOP, HB5, Unit 12- Bed light flickering constantly | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-01 08:30:00 | Pass | Repaired faulty lights in unit 12 hb5
MSA-DCS | WA3424531 | kitchen large mixer faulty | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-08-19 14:30:00 | Fail | 06/07/2020Called as requested to service the mixer. Tensioned the top belts all ok. Bowl guild rollers required. Parts required 2x bowl guide rollers 19/08/2020Returned to site with the parts required fitted tested all working correctly now.
MSA-DCS | WA3424539 | Kitchen, prisoners toilet light fitting broken. | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-03 08:30:00 | Pass | Investigate and replace kitchen toilet light.
MSA-DCS | WA3424540 | Unit 6, Cell B10- Door has dropped from its hinges & is unable to be secured | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 13:15:00 | Pass | replaced hinges and fixings
MSA-DCS | WA3424545 | Unit 14, Cell A11- Cell call buttons are not working/blocked | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-01 11:00:00 | Pass | Inspected call call in cell, found speaker grill completely obstructed by tooth paste and button sticking. Drilled our Rivets, removed cell call from cell. Stripped down cell call to component level, cleaned tooth paste from grill and button and cockroach excreta from PCB. Reassembled and returned to cell, tested to unit control and riveted in place. Final test to unit control - Good audio both ways.
MSA-DCS | WA3424547 | Kitchen proover oeven elements not working & seals broken | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 16:30:00 | Pass | 06/07/2020Parts no longer available. Contact Brian Garcia for a replacement prover
MSA-DCS | WA3424552 | Unit 4, Office- Musky odour/smell coming from air con | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-07 11:30:00 | Fail | Cleaned unit to eliminate odour. All ok
MSA-DCS | WA3424562 | programs rm 8 a/c faulty on heat | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-03 12:00:00 | Pass | No fault found. InformeduInformed that buiis sprone to power surge and lost power recently. All operational at time of departure.
MSA-DCS | WA3424564 | unit 1 officers toilet roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-23 09:00:00 | Fail | REPAIRED ROOF - LIFTED SHEETING AND TURN UP VALLEY ENDS
MSA-DCS | WA3424568 | SHU (9) - Computor Room Computer room window is jammed open,-see notes | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-08 13:30:00 | Fail | COMPLETED ON ANOTHER JOB - THIS IS FOR ATTENDANCE ONLY
MSA-DCS | WA3424571 | Unit 13, C Wing, Cell C3- water from basin flows over sinnk & onto floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 13:00:00 | Pass | Cleared blockage from water tap causing water to spray.
MSA-DCS | WA3424576 | Unit 13, C Wing, Cell 02: Shower drain blocked; cold water not working in shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 09:00:00 | Pass | Cleaned shower head . Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3424579 | Unit 14, A Wing, Cell A8- Clogged sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 08:00:00 | Pass | Plunged basin to clear blockage
MSA-DCS | WA3424580 | SHU, intercom entrance in visits not working. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-01 14:00:00 | Pass | Audio from control ok, no audio to control from the intercom. Replaced rusty intercom but traced the fault to the input on the CI8. Shifted cable from input 2 to input 4 and renamed it on the SITE CONFIG program. Audio loud and clear both in the control room and from the intercom. Description ok. Parts used:Cell Guard intercomRJ45 wiring adapter Consumables
MSA-DCS | WA3424584 | CCU (11), D Wing, Cell D8- Water pressure too high, cell floods | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 10:00:00 | Pass | Installed control valve in shower outlet t restrict volume of water.
MSA-DCS | WA3424594 | Perimeter - NOD 4 supervision alarm, constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 10:29:18 | 2020-06-29 12:30:00 | Pass | Supervision alarm on node 4 side A Omnitrax controller. Module tested ok, zones and cabling tested ok. Cleared clutter setting via UCM. Cleared alarm on EBI. Zones 8 and 9 tested ok.
MSA-DCS | WA3424596 | SHU (9) - SHU cameras may have water damage due to water leak/shu visits area | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-01 09:30:00 | Pass | All cameras tested ok on Indigo in SHU control and gatehouse control. Unable to be escorted to SHU visits to physically check cameras for water damage. All cameras tested ok at the end of the day.
MSA-DCS | WA3424597 | Gate house, MDAS - showing low battery in YEEDA and Z block | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 10:31:42 | 2020-07-07 15:55:00 | Fail | Collected Bosch transponder from PFM stock in Hakea.Replaced TR21, fault still present.Replaced battery and cable from Van stock. Still showing low battery.Measured battery on charge 13.5vdc, measured battery when disconnected 12.40vdcAttempted to contacted Bosch Tech support.Technician delivered 1x transponder from Seme stock. Bench tested in gatehouse. Fault cleared. Installed into Edu block 2. No faults on MDAS system, performed duress test .Control received alarm.
MSA-DCS | WA3424605 | Unit 1, D9 - personal lock unable to be opened with a key parts of the lock have come away. | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 15:00:00 | Pass | replaced door plate, lock, barrel and retaining screws
MSA-DCS | WA3424612 | Unit 3, A & C Wing- Ceiling lights faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-02 09:00:00 | Pass | Repaired multiple faulty lights in unit 3 a/c wings
MSA-DCS | WA3424631 | Unit 3, Cell A10- Water leaking down the wall, to the right of the sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-01 15:00:00 | Pass | Replaced leaking flush pipe rubber in plumbing duct C10 after investigating cause of leak.
MSA-DCS | WA3424644 | INF (10), Dryer in the laundry room intermittently keeps tripping out | Casuarina Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-08-17 10:00:00 | Fail | INF (10) Dryer in laundry room tripping out. Check dryer & controls. Remove for repairs, found to be beyond economical repair. Replace with new machine. Return to store.
MSA-DCS | WA3424648 | Gate house Downpipe broken, flooding Visitors waiting area | Hakea Prison | GMP-BR- HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-24 13:11:00 | Fail | REMOVE RUBBISH ON ROOF AND GUTTERS - FLUSHED OUT PIPES
MSA-DCS | WA3424653 | Bakery, Prover has stopped working- further information below | Casuarina Prison | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 10:52:12 | 2020-07-23 12:00:00 | Fail | 29/06/20 - Called as requested to the prover circuit breakers tripped. Found the a SSR faulty it's permanently on. Will require replacement. Also checked the element and found it possible down to earth further checks required. Also the humidity sensor faulty and requires replacement. 01/06/20 - Returned to site with parts to modify temporarily until the correct parts can be supplied. Tested working now.23/07/20 - Called as require with parts required fitted eyed all working correctly now. Unable to gain access to replace element but left on site for future replacement. Prison industry's to provide future access.
MSA-DCS | WA3424698 | Unit 3, Cell A11, Water trickling out of the sink tap there low water pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-01 17:00:00 | Pass | Replaced blocked spindle in basin tap
MSA-DCS | WA3424706 | Bootshop- Roof Leaking, flooding workshop, skylights faulty | Casuarina Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2021-03-15 09:00:00 | Fail | repairs to skylights carried out
MSA-DCS | WA3424738 | Lenard,A wing, Cell A07 & A08- Cells constantly tripping power | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-01 11:00:00 | Pass | Replaced vandalised gpo with a new one . Tested all gpo’s in the cells ok.
MSA-DCS | WA3424745 | ISU (Harding), A Wing Lounge Room- broken sash window Approx. 350 x 500 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-03 14:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3424798 | Unit 8, Cell D3- Sink pulled away from wall due to sink being broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-07 14:30:00 | Fail | Removed broken basin installed new basin adjusted waste to suit
MSA-DCS | WA3424802 | SOG base front desk alarm system alarm sounding but not showing on screen | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 11:49:53 | 2020-06-30 18:30:00 | Fail | Re-programmed and tested
MSA-DCS | WA3424875 | Unit 4, C Wing- Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 09:00:00 | Pass | Repaired light
MSA-DCS | WA3424878 | Unit 1 A10 Intercom Faulty, very faint | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:10:26 | 2020-06-29 14:15:00 | Pass | Attended site checked and found U1 A10 cell call point speaker grill full of toothpaste. Cleanup the toothpaste, tested with Unit Control and confirmed both sides loud and clear.
MSA-DCS | WA3424880 | Unit 2, Cell B8- Cell Call Faulty,very faint | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:11:34 | 2020-06-29 15:00:00 | Pass | Attended site checked and found U 2 B 8 cell call point speaker grill full of toothpaste. Cleanup the toothpaste, tested with Unit Control and confirmed both sides loud and clear.
MSA-DCS | WA3424889 | Unit 3 D12 Basin Leaking from underneath | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-08 12:20:00 | Fail | Replaced oring in outlet tap and reinstalled
MSA-DCS | WA3424908 | Unit 1, Cells C7 & C11- lights broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-29 14:30:00 | Pass | Repaired lights
MSA-DCS | WA3424925 | Unit 4, Cell A14- Intercom faulty, very faint | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:22:46 | 2020-06-29 15:45:00 | Pass | Attended site checked and found U 4 A 14 cell call point speaker grill full of toothpaste. Cleanup the toothpaste, tested with Unit Control and confirmed both sides loud and clear.
MSA-DCS | WA3424932 | Unit 2, Cell B10- Intercom faulty, very faint | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:26:36 | 2020-06-29 16:30:00 | Pass | Attended site checked and found U 2 B 10 cell call point speaker grill full of toothpaste. Cleanup the toothpaste, tested with Unit Control and confirmed both side loud and clear.
MSA-DCS | WA3424941 | Justice Club, Bar- Hot Water System Behind Bar Has Burn’t Out | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-03 13:00:00 | Fail | Disconnect and reconnect hws
MSA-DCS | WA3424947 | Unit 3, Cell C13- Toilet and Sink smashed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 12:30:00 | Pass | nil
MSA-DCS | WA3424978 | Education - fire control panel alarming | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:39:20 | 2020-06-29 15:26:00 | Pass | Whilst onsite a network fault appeared with all the FIP’s now operating in standalone mode only.POD FIP not communicating with the other FIP’s.Advised staff & notified ARA & Commenced fault finding as instructed.Located & reset tripped Modem rack in the old security building comms room OK.All FIP’s communicating as normal.Whilst onsite “Block A cell A9”L9S45 zone 29 in Maintence fault.Located & replaced dirty detector OK.System status displaying normal on departure.
MSA-DCS | WA3424984 | unit 6, yard - pole light not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:41:34 | 2020-07-06 13:00:00 | Fail | Replaced street lamp fitting
MSA-DCS | WA3424987 | house door lights - not working Unit 5, houses 2, 4, 5,6 & 7 | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:43:13 | 2020-07-01 13:30:00 | Fail | Replaced 5 oyster lights with LEDs
MSA-DCS | WA3424990 | Unit 5, step light post, between house 4 & 5 - not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:44:45 | 2020-07-01 12:30:00 | Fail | Replaced step light with led
MSA-DCS | WA3424993 | Unit 1 C wing Loose Pane Of Glass | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-20 11:30:00 | Fail | SECURED WINDOW SO LONGER LOOSE
MSA-DCS | WA3424995 | Unit 5, Light pillars, houes 3x2, house5x2 house6x2 - Not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:46:02 | 2020-07-01 11:30:00 | Fail | Replaced pole lights with LEDs
MSA-DCS | WA3424997 | Unit 5, house 1 - kitchen exhaust broken, not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-15 13:00:00 | Fail | Replaced rangehood
MSA-DCS | WA3424998 | Admin building, entry light swtich mech - faulty | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:48:56 | 2020-06-30 11:30:00 | Pass | Replaced lights and light switch
MSA-DCS | WA3425004 | Unit 3, CCU, C3 - judas hatch lock is faulty | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:49:50 | 2020-06-30 10:15:00 | Pass | Replaced faulty Lock on Judas Hatch ( Meal hatch )with new lock keyed to Prisons System
MSA-DCS | WA3425010 | Admin building, window lock for the switch board operator is faulty | Bandyup Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 12:51:34 | 2020-06-30 08:30:00 | Pass | faulty lock repaired
MSA-DCS | WA3425014 | MMU, prisoner hot water boiler not working. | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-03 13:46:00 | Pass | Someone accidentally turned power off - TURNED ON AND TESTED RHEEM BWU J11473 ALL WORKING WELL
MSA-DCS | WA3425021 | Unit 5, house 3 - water hamer, washer needed to repair | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-23 12:00:00 | Fail | COMPLETED
MSA-DCS | WA3425027 | Unit 2, c5, c9, D7, d10 showers leaking, | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-27 14:00:00 | Fail | COMPLETED
MSA-DCS | WA3425030 | Unit 2, C5, C16, C18, D4, D8, Dcleaning - sinks leaking, requires new spindles | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-28 10:30:00 | Fail | COMPLETED
MSA-DCS | WA3425034 | Unit 2, D4 - WC Pan leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-14 15:00:00 | Fail | COMPLETED
MSA-DCS | WA3425041 | Unit 14, B Wing- Main cell light is not functioning | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 15:00:00 | Pass | Repaired faulty lights in unit 14 b wing
MSA-DCS | WA3425063 | Canteen West, Middle Store Room- Leaking Roof | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-08-05 11:18:00 | Fail | TURNED UP TROUGHS OF SHEET ENDS ALONG ROOF. ADJUSTED SHEETING AND REPLACED.
MSA-DCS | WA3425089 | Jasper, Cell C01 & C02- Tripping power | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-01 12:00:00 | Pass | Replaced vandalised gpo with a new one . Tested all gpo’s in the cells ok.
MSA-DCS | WA3425098 | Library- PA System seems to be wired incorrectly | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-15 09:00:00 | Fail | Rechecked connections and terminations in EWIS Cabinet. Visited Library and checked with Officer in charge. She advised that she could recall any foreign PA messages from their speakers over the last week. This would indicate that the fault has cleared or, has been cleared during this Fault investigation. Unable to reproduce reported Fault.
MSA-DCS | WA3425135 | POD - small dialog has appeared on the main screen | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 13:40:09 | 2020-06-30 11:30:00 | Pass | Reviewed alarms, found no alarm related to the issue.
MSA-DCS | WA3425237 | Unit 4, B/D - Handle needs replacing on the B/D entry door as its broken and sharp. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 14:30:00 | Pass | new door handle fitted
MSA-DCS | WA3425387 | Unit 1, near cell 54 - PA speaker not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 11:30:00 | Pass | Replaced 2x PA speakers unit 1
MSA-DCS | WA3425391 | unit 3, office - desk light | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 13:30:00 | Pass | Replaced 2x Lights with LEDs
MSA-DCS | WA3425394 | Unit 1, service duct leaking water pipe | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 12:30:00 | Pass | Repair leaking water pipe in service duct - unit one
MSA-DCS | WA3425398 | Unit 7, Cell H3, H4 & H5- Lights not working on circuit | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 15:00:00 | Pass | Repaired lights
MSA-DCS | WA3425404 | Unit 7, E16 - Blocked sink water coming up through floor waste | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-08 10:15:00 | Fail | Unblocked sink with plunger and removing knifes forks and rubbish from drain
MSA-DCS | WA3425407 | Unit 8, Staff Room- Filtered cold water tap leaking from on off tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-10 08:42:00 | Fail | Zip chilltap leaking from faucet on arrival. Water slightly slow out of tap. System is still chilling but vents were blocked and moved unit for better air flow. Need to return to fix a specific zip tap (not common spare) and filter changeReturned 10/7/20 to replace specific zip tap that was vented. Also replaced fcunorogo filter to zip unit. Tap was in tricky spot. Flushed filter and checked under pressure
MSA-DCS | WA3425408 | Unit 14, C Wing, Cell C2- Blocked shower drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-16 17:00:00 | Fail | Used acid and plunger to clear blockage in shower drain
MSA-DCS | WA3425497 | unit 2 control room office security cabinet alarm low battery poss UPS | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 15:29:31 | 2020-06-29 15:46:00 | Pass | Contacted site unit 2 indicated power failure which has since been restored, talked site staff through checking UPS online and charging correctly and indicating all good. No further action is required.
MSA-DCS | WA3425508 | Unit 6, D wing - shower light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 08:30:00 | Pass | Repaired faulty lights in unit 6 showers
MSA-DCS | WA3425569 | Gatehouse: Sally Port Door pedestrian access - on auto switch/control screen it wont register /open | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 21:09:59 | 2020-09-09 10:30:00 | Fail | Replaced defective electronic lock sally port door, tested ok and working as normal. Job completed.
MSA-DCS | WA3425870 | Retrospective work order-Unit 1 A wing buddy door lock damaged during incident the occurred 25/06/20 | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 29 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-02 08:30:00 | Pass | installed strike plate
MSA-DFES | WA3424029 | Main entrance foyer - Fire Panel lost communication | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 29 Jun 2020 | 2020-06-29 10:12:31 | 2020-06-29 13:00:00 | Fail | Attended site - power failure leading to drainage batteries.Reset panel and connected panel to generator.Supplied 2x 26AH batteries. Remained onsite to assist insight arrival.
MSA-DFES | WA3424038 | Power is out, emergency backup is down and currently running on generator power. | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Electrical | Materials (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 29 Jun 2020 | 2020-06-29 10:14:02 | 2020-06-29 12:50:00 | Fail | Complete
MSA-DFES | WA3424104 | Please check HVAC system for the building and reset if required after power loss | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 29 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-29 15:30:00 | Pass | Attend site. Found building to have lost power and is now running on generator power. Check Diesel bulktank levels and found to be 3/4. Organise fuel truck to attend and refuel. Carry on monitoring fuel levels. Monitor plant operation. Check diesel bulk tank and found to be half. Fuel tank arrived, fill bulk tank and test guage, working ok. Access server rooms and reset condenser water flow loss alarm. Check through BMS for any other faults. No more faults found.
MSA-DFES | WA3424184 | ALL engine room doors - not working, unable to operate | CFRS Fremantle | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 29 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-29 12:45:00 | Pass | Technician attended the site of Fremantle Fire Station panel lift doors on 29/06/2020. Noted door 4 A40352187j, jamming on closing.Required to adjust side rails as door scraping on wall and jamming. Applied grease also and got working. Noted isolator at switchboard to doors 1, 3, and 5 tripping out. Located fault to isolator above center roller shutter arcing out. Suspect has water in it. Requires programmed electrician to repair .Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3424624 | Fluoro in kitchen area will not switch on | CFRS Claremont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 11:30:00 | Pass | COMPLETED
MSA-DFES | WA3424730 | Opposite Mel Pextons office - Rubber seal has fallen out of the window | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-09 16:00:00 | Fail | Supply & installed new rubber seal on window. job complete
MSA-DFES | WA3424935 | ALL engine room doors - not working, unable to operate | CFRS Fremantle | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 29 Jun 2020 | 2020-06-29 17:00:00 | 2020-06-29 17:30:00 | Fail | Signed in at 1500. Staff on site reported arcing from roller door isolator, circuit breaker has tripped as a result.Isolator is showing signs of heat stress. Replaced with new 3 phase isolator and tested operation.
MSA-DFES | WA3425020 | BA room ground store Ceiling damage due to water leak-see notes | CFRS Armadale | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-08-21 14:00:00 | Fail | Section of gutter replaced. Water damaged ceiling tiles replaced with new.
MSA-DTAG | WA3424445 | Sally port Camera 123 is not showing on system & 6-7 holding cell intercom is not working correctly | Supreme Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-09 12:30:00 | Fail | Replaced Intercom with new. Re-crimped termination. Tested Intercom, clear voice both ways.Installed new Camera - Sally Port Garden (Camera 123). Setup and tested, OK.
MSA-DTAG | WA3424701 | Level 4 CCTV cameras not working, camera's lost connection to the server | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 29 Jun 2020 | 2020-06-29 15:11:15 | 2020-08-29 18:30:00 | Fail | Located the camera and replaced with new Axis unit. Programmed new camera IP and stream. Unable to ping new camera on network
MSA-DTWD | WA3424094 | T Block - 2 lifts are not working, ground | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 29 Jun 2020 | 2020-06-29 11:01:21 | 2020-06-29 09:00:00 | Pass | Not chargeable
MSA-DTWD | WA3424327 | Level 3, Fashion Tech Office - Window seal is detaching/ making noises when windy | Perth Campus B6 | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-08-01 09:00:00 | Fail | ATTENDED SITE AND ASSESSED, GLASS WILL NEED TO BE REPLACED AS CURRENTLY IN FLOAT GLASS, CITY OF PERTH PERMITS REQUIRED, EWP REQUIRED, 2 MEN + SPOTTERS -BRAF WILL BE SENT END OF THIS WEEK, PLEASE ALLOW 10 - 15 DAYS FOR PERMITS TO BE APPROVED ONCE APPROVAL FOR BRAF RECEIVED RETURNED TO SITE ON A SATURDAY AND REGLAZE GLASS PANEL 1 - 1502 X 1138 ARRISED EDGES,REPLACED RUBBERS 3 MEN AND EWP USED CITY OF PERTH PERMIT REQUIRED
MSA-DTWD | WA3424337 | back of bin room, back of building - drains at back of bin room need cleaning | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 13:00:00 | Pass | Clean and unblock drains behind b2
MSA-DTWD | WA3424389 | R block, level 1, Lecture theatre - Replace faulty Smoke detector. | Joondalup McLarty Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-29 11:15:00 | Pass | Z4 in fault (Lecture Theatre) replaced thermal detector in cleaners store, old detector was dirty. Cleaned detector in female toilets.
MSA-DTWD | WA3424588 | U block roof Flexible ducting to EVAP units perished | Balga Campus | GMP-BR | Air Conditioning | Materials (AC) | Ronley Holdings Pty Ltd | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-02 11:35:00 | Pass | We attended site 30/06/2020 and inspected the 41 x flex connections on the evaporative units on U Block roof. 30 of the flex connections were found to be in need of replacements. We have attached a quotation for these works. We have also included the manufacture and installation of sun shields to increase the longevity of the replacement flex connections.
MSA-DTWD | WA3424627 | B Block walkway north side has damaged drain near cleaners room | Rockingham Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-01 13:18:00 | Pass | Fix sunken pavers and drains
MSA-DTWD | WA3424628 | A Block Staff room SE corner 2 x Four foot batten light fittings faulty, please replace with LED | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 12:15:00 | Pass | Attended site and signed in. Located A block staff room. Located lights faulty with frank. Replaced 2 x old fluros with new LED battens, tested all okay. Job complete
MSA-DTWD | WA3424678 | G Block, (Room 23a)- Roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 14:12:00 | Pass | Leak resolved-confirmed with Frank
MSA-DTWD | WA3424718 | J Block, Room J002- Branch above steps requires lopping | Balga Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 09:15:00 | Pass | Carry out essential pruning of two trees at J and E blocks. Carry out mulching at M block as fire risk. Labour: six staff for 1.25 hours at $100 per hour = $750Materials: 2 vehicles for 1.25 hours at $100 per hour = $250
MSA-DTWD | WA3424754 | J Block, J002 (external) - Damaged rail at stairs | Balga Campus | GMP-BR | Building | Steel Work (BU) | AWB Co. | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 12:30:00 | Pass | Replaced broken hand rail
MSA-DTWD | WA3424976 | M block ground M001.5 (East/West corridor, east end) Water leaking through ceiling | Balga Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-06 14:45:00 | Fail | Sighted water ingress only, need to returnReturned with materialsM Block 3x leaks shown. sealed corner flashing over staffroom, leak to corridor modified DWP - leak to main walkway near toilets, possibly cable penetration aand flashing joints.
MSA-DTWD | WA3425111 | level 1 - William St entry inner sliding door making noise | Perth Campus B2 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-06-30 13:58:00 | Pass | Found that the pelmet was vibrating while closing, secured the split pelmet with a bracket, tested all ok.
MSA-DTWD | WA3425123 | A Block, G Floor, Room A20- 6x lights not working, will need EWP | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-03 11:15:00 | Fail | Attended site and signed in. Replaced faulty lights in A block. All now working
MSA-DTWD | WA3425156 | Levle 2, Main entry - Card reader main entry not reading cards | Perth Campus B2 | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 29 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-10 15:00:00 | Fail | Investigated fault found reader not responding. Disconnected and reconnected found reader foundpower to be intermittent and flickering.Left site to pick up part HID Iclass SE10 Open format reader from suplier. Returned to siteinstalled new part. Found new reader not registering site cards.used old reader to test at panel. tested OK. Reinstalled old reader and tested Ok . Required tostrip cable back due to damaged cores on old reader.informed site on status of job. will return to site for further testing.10/07/2020Returned to site with a replacement reader from Supplier. install and test readerParts Supplied to Cient: I Class SE RP10 MultiClass Open Format with SCN FunctionEnabled(CUstom Programmed), Install and test reader OK.Notified Dave Gaff before departing to Site.
MSA-DTWD | WA3425228 | G Block East security lights not operating. Tripping Blue 5 RCD. | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 14:02:00 | Pass | Rectified fault to light circuit and replaced faulty lamps.job completed
MSA-DTWD | WA3425419 | A block A146 BMS issue boiler wont activate | East Perth Campus | GMP-BR | Mechanical Services | Boilers (MS) | Building Automation & Electrical Services Pty Ltd | 1 | COMPFIN | 29 Jun 2020 | 2020-06-30 17:00:00 | 2020-06-30 14:00:00 | Pass | Repair carried out remotely, need to confirm if BAE will charge for this work.Work order closed out at $0 cost
MSA-DTWD | WA3425457 | Red fence carpark Lord St- has graffiti and needs to be removed | Mount Lawley Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 1 | CLOSE | 29 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-02 16:00:00 | Fail | Color matched only on the 30/06/2020 and returned to remove on the 2/07/2020 very extensive graffiti. Was told by Steve Mayer to remove graffiti immediately due to Mark McGowan Premiere arriving the next morning.
MSA-DTWD | WA3425462 | B Block, Room B45- water leak in centre of room | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 10:45:00 | Pass | Stripped section of roof above area. found profile capping full of debris and cleaned out. Founnd lap of sheets full of dirt - retainign water . Cleaned and found window above area with small gaps in seals - resealed
MSA-DTWD | WA3425484 | D block D01 Leak in library near bookshelf number 1 | Midland Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 29 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 12:45:00 | Pass | D Block - investigated area above leak and found loose/missing fixings over the area - replaced all fixings - found dektite seals worn over area, carried out prep and seal.
MSA-DCA | WA3426433 | Research office- lighting circuit has tripped and light switch is hot | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 0 | CLOSE | 30 Jun 2020 | 2020-06-30 18:25:22 | 2020-06-30 15:32:00 | Pass | Faulty light switch was replaced with new, no signs of heat were reported on site.
MSA-DCS | WA3425684 | Control - PTZ 5 & 8 not working | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 07:06:10 | 2020-07-02 12:00:00 | Fail | Checked operation of cameras following remote reset. Checked and adjusted preset locations.
MSA-DCS | WA3425696 | Jeelia A7 bottom bed light not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-06 08:30:00 | Fail | Investigate and repair lights in Jeelia A7
MSA-DCS | WA3425698 | Jeelia C2 obs light not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-06 11:30:00 | Fail | Investigate and repair Jeelia C2 Obs light
MSA-DCS | WA3425701 | ISU D11 water not working to basin & toilet (suspect power pack issue) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Jun 2020 | 2020-07-02 17:00:00 | 2020-07-02 07:50:00 | Pass | Adjusted valve and reseted system. Everything working fine.
MSA-DCS | WA3425706 | Health ceiling panels loose and falling | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Jun 2020 | 2020-07-06 17:00:00 | 2020-09-18 14:35:00 | Fail | replaced only half of damaged panels as access to health center has been denied till further notice - ask to close off job cost to date. reaming loose panels made secure.
MSA-DCS | WA3425744 | POD Camera 85 is faulty - coming up with a blank screen | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 07:53:59 | 2020-06-30 12:00:00 | Pass | Rebooted camera, confirmed image back to normal.
MSA-DCS | WA3425761 | Unit 4, Cell B1- Viewing hatch glass broken | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-08 12:30:00 | Fail | OBS PANEL REPLACED
MSA-DCS | WA3425762 | Control - fire panel is showing Zone control 2 is in fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 30 Jun 2020 | 2020-06-30 12:09:45 | 2020-06-30 11:38:00 | Pass | Zone 2 alarm activated at 0740 this morning. Conventional zone alarm reset on arrival. Zone 2 also showing 3 faults;-Unit 6 vesda 1. Found vesda isolated, removed isolation and fault cleared.-Post 6 on external perimeter. Found corroded junction, repaired, fault still present. Found old ep detector upstairs. Replaced with newconventional head and base. Fault cleared.-Zn 32 SIP fault. Zone is spare with no field wiring connected. Moved EOL in zone card and fault didn’t not clear. Found FIP Zone card to notbe respondent to fault. Soft reboot locked up FIP. Hard reset FIP and system came normal. Possible cause of morning alarm.Left FIP normal and fully operational.
MSA-DCS | WA3425764 | Unit 5, D Wing, Cell D12- Damaged viewing panel frame | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-08 10:00:00 | Fail | VIEWING HATCH FRAME REPAIRED
MSA-DCS | WA3425767 | Eastern Chapel Electrical socket has exposed wires on back wall | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-02 12:00:00 | Pass | Exposed cables
MSA-DCS | WA3425769 | Unit 4, Showers all landings are not working to full capacity | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 10:00:00 | Pass | All tmv’s, strainers and shower heads stripped, cleaned and tested in all wings
MSA-DCS | WA3425774 | Unit 1 Cell B2 light switch smashed | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 08:18:48 | 2020-06-30 10:30:00 | Pass | Replaced light switches
MSA-DCS | WA3425779 | Unit 14, B & D - One of the Non essential power RCD's keeps tripping | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-06-30 13:30:00 | Pass | Repaired waterlogged gpos in unit 14 b/d kitchen
MSA-DCS | WA3425785 | Front Gate Master Control Cameras Not Working x 2 | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 08:25:39 | 2020-06-30 16:47:00 | Pass | Attended site, investigated several cameras not showing on workstation, found these cameras are located in Hakea, investigated Hakea system and interface to Melaleuca, repaired server fault. Found workstation also has data errors on hard drive. Sourced replacement hard drive, loaded all data and tested OK.Job CompleteParts used (SEME Stock):1 x 2.25" Solid State DriveConsumables
MSA-DCS | WA3425787 | Front Gate, Master Control- Camera out of adjustment | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 08:27:58 | 2020-06-30 16:49:00 | Pass | Attended site, adjusted multiple camera views as per Security. Confirmed correct views with Security Officers.Tested OKJob Complete
MSA-DCS | WA3425793 | Unit 2, A-C Wing Laundrys- Lights not working | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-14 14:03:00 | Fail | Reset lights and tested control circuit
MSA-DCS | WA3425795 | Jeelia - A7 - toilet flush not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-03 12:00:00 | Pass | Adjust flush time to solenoid on flush mechanism
MSA-DCS | WA3425797 | Jeelia, Cell B1 & B2- Powerpoints cracked | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-06 10:30:00 | Fail | Replaced cracked GPO's in Jeelia B1 & B2
MSA-DCS | WA3425824 | Whole office has lost power | Rockingham | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 08:47:45 | 2020-06-30 13:45:00 | Pass | Data rack had lost power due a power rail on/ off switch failing. Removed faulty rail from service and tagged it out. Moved equipment onto middle power rail and restored communications. Informed Alvin Fong at Datacom of the situation.
MSA-DCS | WA3425830 | EC-8 offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-06-30 10:15:00 | Pass | Ec8 controller offline, spoke to I.Harmer and walked him through powercycle the controller. Checked status of controller and found software not the correct version for site. Walked I.Harmer through loading V7.70 onto controller.System back online
MSA-DCS | WA3425847 | Front Gate door is not functioning correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Jun 2020 | 2020-06-30 17:08:21 | 2020-06-30 14:44:00 | Pass | Contacted site, door locks and unlocks but shows open unless the custodial jaws are pushed in, causing interlocked doors not to open.Travelled to site, Door is in poor condition and dropped. Adjusted custodial lock and tongue. Adjusted door closer to pull door shut. Door showing closed now.Adjusted door 2 closer as fault similar to door 1
MSA-DCS | WA3425961 | market garden chemical store room roof leak | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-11-23 09:00:00 | Fail | REPAIRS CARRIED OUT TO ROOF
MSA-DCS | WA3426064 | Amenities - Female Gym fluro light not working on shower side | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-01 10:00:00 | Pass | Repaired faulty lights in amenities female gym
MSA-DCS | WA3426089 | Zone Control 2- East side gate not opening properly when buzzed | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 10:54:26 | 2020-06-30 14:15:00 | Pass | All gates working ok electronically. Adjusted door closer to stop the gate from slamming. Strike is loose in the gate. Spoke to the Industries Managerabout having a lock smith repair the strike.
MSA-DCS | WA3426122 | Unit 3, Front Entrance- Beeper is not functioning correctly | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-01 16:00:00 | Pass | Buzzer would continue to sound after the IN cycle had completed. Checked connections to IN, OauT and FREE buttons. Voltages ok. Reset mains power, tested ok. Parts used:Consumables
MSA-DCS | WA3426279 | Social Visits Tables 6 & 7 Water leaking onto the carpet | Melaleuca Prison | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 12:39:54 | 2020-07-08 08:00:00 | Fail | Attended site and carried out repairs to the doors and door seals located on the western side of the social visits building.
MSA-DCS | WA3426284 | social visits Large vinyl bubble in the contact visits area. | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 14:00:00 | Pass | VINYL REPAIRED
MSA-DCS | WA3426344 | Macerator is blocked | Melaleuca Prison | GMP-BR- HO | Waste Management | Water Treatment (WM) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 30 Jun 2020 | 2020-06-30 17:14:51 | 2020-06-30 15:15:00 | Pass | COMPLETED
MSA-DCS | WA3426413 | West Gym, Hallway- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-06 12:00:00 | Fail | Repaired 4 x lights in West Gym lights n/w
MSA-DCS | WA3426415 | kitchen office Air Con Not Heating | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 11:00:00 | Pass | Found unit in communication fault. Failed to run in cooling and heating. Isolated power and reset unit. Checked components. All ok. Ran unit up in all modes successfully. Fault possibly from power surge. All ok at time of departure.
MSA-DCS | WA3426416 | Zone control 2- Gate not closing and latching | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-02 15:30:00 | Pass | Job completed - Assessed issue with latch. Requires new lock.On site 02/07/2020. Supplied and fitted new lock
MSA-DCS | WA3426420 | Canteen West, Office- Roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-22 11:41:00 | Fail | REPAIRED ROOF SHEETING AND FLASHING - SEALED
MSA-DCS | WA3426437 | Social Visits, Court Yard- 12x lights not working (Scissor lift Required) | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-02 13:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3426443 | Stores, office- Hole in the wall above Officers Desk | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-13 15:30:00 | Fail | Attended site and carried out repairs to the holes in the gyprock where data points have been removed
MSA-DCS | WA3426460 | Official Visits control pod Repair Hole in the wall at door entrance | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-17 15:30:00 | Fail | Attended site and carried out repairs to the holes in gyprock walls in the official visits area.
MSA-DCS | WA3426541 | learning centre fire panel in constant alarm without fire | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 30 Jun 2020 | 2020-06-30 19:51:48 | 2020-06-30 20:42:00 | Fail | Replaced broken glass on MCP in learning centre returned ampac panel at learning centre to normal. There was a reoccurring fault coming from detector in infirmary. I was trying to disable device to stop it from reoccurring as there is over 50 faults coming from infirmary from construction works. I was unable to disable device so I removed the DET and base from loop. Will have to reinstate device once construction works completed. Device is M1-100 in dental clinic.
MSA-DFES | WA3426227 | Training room Leaking roof has damaged the wall.-see notes | VFRS Mundaring | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-08-19 11:29:00 | Fail | nternal repairs to ceiling/wall/plasterboard:• Prep the affected area the with polythene + 3 mm Mdf.• Demo the affected plasterboard and bulkhead and remove off site.• Supply + install new framing as required.• Supply + install new plasterboard, flushed and sanded ready for painting .• Painting to the affect location as required.• Removal of all waste materials as required.
MSA-DFES | WA3426271 | Yard, outside gym Downpipe is U/S and broken away from gutter-see notes | CFRS Daglish | GMP-BR | Roofing | Guttering (RF) | AWB Co. | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-10 14:15:00 | Fail | Attended site and inspected works - will need to order downpipes and return to fit outDownpipe lower sections replaced
MSA-DTAG | WA3425677 | Victim Support/Child witness area - please investigate leak in this area | Rockingham Justice Complex | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Jun 2020 | 2020-06-30 17:00:00 | 2020-07-24 13:26:00 | Fail | Install new flashings
MSA-DTAG | WA3425819 | Custody centre- Camera & electric door system is offline | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 30 Jun 2020 | 2020-06-30 12:46:20 | 2020-06-30 09:30:00 | Pass | Changed settings for computer to auto login and programs to boot up. Tested system and all restored.
MSA-DTAG | WA3426056 | ground court 2 2 entry doors green light hasn’t been displaying when the door is unlocked | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-30 13:20:00 | Pass | On inspection, found LED globe to entry face plate faulty.Advised management that security access (sontec) will need to attend to resolve this problem.
MSA-DTAG | WA3426341 | Court 1 & 2 entry doors green/red light hasn’t been displaying when the door is unlocked/locked | Armadale Courthouse | GMP-BR-HO | Security | Monitoring (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-02 14:45:00 | Pass | 2/7/20 - Dean Simpson, Ryan VestyReplaced faulty LED's on court 1 and 2 entry doors.Tested all working ok.
MSA-DTAG | WA3426411 | kitchen Ground Floor and Level 2A Water leaking from inside cupboard on both floors-see notes | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 17:00:00 | 2020-07-14 15:15:00 | Fail | Complete
MSA-DTAG | WA3426570 | jury room camera 21 CCTV 2 pointing to vehicle gate barely visible | Rockingham Justice Complex | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 17:00:00 | 2020-08-24 12:30:00 | Fail | Found resolution when having remote access to site. All in working order.
MSA-DTWD | WA3425724 | Admin A009 area roof leak - please investigate | Naval Base | GMP-BR | Roofing | Tiled Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 30 Jun 2020 | 2020-07-02 17:00:00 | 2020-06-30 12:30:00 | Pass | Inspected/unblocked box gutter & rain head. No further leaks reported from site. Job complete
MSA-DTWD | WA3425750 | E Block, Room E205 roof leak | Mount Lawley Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 30 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 09:15:00 | Pass | Sealed pan flashing, dektites, anchor points. Cleaned back under pan flashing.
MSA-DTWD | WA3425751 | D Block Repair leak into D309 from concrete floor above | East Perth Campus | GMP-BR | Roofing | Concrete Roof Construction (RF) | AWB Co. | 3 | CLOSE | 30 Jun 2020 | 2020-07-06 17:00:00 | 2020-07-06 14:45:00 | Pass | Sealed multiple cracks in concrete slab, also lifted drain and sealed inside.
MSA-DTWD | WA3425753 | N Block, Room N229 corner desk, Roof leak | Mount Lawley Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-07 10:30:00 | Pass | Side flashing lifted - repositioned and sealed. Sealed a number of creased sheets and 1x dektite torn - filled and sealed
MSA-DTWD | WA3425782 | B Block, B29a tutorial leaking from roof | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-17 13:00:00 | Fail | Investigate area above leak. Found 2x issues unrelated to previous works. Found downpipe blocked, unable to take pipe off so tried to unblock from top, found small hole in roof sheet, made repairs. Measured up to replace rusted downpipe to area . Attended site with materials and fitted new downpipe. Electrician to reattend to connect light.
MSA-DTWD | WA3425803 | Ground floor Welding bay 8 Metal Fabrication 1 - damaged 3 phase power point & plug | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-07 11:00:00 | Pass | Replaced burned out 3phase outlet and plug. Job completed
MSA-DTWD | WA3425808 | B Block, Room B209- Zip Boiler has fault and not reaching temperature | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-03 12:13:00 | Pass | Replaced element ZIP HYDROTAPA40421339F ZIP HYDROTAP REPALCED ELEMENT/TESTEDE CENTRAL LEVEL 2 BLOCK B B209
MSA-DTWD | WA3425814 | Block 6, Car park lighting west side of campus- RCD - R9 tripping in block 6 main switchboard | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-07 16:00:00 | Pass | Tested light poles and cabling to R9 circuit building 6. All working fine job completed
MSA-DTWD | WA3425926 | E Block, E58 L.S.K – Cleaners tap leaking badly | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 30 Jun 2020 | 2020-07-01 17:00:00 | 2020-06-30 14:00:00 | Pass | Re fix and fix pipework leaking
MSA-DTWD | WA3425944 | Level 2, Room A228 (store room)- broken light switch. | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 15:09:00 | Pass | Repalced faulty switch in A228
MSA-DTWD | WA3426025 | Print Area, Male Toilet- Broken toilet seat | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-29 12:30:00 | Fail | Complete
MSA-DTWD | WA3426091 | V block ground canteen. Refit securely vinyl floor tiles under vending machine | Joondalup McLarty Campus | GMP-BR | Flooring | Tiling (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-09 13:55:00 | Fail | Replaced tiles as requested by site
MSA-DTWD | WA3426153 | F Block, F56 ladies toilet- Roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-09-07 15:00:00 | Fail | Carried out further repairs, hose test indicates leak resolved, will wait for rain forecast for next week to confirm. Refer to Andrew Crawford. Site confirmed not going ahead. Job closed off
MSA-DTWD | WA3426345 | F Block, FG369- Damaged/Faulty GPOs at sign-in bench | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-02 16:59:00 | Pass | Attended site, repaired quad gpo underneath sign in bench. Tested, all working. Job complete
MSA-DTWD | WA3426382 | E Block, E9 Corridor – Door not locking properly | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-30 14:30:00 | Fail | E Block - E9 corridor - door lock not working.Digital Lock replaced.
MSA-DTWD | WA3426384 | C Block, Walkway outside Cafeteria – Roof leaks | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 14:00:00 | Pass | Leak resolved would recommend a more regular sweep and cleanup of the roof area due to the large pine trees
MSA-DTWD | WA3426498 | Block 1, PABX room 1G26- Faulty Lock | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 30 Jun 2020 | 2020-07-07 17:00:00 | 2020-07-06 08:30:00 | Pass | Block 1 (1G26) PABX Room - Lock Faulty.Lock repaired.
MSA-MRWA | WA3426448 | Ground Floor - Disabled Toilet Full flush button has been broken with the toilet cistern | Heavy Vehicle Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 30 Jun 2020 | 2020-07-03 17:00:00 | 2020-07-01 15:05:00 | Pass | Removed old flush mechanism replaced with new
MSA-DCA | WA3429439 | Plant room - 2 boilers in fault & water leak on boiler 2 | His Majesty's Theatre-Theatre Building-Level 4-Plant Room 1 | GMP-BR | Mechanical Services | Boilers (MS) | Precise Air Group | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-01 11:30:00 | Pass | Attended site,gained access to boiler plantroom,found boilers to require manual reset,found boiler isolator cover to be fitted incorrectly causing no power to boiler,rectified issue, left boiler 1 operational and boiler 2 to require boiler tech to be attending site to look into further issue.
MSA-DCS | WA3429211 | System 1 fault in the York Tower - Cooling issue | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Cooling Tower (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 06:46:50 | 2020-08-05 08:00:00 | Fail | Essential Ref attended, found system tripped on low oil, adjust oil level and reset , monitor system system tripped again, adjust oil level and confirm oil refills as required .All operational
MSA-DCS | WA3429255 | Jeelia, A4 - Shower and drain blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 01 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-03 11:15:00 | Pass | Clear blockage to shower waste
MSA-DCS | WA3429306 | UNit 7, Regi Area- Vinyl floor cover lifting needs regluing | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-04 11:30:00 | Pass | FLOOR COVERINGS RE GLUED
MSA-DCS | WA3429308 | Unit 3, C3 - Blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 09:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3429313 | CCU, C WING, C6 - shower leaks from shower head when turned off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-10 09:00:00 | Fail | Replaced leaking spindle.
MSA-DCS | WA3429314 | UNit 1, A Wing- Lights not working in shower | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-01 11:30:00 | Pass | Repaired faulty lights in unit 1 showers
MSA-DCS | WA3429331 | Unit 1 - Lights out in Lobby | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 08:15:02 | 2020-07-01 15:00:00 | Pass | Repaired multiple faulty lights in unit 1 lobby
MSA-DCS | WA3429332 | Unit 1 - A/C and B/D dayrooms and showers | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 08:16:02 | 2020-07-02 12:00:00 | Fail | Checked lights in unit 1. Found transformer in switchboard needed resetting. Unsure what was cause. Possibly latching relays. Left to monitor.Returned and reset transformer, isolated and Removed latching relays. All ok
MSA-DCS | WA3429341 | Mechanical workshop, office - A/C keeps shutting down | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-20 10:22:00 | Fail | Compressor faulty. Replace with wmsNew Daikin 3.5Kw wall mounted split system installed, room air conditioner reclaimed refrigerant charge & moved to off site waste recycling.
MSA-DCS | WA3429359 | Kitchen salad bar - Wires are damaged | Karnet Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-03 10:30:00 | Pass | Investigate and repair damaged wires on kitchen salad bar.
MSA-DCS | WA3429473 | Kitchen, water leaking into exit sign | Wooroloo Prison Farm | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 09:32:36 | 2020-07-24 13:24:00 | Fail | REPLACED FLASHING, SHEETING & SKYLIGHT
MSA-DCS | WA3429475 | Kitchen - Exit lighting not working due to water leak. | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 09:00:00 | Pass | Replaced exit sign in kitchen
MSA-DCS | WA3429492 | Industries Yard - Hoes reel has split in it | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-01 11:16:00 | Pass | completed replacement
MSA-DCS | WA3429498 | Kitchen - Insulation breaking away from coldroom pipe. Coldroom 1 | Hakea Prison | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-01 15:20:00 | Pass | Found insulation had broken away, causing ice to form which would leak while melting. Defrosted ice, replaced isolation and cut away metal frame putting pressure on insulation. All ok at time of departure.
MSA-DCS | WA3429618 | Administration, Lobby Area, Visits CCV monitor in lobby power suppy not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-07 15:32:00 | Fail | Investigated visits workstation, found one display has failed and staff reported workstation slow. Sourced replacement display, modified bracket and cabling for new display, repaired software issues with operating system. Confirmed correct and efficient operation.Job CompleteParts (SEME Stock):1 x 21.5" LCD Display.Job Complete
MSA-DCS | WA3429626 | Unit 2 - D Wing lights faulty 2nd and 4th lights in hallway | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-09 12:00:00 | Fail | Repaired faulty lights in unit 2. Picked up replacement emergency packs. Retro fit in replacement eagle fitting. Returned to unit 2 and installed
MSA-DCS | WA3429629 | Constant tamper alarm on IRB A1, A2, A5 | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 08:48:45 | 2020-10-12 13:52:00 | Fail | Investigated and repaired multiple duress faults.Tested OKJob CompleteParts:Consumables
MSA-DCS | WA3429631 | Internal Zone 12 microphonic constant alarm | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 08:50:59 | 2020-07-01 14:04:00 | Pass | Zone in tamper,Tested cable, showing open circuit.Traced cable and re-terminated splice kits on bottom row.Tamper cleared.Tested activation and confirmed with SOG.Zone secured and stable
MSA-DCS | WA3429633 | Ultra key light CCTV keyboard not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 08:52:00 | 2020-07-01 15:26:00 | Pass | Sourced parts, attended site, repaired faults with CCTV keyboards.Tested OKJob CompleteParts:Consumables
MSA-DCS | WA3429642 | Maintenance, whole unit - replace unit headlight covers in units/damaged | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-02 15:00:00 | Pass | Quote to replenish site stock cell light diffusers.
MSA-DCS | WA3429663 | Kitchen - Breadslice has broken blades, | Karnet Prison Farm | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 10:40:42 | 2020-07-01 16:15:00 | Pass | 01/07/20Called as requested to the bread slicer blade broken. Obtained & replaced blades with new as required. Tested ok.
MSA-DCS | WA3429669 | Kitchen - filters on rational ovens blocked requireing replacement on both ovens | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 10:42:40 | 2020-08-06 16:15:00 | Fail | 06/08/2020Replace all filters, test ok
MSA-DCS | WA3429671 | Unit 14 - A Wing Lower shelf power point not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 10:00:00 | Pass | Replaced damaged cell gpos in unit 14 a1
MSA-DCS | WA3429705 | Entrance road fill pot holes-contractor on site | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 10:50:22 | 2020-07-02 10:30:00 | Pass | 02/07/20repair pot holes entrance road
MSA-DCS | WA3429765 | Unit 2D and multiple locations PDA system showing no respons alerts | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Jul 2020 | 2020-07-01 15:14:42 | 2020-07-03 11:31:00 | Fail | Job complete
MSA-DCS | WA3429781 | U9 A10 Water leaking from sink waste | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-08 08:43:00 | Fail | Tightene up loose set
MSA-DCS | WA3429782 | Unit 4, Cell A11 - toilet not filling up with water/blocked pipes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 17:00:00 | Pass | Inspected. Replaced inlet valve in cistern.
MSA-DCS | WA3429794 | Unit 2, A Wing, Cell A7- Window wont open correctly | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-03 09:00:00 | Pass | JOB DOUBLE UP- COMPLETED ON WA3415244
MSA-DCS | WA3429846 | Unit 1 & 2, laundry - Clothes Dryer Ducting Blocked | Melaleuca Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | Schlager Construction Group | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 11:44:25 | 2020-07-16 15:30:00 | Fail | Removed and stripped all 100mm pipe and ducting from the laundry dryers to the ceiling space.Vacuumed and removedl the build up of lint and fluff within the pipe and ducting.Reattatched all pipe and ducting.Removed all ceiling vents and cleand.
MSA-DCS | WA3429847 | Hakea justice club bar area Ruptured Rinni hot water tank | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 13:03:00 | Pass | Replace 50lt storage HWU to bar area in social club
MSA-DCS | WA3429851 | Sally-Port Access Door to Front Gate Kitchen - Door Document Tube Broken | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 12:01:22 | 2020-07-08 09:30:00 | Fail | Attended site and carried out works to the document tube in the Sally port access door.
MSA-DCS | WA3429854 | Justice Club- Roof leaking in several places | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-10-08 13:29:00 | Fail | 2X LEAKS REPAIRED TO ELIMINATE LEAKING
MSA-DCS | WA3429872 | Carpentry work shop- Broken window and frame | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-15 11:30:00 | Fail | WINDOW RE GLAZED- FRAME REPAIRED
MSA-DCS | WA3429928 | ISU B08 Basin not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-02 08:55:00 | Pass | Adjusted valve and reseted system. Everything working fine.
MSA-DCS | WA3429943 | unit 4C HW heater 260lt system not working leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 12:59:55 | 2020-07-06 13:30:00 | Fail | Complete
MSA-DCS | WA3429994 | Reception - strip search room light faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 11:00:00 | Pass | Replaced 2x led half panel lights
MSA-DCS | WA3429995 | Reception - outside door, bunker light not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 12:00:00 | Pass | Replaced outdoor light
MSA-DCS | WA3430032 | auto entrance door not opening and closing and is on an angle | Rockingham Justice Complex | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 01 Jul 2020 | 2020-07-01 17:57:15 | 2020-07-01 17:20:00 | Pass | Attended site tightened door Found presence sensor cable damaged Repaired while onsite and tested and left in full working order
MSA-DCS | WA3430160 | Unit 2 D Wing Yard Door Lock Door Lock Handle Broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 16:00:00 | Pass | job completed - Assessed issue with door. Determined parts required.On site 06/07/2020. Supplied and fitted required parts
MSA-DFES | WA3429435 | The rear door (2nd Engine bay) Door indicator lights have been knocked off the wall | CFRS Welshpool | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 15:11:00 | Pass | No work performed due to the light not been damaged or needing repair. Spoke to Welshpool FS command and they don’t know of problems andafter inspection of lights all working, fill out paperwork and left.
MSA-DFES | WA3429609 | Engine room door (rear door behind light tanker) - not operating, door coming off | CFRS Claremont | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-09 13:15:00 | Fail | Technician attended the site of Claremont Fire Station to the Engine Room Bi-fold Door No. W 23723 on 01/07/2020. Following a full test and inspection of door components found fault to be door found door was hit by light tanker. Quote was submitted. Technician returned on site on 09/07/2020 and completed quoted works. Full test and inspection of door function completed prior to leaving site. Breakdown of cost: Labour = $ 1,007.50Parts = $ 69.69
MSA-DFES | WA3430052 | ground office faulty lights in office various locations-see notes | CFRS Claremont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-02 12:00:00 | Pass | COMPLETED
MSA-DFES | WA3430064 | Rear yard One set of red lights on one of the bollards at the back of the Central FS-see notes | DFES Education and Heritage Centre | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-08-03 08:30:00 | Fail | Attend sitem removed bollard plates and replaced cable between bollards 5 and 6 for LED's. Tested for operation, all working
MSA-DFES | WA3434161 | Retrospective work order - SINGLE Z18 REED SWITCH DAY 1 FRONT ROLLER DOOR | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-01 11:24:00 | Pass | STAFF ONSITE, STAFF WENT TO A JOB. ALL IS OKAY
MSA-DTAG | WA3429415 | ground Magistrates Chambers 1 Leaking roof | Armadale Courthouse | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-24 13:00:00 | Fail | REALIGN TILES WHERE LEAK WAS LOCATED
MSA-DTAG | WA3430168 | L1 Court 1 ie door lock tongue not catching - see notes | Midland Courthouse | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 13:00:00 | Pass | 06/07/2020. Disengaged turn snib to ensure correct function.
MSA-DTAG | WA3430171 | ground Registry Manager’s Office-When recording security footage it does not pick the time selected | Midland Courthouse | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-02 14:20:00 | Pass | Synced workstation time with CCTV server and adjusted time zone from -8 to +8 Perth.Checked footage and restarted workstation.Rechecked for any changes.Time now correct when manager downloads footage
MSA-DTWD | WA3429239 | Level 2, inside & outside library - loose hand rails | Perth Campus B2 | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 3 | CLOSE | 01 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-11 11:00:00 | Fail | HANDRAIL DAMAGED Attend site sign in Locate Level 2 Handrail as per work order, resecure handrailAdditional handrail requires welding repairs assess additional works and provide quoteSpecialist Contractor (Welder) Fabricator to attend site and weld 1 x floor/post connection.Scope of works / External HandrailRemove affected handrail x 1 and remove off site to fabricate new fixing points.Reinstate handrail to existing location and fixed with additional fixings.Specialist ContractorElectrician to attend and disconnect Smoke Alarms for welding works
MSA-DTWD | WA3429265 | A Block, level 1, A146 - Repair Barrel to lock on Central Store door | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 01 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-01 10:15:00 | Pass | replace cylinder components to room A146
MSA-DTWD | WA3429280 | Security system - all the swipe cards are not working | Kwinana Automotive Centre | GMP-BR | Security | Security Management System (SE) | BJ SYSTEMS | 0 | CLOSE | 01 Jul 2020 | 2020-07-01 11:50:23 | 2020-07-01 16:30:00 | Fail | Attend site and found both controllers offline with no power. Batteries were also out of date and had run flat. Staff said there was a power outage and doors weren’t working after power came back on. Measured 4V on power supplies. Disconnected batteries and re-powered power supplies. Power to controllers keeps dropping off and won’t hold. Went through process of elimination and isolated each device (controllers, readers, locks) to find devices causing the fault. Also tested each power supply to see if power holds. Found at least 2 of the power supplies to be faulty and the alarm dialler also faulty. Removed old power supplies from wall and installed new 8 amp power supply inside the cabinet. Existing cables to controllers and batteries weren’t long enough to reach new power supply. Ran new cables and re-terminated all connections. Replaced alarm dialler. Replaced batteries. Powered everything up and found main auto door not opening. Checked head of auto door and power cycled motor. Mai
MSA-DTWD | WA3429347 | Carpark entry door (solid steel door)- Door broken, see further notes below | Perth Campus B1 | GMP-BR | Building | Steel Work (BU) | AWB Co. | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 10:30:00 | Pass | As per Sig Slip
MSA-DTWD | WA3429430 | G block, Room G129- Male toilets last cubicle blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 11:30:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3429442 | E block ET01-Lock jammed and can’t get into classroom. | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-01 12:55:00 | Pass | E Block - ET01 - Lock is jammed and can not open.Lock repaired.
MSA-DTWD | WA3429476 | E block E29 Dem lab – Lights not working | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 11:15:00 | Pass | Replaced faulty light switches in E29. All now working.
MSA-DTWD | WA3429503 | Store builidng roof sheeting has come loose | West One Services | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 08:20:00 | Pass | Investigated loose roof sheets - Didn't find any loose sheets but found flashing was loose and when wind is blowing it would sound like loose sheeting. tightened fixings
MSA-DTWD | WA3429575 | E block E300 Remove damaged sink and make safe in the Automotive workshop | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-10 10:30:00 | Fail | Removed sink and tap
MSA-DTWD | WA3429661 | front elivation emergency exit door , door panel glass has been shattered | Armadale Campus - 145 Jull Street | GMP-BR | Building | Doors (BU) | ACTION GLASS & ALUMINIUM | 0 | CLOSE | 01 Jul 2020 | 2020-07-01 14:38:19 | 2020-07-23 11:45:00 | Fail | ATTENDED SITE 01//07/20 - PATCHED AND SECURED BROKEN GLASS PANEL, COLLECT PUTTY SAMPLE TO BE TESTED FOR ASBESTOS, PUTTY TESTED POSITIVE FOR ASBESTOS.ASBESTOS PUTTY REMOVED, REGLAZED DOOR PANEL 6.38 CLEAR LAMINATED SAFETY GLASS 1 - 1835 X 642SILICONE USED, RIVETS USED 12 X 12 ANGLE USED - 2 @ 1840, 2 @ 645.*****PLEASE NOTE - TINTING WILL DONE ON A WARRANTY AT ACTION GLASS'S COST***
MSA-DTWD | WA3429920 | Admin area main entry automatic door - not operating correctly | Clarkson Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 01 Jul 2020 | 2020-07-01 14:37:18 | 2020-07-01 12:53:00 | Pass | 1052822, arrived onsite and signed in , inspected door and found controller in obstruction fault, checked door manually and reset unit and tested operation in all modes and could not fault. Load tested batteries, checked safety’s etc all correct.
MSA-DTWD | WA3429984 | Damaged pavers around F and H Blocks | Rockingham Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-19 14:00:00 | Fail | As per sig slips
MSA-DTWD | WA3430058 | Inside auto door (near room AT218) - not working | Kwinana Automotive Centre | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-02 08:35:00 | Pass | Found door was in power fault causing door to not operate, reset door and checked over and tested all ok
MSA-DTWD | WA3430063 | G block paved area and E2 Ramp - uneven paving | Murdoch Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 14:00:00 | Pass | Removed and relaid approx 20 pavers and 2 concrete pavers. Rebedded in sand and cement. Will need BRAF for courtyard area.BRAF DECLINED - CLOSED OFF
MSA-DTWD | WA3430109 | E Block, Room E617- Male toilet is broken (no 4) | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 01 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 11:50:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3430117 | Block 10, 1st floor, Walkway- Lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 13:30:00 | Pass | Reset tripped rcd to walkway lights and replaced 1x faulty lamp.job completed
MSA-DTWD | WA3430124 | block 8 L1 passageway Lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 16:00:00 | Pass | replaced faulty light fitting in block 8- L1
MSA-DTWD | WA3430152 | Block 1, Room 1G10- Broken power point | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 12:00:00 | Pass | replaced faulty GPO and added extra to eliminate cords across room
MSA-DTWD | WA3430163 | L3 A block south male toilet and pan has come loose from the floor | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-02 17:00:00 | Pass | reinstalled pan
MSA-MRWA | WA3428136 | AC 1 Fault - Basement Server room | Don Aitken Centre MRWA Head Office-Main Building-Basement-IT Server Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 01 Jul 2020 | 2020-07-01 06:18:03 | 2020-07-01 10:00:00 | Fail | Over all crack unit was found in fault and required a manual reset. After applying works, unit automatically started up. Ran and tested all okay.Second CRAC alarm, was called to site and found units in a comms fault again, carried out power cycle and units started correctly. Will get pricing for Stulz to attend site and check system programming for issues. Will resubmit quote to replace bus link between units.
MSA-MRWA | WA3429297 | Level 2, Zip water unit tap broken | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-01 09:48:00 | Pass | Replaced zip tap on Autoboil L2 and tested
MSA-MRWA | WA3429591 | Toilet reported to be continually running | Don Aitken Centre MRWA Head Office-Main Building-Second Floor-Toilet-Female | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Jul 2020 | 2020-07-02 17:00:00 | 2020-07-01 16:52:00 | Pass | Replaced faulty inlet
MSA-MRWA | WA3430145 | Bridge compound inspection shed inspection shed Broken RCD switch in the boat shed switchboard | Materials Engineering Branch | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 01 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 09:30:00 | Pass | Replaced faulty rcd
MSA-DCA | WA3430383 | Lights tripping after water leak | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Chi Cho Gelato | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-08-18 11:51:00 | Fail | Replaced damaged lights with new
MSA-DCA | WA3431021 | ground lift Main lift is shuddering and jumping moving between G & L1. -see notes | Maritime Museum Victoria Quay-Main Building | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-30 10:00:00 | Fail | job completed - call covered under contract. No charge to be applied
MSA-DCS | WA3430287 | SHU (9), East wing, Cell B5 - OBS light of SHU not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-06 13:00:00 | Pass | Investigate and repair SHU Cell B5 light
MSA-DCS | WA3430296 | Unit 2, D wing - cleaning cupboard drain hole blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 08:00:00 | Pass | Removed paint from grate and plunged to clear blockage.
MSA-DCS | WA3430309 | Unit 1, Cell D3- personal light on cell turns on and constantly flickers | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 10:00:00 | Pass | Repaired faulty lights in unit 1 d3
MSA-DCS | WA3430312 | Entry Pod - Fire alarm panel fault, in constant alarm. | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 07:43:17 | 2020-07-02 13:48:00 | Pass | 2/07/20 EIAttended site & on arrival inspected POD FIP.FIP reporting intermittent supply fault on Industries/textiles node 2 FIP.Investigation of Node 2 Industries/textiles FIP identified PSU damaged.Replaced PSU for new.Systems status displaying normal on departureNote:Industries/textiles FIP batteries 2 x 12V 26A/h are approaching recommended replacement date.Recommend replacement.
MSA-DCS | WA3430313 | Unit 1, B Wing, Cells B5 & B6- Obs lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-02 10:30:00 | Pass | Repaired faulty lights in unit 1 b5 and b6
MSA-DCS | WA3430315 | Unit 5, A Wing, Cell A9 - Toilet is running and wont stop | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 14:00:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3430336 | Unit 3, Staff Room- Tap is leaking, washer may need replacing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 15:00:00 | Pass | Replaced both jumper valves in kitchen taps.
MSA-DCS | WA3430370 | Node 8 supervision in alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-02 12:59:00 | Pass | Cleared clutter from all 9 Nodes both A and B side.Fault on Node 8 B side has cleared. A side still active.Checked through programming and powercycled controller. Decluttered Node 8 A side and monitored.Zone stable, walk tested and confirmed operational.Zone stable
MSA-DCS | WA3430389 | Unit 4, PRU perimeter, zones 4 - 7 are offline | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Jul 2020 | 2020-07-02 16:53:02 | 2020-07-02 12:50:00 | Pass | PRU perimeter indicating offline, attended bunbury to find controller failing to communicate, re established communications and tested fully operational under stress. All ok
MSA-DCS | WA3430398 | Kitchen, main work area - lights not working x 2 | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-14 01:00:00 | Fail | Replaced faulty lamps and ballast
MSA-DCS | WA3430404 | Kitchen, main work area - unblock floor drain & repair broken&missing floor drain filter screens | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 09:00:10 | 2020-07-02 15:59:00 | Pass | Clear blockage to kitchen
MSA-DCS | WA3430407 | Unit 4, Lobby Area- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-02 13:00:00 | Pass | Replaced broken light switch.
MSA-DCS | WA3430411 | Unit 2, D5 - bed headboards light switch broken | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-14 14:00:00 | Fail | Replaced faulty switch
MSA-DCS | WA3430413 | kitchen main work area Roof Vent Leaks When Raining | Melaleuca Prison | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-24 12:00:00 | Fail | Attended site and assessed what repairs where required.Reattended site and carried out repairs to the flashings around the roof vents that where damaged and leaking.
MSA-DCS | WA3430414 | Investigate sprinkler fault that occurred overnight. Possible location West Admin | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-02 14:31:00 | Pass | Attended site and found no sprinkler alarm in system.Spoke to Will on site and turned out it was a DBA alarm that eventually reset ok on the night. Apparently pumps hadn’t started.Checked valve set and found all pressures normal.Note system has no jacking pump so same pressure above and below valve set.Checked pumps and found all normal.Alarm possible due to air in system.
MSA-DCS | WA3430458 | SHU (9), Cell A5- Obs light of the west wing is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-07 08:30:00 | Pass | Investigate and repair SHU Cell A5 light
MSA-DCS | WA3430466 | Gym, Water Fountain- Water tastes off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-06 09:40:00 | Pass | Replaced filter and flush systemGac System feeding Arcus FountainA40191333D
MSA-DCS | WA3430468 | Left hand potato rumbler - struggling to operate while under load, slowly spinning | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-03 08:30:00 | Pass | Repaired faulty potato rumbler in veggie prep
MSA-DCS | WA3430485 | Unit 14, Cell A12- Overhead light and top bunk lamp not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-06 10:00:00 | Pass | Repaired faulty lights in unit 14 a wing
MSA-DCS | WA3430490 | Level 3 glass door not opening or closing properly | East Perth | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 09:37:03 | 2020-08-14 14:00:00 | Fail | Technician attended the site of Department of Corrective Services, Level 3 Automatic door # W21169 on 02/07/2020. Following full test and inspection of door components identified fault was ongoing issue with MUK Kit.Technician returned on 14/08/2020 and remove existing Rubek R7000 operator replaced it with an Assa Abloy SL 500 MUK. Tested operations, all okay.Full test and inspection of door components completed prior to leaving site.
MSA-DCS | WA3430509 | Amin, Left hand cubicle in Male admin toilet is continually running. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 12:00:00 | Pass | Replaced leaking outlet rubber inside cistern.
MSA-DCS | WA3430575 | Unit 6, Computer room & Lobby area- Hot water pump is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 10:41:20 | 2020-07-27 10:30:00 | Fail | 3/7/20 - Investigated leak. Braf required, to continue works to repair leaking main shaft seal on domestic heating sealed water main pump.27/7/20 - collected pump offsite. Installed new pump and gasket and tested.
MSA-DCS | WA3430597 | Centrel control vehicle grill - tracks are broken under the motor-see notes | Greenough Regional Prison | SPA-BR | Security | Access Control (SE) | AFD Contracting | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-08-06 14:30:00 | Fail | 06/08/20Replaced overhead track as per BRAF
MSA-DCS | WA3430666 | Unit 14, A12 - top bunk light & main light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 11:30:00 | Pass | Repaired faulty lights in unit 14 a12
MSA-DCS | WA3430685 | zone control 2 - easter gate to U8,9 & 10 - Self-closer requires attention | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 11:38:58 | 2020-07-06 16:30:00 | Fail | Supplied and installed new closer.
MSA-DCS | WA3430692 | MMU, Cell 3 - Rear door lock is sticking | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 11:43:57 | 2020-07-03 09:30:00 | Pass | adjusted cell lock and door strike on cell 3 MMU
MSA-DCS | WA3430721 | U7, G12 - Toilet requires fixing to floor and may require new inlet rubber at back of pan | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 12:18:00 | Pass | Removed broken toilet reinstalled new one
MSA-DCS | WA3430746 | Unit 6 cell N9 Toilet constantly running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 10:02:00 | Pass | Removed old cistern replaced with new
MSA-DCS | WA3430752 | Unit 6 cell A4 Toilet constantly running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 08:15:00 | Pass | Pulled apart cistern replaced outlet washer
MSA-DCS | WA3430755 | Metal Shop - Workshop-Burnt out 3 phase plugs x . Required urgent to carry on with work load | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 12:00:00 | Pass | Replaced damaged 3phase lead in metal shop
MSA-DCS | WA3430759 | Unit 13 - A & C Low water pressure in C12 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 12:00:00 | Pass | Cleaned strainers in basin and shower outlet
MSA-DCS | WA3430762 | Unit 6, Cell D11- Light switch not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-03 10:12:00 | Pass | Replaced broken light switch U6 D11.
MSA-DCS | WA3430764 | Unit 6, Cell B9- Toilet constantly running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 09:06:00 | Pass | Pulled apart cistern replaced outlet washer
MSA-DCS | WA3430771 | Cell C12 - low water pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-13 14:00:00 | Fail | Adjusted water pressure in plumbing duct.
MSA-DCS | WA3430789 | Hakea Justice club, ,emergency lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 12:51:35 | 2020-07-08 14:30:00 | Fail | Replaced 2 x Emergency Exit lights not working Hakea social clubJob Complete 080720 - Once we received Lights
MSA-DCS | WA3430792 | prisoners industries cleaning room Light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 13:30:00 | Pass | Repaired light
MSA-DCS | WA3430830 | PHS, by white board- Light switch unable to turn off | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-02 14:00:00 | Pass | New light switch
MSA-DCS | WA3430837 | Operations, Kitchen Sink Leaking from copper pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-08 15:00:00 | Fail | Rewashers taps
MSA-DCS | WA3430935 | Unit 5, Cell A11- Toilet is not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 16:00:00 | Pass | Installed new push button spring. Adjusted flush button. Ok
MSA-DCS | WA3430943 | re entry house fault RCD | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-03 13:30:00 | Pass | Replaced faulty rcd
MSA-DCS | WA3430970 | Unit 3, D Wing- Shower window is not staying up, metal at right side broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-03 11:30:00 | Pass | NEW WINDOW BALANCES FITTED
MSA-DCS | WA3430977 | Unit 3, C Wing, Window in shower not staying up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-03 10:15:00 | Pass | NEW WINDOW BALANCES FITTED
MSA-DCS | WA3430994 | Outside Unit 2 C Wing, Sterlie Zone- Water Leaking from new Valve- further info below | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 15:01:14 | 2020-07-03 11:21:00 | Pass | Dug up and located leak in pipe replaced section off pipe and back filled
MSA-DCS | WA3430998 | Unit 3, Cell C13- GPO smashed | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-13 15:00:00 | Fail | Replaced damaged gpo and blank plates
MSA-DCS | WA3431005 | Unit 1, Cell A7- Middle & top hinge to cell door are damaged | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 15:11:51 | 2020-07-02 18:00:00 | Pass | Attended site and carried out repairs to the hinges on cell door.
MSA-DCS | WA3431008 | Unit 5, House 10, Room 3- wall mounted split system has error fualt "U4" | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 15:13:19 | 2020-07-03 10:00:00 | Pass | Attended site 3-7-20 0800. AC system servicing unit 5, house 10, room 3 system faulting on a U4 error code. Applied tests and checks to find system to have faulted on a communication error between indoor and outdoor. Checked all applicable electrical connections and incoming voltage and current (ok). Reset system and carried out test operation procedures. System operating correctly. Left site 1000.
MSA-DCS | WA3431044 | Unit 10 D9 Door misaligned (possible change of hinge and re-tapping) | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 13:00:00 | Pass | Supplied and fitted replacement hinges.
MSA-DCS | WA3431052 | unit 1 A18 blocked toilet and sink | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 16:40:43 | 2020-07-03 18:03:00 | Fail | unblocked main drain which cause blockages to the toilet/basin
MSA-DFES | WA3431019 | Training Room & Pump Room- lighting issues as per the below | VFRS Secret Harbour | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-24 12:30:00 | Fail | Arrived at site and signed in at 824 to replace 12fluro fillings with LED, couldn’t find a register. Replace cleaned tested and filled out paperwork. Signed out at 1219.
MSA-DTAG | WA3430464 | L3 JSO Water pooling from the dishwasher on the floor. | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-02 17:01:00 | Pass | Promap faults, correct times : 2/7/20 12.30pm to 1400 pm
MSA-DTAG | WA3430607 | No video signal from any of the lift cameras | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-10-03 13:30:00 | Fail | Install Moxa CAT 6 cables into lift controllers.
MSA-DTAG | WA3430610 | level 1 room 1.07 - card reader faulty | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-02 11:30:00 | Pass | Attended site. Faulty Card Reader on Level 1 Room 1.07, replaced and checked.
MSA-DTAG | WA3430962 | Wireless duress reciever - in fault | Midland Courthouse | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-02 15:27:00 | Pass | Located duress button 2 and 3, both tested correctly. Duress button 1 showing inactive.Located duress button and installed CR2 battery, fault cleared.
MSA-DTAG | WA3431589 | Bio clean in cells | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Cleaning (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-02 18:00:00 | Pass | Job carried out as per work order
MSA-DTWD | WA3430293 | B Block, Room BG20- Edge/corner section of ceiling has dropped & is hanging above walkway | Carlisle Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 02 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-17 09:30:00 | Fail | Ceiling panel is secured.
MSA-DTWD | WA3430355 | A Block, Room A353b, Male toilet- toilet pan has come away from the floor | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 16:00:00 | Pass | Complete
MSA-DTWD | WA3430364 | B block, level 3, Male toilets basin - basin tap cannot turn off completely | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 15:46:00 | Pass | COMPLETED
MSA-DTWD | WA3430489 | Lvl 1, Staff office D115 & print area- Loud bang when lights switced on. No longer working. | Perth Campus B4 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-03 13:30:00 | Pass | Replaced 4x tubes and 1x ballast to fitting in B4. Tested, job complete.
MSA-DTWD | WA3430536 | Kendrew. Kendrew. D block. Level 2 executive kitchen/toilet - cockroaches infestation | Joondalup Kendrew Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 11:30:00 | Pass | Gelled kitchens and toilets in D block-Level 2 and dusted under cupboards
MSA-DTWD | WA3430551 | E Block, Cafeteria- Main in controller to freezer is not functioning | Rockingham Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-03 15:00:00 | Pass | TRAVELLED TO SITE SIGNED IN. REMOVED AND WIRED IN NEWROCKER SWITCH AND CHANGED THE PARAMETERS ON THE CONTROLLER ADJUSTED SET POINT TO -16.5 DEGREES. TESTED OPERATION. FREEZER NOW CYCLES AND TESTED DEFROST. ALL OK.
MSA-DTWD | WA3430555 | C block. C205 - mice infestation | Joondalup Kendrew Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 10:55:00 | Pass | Installed 5 small rodent stations and 10 Ditrac blocks to Room C205
MSA-DTWD | WA3430580 | Level 2, W207 - Repair/Replace faulty switch light | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-09 10:51:00 | Fail | Repalced faulty 3 gang switch in classroom.job completed
MSA-DTWD | WA3430602 | Level 1 library access toilet. Disabled rail requires re fixing to wall | Joondalup Kendrew Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-02 14:15:00 | Pass | Reinstalled handrail
MSA-DTWD | WA3430670 | E block, Ground floor, fire panel - repair/replace faulty smoke detector | Joondalup Kendrew Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-02 15:00:00 | Pass | Attended site - investigated call out at E Block - Zone 3 isolated upon arrival - no alarm activated at this time - isolated FIP & code red - deisolated Z3 - waited 50 minutes - no alarm - returned FIP & code red to normal.
MSA-DTWD | WA3430679 | A block, level 1, A116 & A118 - FCU 16 & FCU 17 require repair to fan coil units as faulty/damage | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-24 15:00:00 | Fail | Obtained parts for a116. Accessed a118 and rectified noise from return air and power issue. Test via controls as directed ok. Accessed a116 and proceeded with fcu 17 fan deck replacement. Installation carried out and repair checked and test run ok. Both units returned to automatic bms controlled service.
MSA-DTWD | WA3430693 | Flat A & Flat D bathrooms - One Cistern in each bathroom leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Materials (PD) | Lane's Plumbing | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-03 11:30:00 | Pass | Repaired leaking cistern
MSA-DTWD | WA3430766 | block 2 ground 2G20 Maint.Officers office.Faulty temperature readings on BMS. | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 16:30:00 | Pass | Replaced burnt out wiring on stage 1 and tested. Ac2 back online
MSA-DTWD | WA3430779 | F block F100 Heavy Fabrication welding bay 35 Midland campus is inoperative and needs replacing | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 15:30:00 | Pass | Attended site and signed in. Located bay 35. Found tagged out faulty switch. Disconnect and removed. Replaced with new 32amp industrial switch. Tested all okay. Job complete
MSA-DTWD | WA3430820 | Main entry door - has a very stiff lock cylinder, require service/repair | Armadale Campus? 45 Commerce Ave | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 10:00:00 | Pass | Main entry - door lock hard to operate.Lock repaired.
MSA-DTWD | WA3430833 | level 3, prior A305 entry into staff area - bottom of glass door frame swings out | Perth Campus B5 | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-06 12:30:00 | Pass | ATTENDED SITEUSED 20x12 BLACK ANGLE 1-300 mm TO SECURE DOOR FRAME4 SCREWS, 4 PLUGS AND 2 RIVETS USED
MSA-DTWD | WA3430946 | A block, level 1, Main EWS panel - Fault on 11 Zones on EWS panel | Leederville Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-03 09:00:00 | Pass | System investigated and all faults have been cleared.
MSA-DTWD | WA3430954 | Shaded area behind AG22- Water bubbling out of the ground | Carlisle Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-06 17:05:00 | Fail | Repair burst water pipe and re instate area
MSA-DTWD | WA3430985 | T block BMS is not responding - see notes | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-03 10:17:00 | Pass | Travelled to site to check if there were any issues with upgrading enteliweb server to windows 10.Spoke with Mike who also had an issue with the energy reports for the Café which had no data sinceMay.Checked & found the copper cube showing offline on the system, checked copper cube & found thepower off, switched on at copper cube & checked on system now online.Checked reports now showing actual data for the last 6 days & average data since it went off in May.Checked enteliweb ver 4.6.128 . Installed Modules – BMS Reporting Ver 4.6.9, PAS Plug-In ManagerVer 4.6.9, Tenant Billing Ver 4.6.3.Enteliweb License I/O Limit 2500 actual 1386License Serial No. ql8V5-65dF6-QzGak-4WEEa-ob5MO-0X5znSoftware Maint Subscription Expiry - Oct 10 2019Spoke with Wing from IT about upgrade found they are not upgrading server just remote PC in L2server room which connects to server via web server so no upgrade of enteliweb is required for thiswork.The current available version of enteliweb is v
MSA-DTWD | WA3431003 | Rooms F4, F5, F6, F38, F36 and H Block Library-Damaged curtains need removing and not replaced | Rockingham Campus | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 12:00:00 | Pass | Removed curtains from Rooms F4, F5, F6, F38, F36 and H Block Library as requested by site
MSA-DTWD | WA3431036 | Cafeteria Kitchen. Tap spout on main sink has snapped off. | Carlisle Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 02 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-03 17:06:00 | Pass | replace broken tap
MSA-MRWA | WA3430316 | Bridge Compound, Ancillary Shed - rooftop ventilator fan blown off bridge inspection garage ancillar | Materials Engineering Branch | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-03 10:15:00 | Pass | Replaced damaged roof vent with new
MSA-MRWA | WA3430350 | outside ground floor - blown lamps | Traffic Operations Centre | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-02 11:21:00 | Pass | Repalced faulty lamps to security lights around site. Repalced faulty lamps in foyer , checked timeclock and pe cell. All working properly job completed
MSA-MRWA | WA3430855 | Lvl 8, Zip water boiler is not working | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 02 Jul 2020 | 2020-07-03 17:00:00 | 2020-07-03 13:33:00 | Pass | REPLACED HOT PUMP ON HYDROTAP ZIP A404040287 LEVEL 8
MSA-MRWA | WA3430933 | 812 only 1 of 3 tubes working in light fitting, please inspect and rectify | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 02 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 09:00:00 | Pass | Attended site. Replaced multiple fluros in Rm 8.12, replaced ballast and Fluro on lvl 7 as shown by site. Complete.
MSA-DCA | WA3431723 | Plant room 4 - mutiple BMS alarms after power outage | Art Gallery of WA - James St - Main Building (Block B)-Level 4 - Roof Ventilator Plant | GMP-BR | Building | General Building (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 03 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 13:25:00 | Pass | Attended call-out. Power outage in Perth CBD caused mechanical equipment failure, requiring manual resets. Reset Chiller 1. Pneumatic Station and stand alone unit both reset. Steam Boiler Unit 1 and 2 reset on gas valve. Monitored operation of system. ETS in LOCAL mode for Museum testing. All alarms cleared.Closed job.
MSA-DCA | WA3431822 | Water inside shaft from roof | State Library of WA-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-06 17:10:00 | Pass | Replaced leak pipe
MSA-DCA | WA3432062 | security control room fault on the ewis fire panel | State Library of WA-Main Building-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 0 | CLOSE | 03 Jul 2020 | 2020-07-03 20:52:04 | 2020-07-03 18:00:00 | Pass | Charger fail fault on arrival, reset and waited around for 15 minutes. Fault did not reappear.
MSA-DCS | WA3431282 | Car dax Gatehouse door gate control signal gone down and sliding door override | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Jul 2020 | 2020-07-04 05:16:39 | 2020-07-06 10:27:00 | Fail | Picked up parts, travelled to Karnet prison farm, replaced and mounted replacement KVMs, tested fully operational.
MSA-DCS | WA3431382 | WWTP screening pit leaking at pipe before pit | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-27 15:00:00 | Fail | Remove damaged pipe work and fittings and replace with new.
MSA-DCS | WA3431385 | Security foyer light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-03 13:00:00 | Pass | Investigate and repair security foyer light
MSA-DCS | WA3431483 | Entry building - Foyer door has droped, scraping on the floor tiles and jamming up | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 15:30:00 | Pass | Attended site and carried out repairs to the main foyer entry door.
MSA-DCS | WA3431486 | INF (10)- Hose on kitchen tap is damaged | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 13:00:00 | Pass | Repaired burst section of wash down hose. Tested.
MSA-DCS | WA3431487 | Unit 14, A Wing, Cell A02- shower seal is leaking causing bedding & mattress to get wet | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-09-03 10:45:00 | Fail | SHOWER RE SEALED
MSA-DCS | WA3431491 | Unit 14, A & C Regi fridge tripped out, cannot reset on main board | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 12:45:00 | Pass | Fridge running. Fault due to pests. All ok
MSA-DCS | WA3431492 | Unit 14, Cell A12- Toilet wont flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 15:00:00 | Pass | Tested toilet multiple times. No issues found.
MSA-DCS | WA3431497 | Between Assessments and Courts - lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-06 10:00:00 | Pass | Repaired lights
MSA-DCS | WA3431548 | Front Gate- Entrance door to prison- Door not locking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Jul 2020 | 2020-07-04 08:40:15 | 2020-07-03 12:45:00 | Pass | Electronically working ok. No issue with custodial strike. Made adjustment to door closer. Tested ok.
MSA-DCS | WA3431551 | Unit 5, B & C Wing- Heater Detached from Upper Landing | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-03 14:00:00 | Pass | Re-mounted U5 B+C Wing heater.
MSA-DCS | WA3431561 | Kitchen, Rational Oven No 2- 2x lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-03 14:40:00 | Pass | Repair connection at lamp junction. Test both lamps working ok.
MSA-DCS | WA3431563 | Stores, Kitchen - Billi unit, filter fault, filter requiring change as affect heating of unit | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 09:15:00 | Pass | Replaced filter, plv and safety solenoid
MSA-DCS | WA3431566 | Unit 2, B Wing, Cleaning cupboard- Tap has snapped at seal | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 14:00:00 | Pass | Inspected job. Reinstalled tap which had been removed from wall. Tested.
MSA-DCS | WA3431618 | Unit 14, Cell A8- Sink/shower blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 13:00:00 | Pass | Tested sink and shower drains multiple times. No issues found
MSA-DCS | WA3431623 | Unit 14, Cell A11 - shower has low pressure. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 16:00:00 | Pass | Cleaned shower head strainers to clear blockage.
MSA-DCS | WA3431657 | Lenard unit C wing asses damage make safe and carry out repairs | Banksia Hill Detention Centre | WSM-BR-RC | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-10-19 13:52:00 | Fail | MAJOR WORKS CARRIED OUT FOR RIOT DAMAGE. INCLUDING ELECTRICAL, CLEANING AND MULTIPLE RE GLAZING OF WINDOWS
MSA-DCS | WA3431683 | boiler room lock on the door has ceased | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-06 13:15:00 | Pass | Replaced ceased lock on Boiler room Door ( lock was missing from door )supplied new deadlatch and double door strike keyed to Prisons System
MSA-DCS | WA3431710 | Gardens W/S - broken GPO's | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-10 10:00:00 | Pass | Investigate and replace gardens workshop broken gpos
MSA-DCS | WA3431732 | Unit 2, lower outside landing ablutions trough cabinet rusted | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 12:00:00 | Pass | Supply and install new trough in lower landing ablution block - unit 2
MSA-DCS | WA3431747 | Unit 1, Huts 5,10,13,21 & diary hut fire cabinets faulty | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-08-11 12:32:00 | Fail | Multiple replacements carried out - further work required, manager not available to approve replacements cabinets will need to return.
MSA-DCS | WA3431748 | Unit 13 - D6 shower head leaks, constant drip. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-09 08:00:00 | Pass | Replaced leaking spindle.
MSA-DCS | WA3431751 | Visits area- Heating doesn’t seem to be working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-22 09:15:00 | Fail | Replaced cable and test ran unit. Unit fully operational at time of departure.
MSA-DCS | WA3431756 | Unit 13 - A3 sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 15:00:00 | Pass | Plunged basin to clear blockage
MSA-DCS | WA3431759 | Unit 13, Cell D13- Shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 17:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3431761 | Unit 13, Cell D1- very low shower pressure. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 16:00:00 | Pass | Cleaned basin and shower strainers.
MSA-DCS | WA3431762 | Unit 13 - A9 shower glass still got leak on right hand side | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-16 15:00:00 | Fail | SHOWER SCREEN RE SEALED
MSA-DCS | WA3431767 | Gardens office - Broken light fitting | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-03 15:30:00 | Pass | Investigate and replace broken light fittings in gardens office
MSA-DCS | WA3431771 | Reset Visits Centre, Roof leak above kitchen | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-09-04 14:22:00 | Fail | REPAIR SARKING, SEAL LOCAL VENTS, ADJUST FLUES, REPLACED SHEETING
MSA-DCS | WA3431883 | vegi prep W/S the potato rumbler is not working properly ,belt slipping | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-07 11:00:00 | Pass | Vegie Prep potato rumbler faulty. Check peeler & controls. Dismantle, repair pulley drive. Assemble & test.
MSA-DCS | WA3431925 | Unit 2, the 3 dongas hot water issues not heating correctly | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-08-13 07:00:00 | Fail | Removed tempering valves and installed a thermostatic mixing valve next to hot water systemIn cage
MSA-DCS | WA3431930 | Admin/Stores, roof leaks under the ridge capping the entire lenght of building | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2021-06-28 08:00:00 | Fail | seal ridge capping and sheeting at approximate/area leak may be penetrating
MSA-DCS | WA3431954 | Perimeter power supply fault | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Jul 2020 | 2020-07-04 13:59:11 | 2020-07-06 11:30:00 | Fail | Traced fault to the input on SM8 in Obs Post 6. Swapped wiring to unused input. Altered programming. Power supply fail alarm tested ok.
MSA-DCS | WA3431958 | zone control 2 cannot open any doors electronicly | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Jul 2020 | 2020-07-03 18:06:36 | 2020-07-03 17:00:00 | Pass | Reed switch magnet on one of the gates was loose. Removed one screw and drilled out one rusty screw. Replaced with thicker screws. All 4 gates tested ok. Parts used:Consumables
MSA-DCS | WA3431995 | Reception- Door not latching closed, strike plate appears out of shape | Mandurah | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 10:00:00 | Pass | Attended site and carried out repairs to the damaged striker plate on door frame.
MSA-DCS | WA3432056 | Essential Medication Area external door not securing properly | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 11:00:00 | Pass | Replaced faulty lock.
MSA-DCS | WA3432078 | self care unit, end of B wing , hot water coming out from foundation (water leak) | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 03 Jul 2020 | 2020-07-03 21:33:14 | 2020-07-07 11:00:00 | Fail | Investigated job. Collected parts and tools. Removed concrete. Dug up pipe. Repaired. Tested. Filled hole. Reconcreted hole. Cleaned sand from spindle inside control.
MSA-DFES | WA3431488 | Rear engine room door has rust coming through on the bottom frame | Butler Career Fire Station | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 03 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-07 09:15:00 | Pass | Technician attended the site of Butler Fire Station Engine Room rear doors W23747 & W23748 on 07/07/2020. Noticed doors had already been repaired on a previous occasion. Checked doors for any holes that may be allowing water into the frame and rotting it out from the inside, doors seemed to be sealed ok and the rust looks to be surface rust only. Then sanded and filed all the rust areas and drilled a number of holes to the inside of the frame to release any water that may be getting in, re-galvanized all the repaired areas of the door. It could be the close proximity to the ocean may be a factor in causing the rust. Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3431571 | ground entry door not closing properly-see notes | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-03 11:00:00 | Pass | Repositioned striker plate and tightened fixings
MSA-DFES | WA3431601 | leaking tap outside next to washing machine. Please check taps and shower heads in dorm & station | Butler Career Fire Station | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 12:16:00 | Pass | Replacing taps at the laundry trough
MSA-DFES | WA3431705 | Ground floor Security desk Pacom system is not operating | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 03 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 10:45:00 | Pass | 6/7/20 - Dean SimpsonRestarted the GMS server as there was no communication connection between the server and the ground floor workstations.All tested ok.
MSA-DFES | WA3431776 | Boom Gate – applied Training boom gate staying open/up | FESA RHQ - Forrestfield | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-07 14:30:00 | Pass | 7/7/20 - Dean Simpson, Ryan VestyInvestigated boom gate not closing.Found 2 door controller to be faulty.Replaced and tested all ok.
MSA-DFES | WA3431929 | Admin, ground level, Training Services Room (KaTS) - External door is not unlocking. | FESA RHQ - Forrestfield | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-07 16:30:00 | Pass | 7/7/20 - Dean Simpson, Ryan VestyInvestigated issue with door not unlocking.Configuration of Reader 10 had changed, reset and tested. All working ok.No call out fee as already onsite.
MSA-DFES | WA3432051 | billi water filtration systen tap is not working | DFES Regional Office - Joondalup | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 11:33:00 | Pass | Replaced inlet and dual solenoids and level sensors assynew issue developed after first repairs on 7.7.2020- tech attended using same WO number but issue was not related - new XL Tap was needed and installed
MSA-DTAG | WA3431580 | Near front entrance-Alarm is sounding near front entrance-see notes | Rockingham Justice Complex | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Jul 2020 | 2020-07-03 13:03:36 | 2020-07-03 12:19:00 | Pass | Travelled to rockingham court, alarm is being caused by entrance access door, Dorma is currently onsite workin g on door, all access control equipment operating correctly. No further action is required.
MSA-DTAG | WA3431631 | Cameras down & unable to open doors remotely for both SAT & DMJC | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 03 Jul 2020 | 2020-07-03 13:53:03 | 2020-07-03 11:30:00 | Pass | Job completed - Attended site. Host down at SAT, started up and turned on VM Software. (There has been a Quote submitted to upgrade Servers)
MSA-DTAG | WA3431634 | Ground floor, male staff toilets - Hand dryer continually on | Perth Children's Court | GMP-BR-HO | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-22 08:30:00 | Fail | Job complete
MSA-DTAG | WA3431639 | Near front entrance-Alarm is sounding near front entrance-see notes | Rockingham Justice Complex | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 03 Jul 2020 | 2020-07-03 14:01:53 | 2020-07-03 12:50:00 | Pass | 1096382. Call to site, attend to auto door. Locate and replace failed components due to corrosion. Setup and test operational and safety features - all okay.
MSA-DTAG | WA3431640 | SAT ‘In Session’ security button on Hearing room 5:06 is not working (intermittent). | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-03 12:00:00 | Pass | Attended site. Checked all In Session buttons on Level 5.No fault found. Job completed.
MSA-DTAG | WA3431891 | L5 court 57 Water fountain near Court 57 not draining properly | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 15:03:00 | Pass | Drain is completely blocked needs a plumber to attendAll hard plumbed 3 inch copper pipe
MSA-DTAG | WA3431960 | Electronic gate to secure carpark compound is jammed open | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 03 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 16:35:00 | Pass | Inspected gate and found pe sensors faulty due to water damage. Replaced sensors and set up all ok at time of test.
MSA-DTAG | WA3432029 | Custody Carpark Sallyport carport door does not close correctly – very slow see notes | Perth Children's Court | GMP-BR-HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 03 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 07:00:00 | Pass | Still operational but recommend new drive.
MSA-DTWD | WA3431400 | A Block, level 1, Switchboard Opp security - Exterior Lighting not working A Block | East Perth Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 03 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 13:30:00 | Pass | Job complete
MSA-DTWD | WA3431500 | E Block, Room E617, Male toilets - 2nd cubicle blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-03 12:15:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3431522 | C Block, Room CG40- Corner window CG40 is extensively cracked | Mandurah Campus (formerly Peel) | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-15 16:30:00 | Fail | ATTENDED SITE, SECURED BROKEN GLASS PANEL WITH 1SQM OF FILM RETURN TO SITE AT LATE DATE AND REGLAZED6MM CLEAR TOUGHENED SAFETY GLASS 1- 571 X 1425 TINTING SUPPLIED AND FITTED TO MATCH
MSA-DTWD | WA3431569 | A Block, Room AG03- Card Reader or network not working | Mandurah Campus (formerly Peel) | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 16:00:00 | Pass | IT AG03 room not allowing access. RAS 11 offline. Could not find location. Left as is. Client to search for RAS 11 location
MSA-DTWD | WA3431688 | L1 Lifts 5 & 7 Lift not working | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 03 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-03 15:00:00 | Pass | When responding to the callback dated 03.07.2020, the Schindler Technician found a problem with thier equipment. Components inrelation to floor selection were faulty. Following our attendance, the equipment was left in service.
MSA-DTWD | WA3431708 | Main Power Room - 25Ab automatic power switch for building failed to start | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | NILSEN (WA) PTY LTD | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-06 09:00:00 | Pass | ATS change over checks/investigation
MSA-DTWD | WA3431722 | S/W & S/E external ring road ¦ Blocked road sumps | Midland Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | High Tech Maintenance | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-09 10:00:00 | Pass | Ring Road sumps were blocked due to tree roots growing through the pipes, contractors removed what they could. Water drained away from the road once tree roots were cleared.
MSA-DTWD | WA3431801 | Block 1, Alarm panel reading fault (advised by Education Security) | Thornlie Campus | GMP-BR | Security | Security Management System (SE) | CONNECT SECURITY SYSTEMS | 1 | CLOSE | 03 Jul 2020 | 2020-07-04 11:36:39 | 2020-08-11 12:57:00 | Fail | Returned to site once approval recieved on remedial work. High Gain Antenna installed on external of Block 1 to improve signal to Alarm Dialler.
MSA-DTWD | WA3431869 | D block room D2 timer light switch is faulty | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 09:30:00 | Pass | Replaced faulty timed light switch in D2. All now working. Informed site
MSA-DTWD | WA3431881 | outside field ligts not working in the Turf area | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-14 15:00:00 | Fail | Attended site and signed in. Located faulty pole lights as per AJ checked out. Unbolt the lock bolt of swing pole, 3 were seized and required a lot of work to remove and replace. Tip over poles to access heads. Replaced 4 x lamps and 3 x ignitors. Replaced cabling from base to head on 1 pole. Re stood up poles and bolted up with lube to be able to access later. Tested all okay. Job complete
MSA-DTWD | WA3432003 | LEVEL: 1 ROOM/OFFICE: D110 repair tagged out power point. | Perth Campus B4 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 03 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-20 09:30:00 | Fail | Attended site, repaired gpo in room D110, tested, job complete.
MSA-DTWD | WA3432010 | BLD 838 Classroom 3 & 4 toilets at back- Taps loose in 2 vanity basins | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 03 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 14:00:00 | Pass | Repaired loose tap
MSA-DCA | WA3432097 | Whole site. power is off to certain areas through out the building. | His Majesty's Theatre-Theatre Building | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 0 | CLOSE | 04 Jul 2020 | 2020-07-04 12:34:55 | 2020-07-04 11:30:00 | Pass | Unplanned western power outage
MSA-DCA | WA3432105 | Level 4 - Plant room - Numerous BMS alarms are in alarm. due to power outage. | Art Gallery of WA - James St-Main Building (Block B)-Level 4-Plant Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 04 Jul 2020 | 2020-07-04 12:56:33 | 2020-07-04 14:00:00 | Fail | Spoke with call roster team. Recieved breif instructions about the call out. Travelled to site, whilst informing security I was on my way to site. Investigations found R.O and the steam plant in fault as there was a power outage across the Perth CBD. Leaving all humidifiers needing manual reset. After checking the BMS, I went ahead and reset the R.O and steam plants. I waited for the tanks to fill up as per the run up procedure. Once equipment was fully reset and up an running I went to each humidifier and manually rest all equipment via its controller. A quick check on the BMS stated all Alarms had been cleared and operations were commencing.
MSA-DCS | WA3432108 | Hot water leaking in unit7 out side B5 .SJ | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 04 Jul 2020 | 2020-07-04 13:18:22 | 2020-07-07 11:00:00 | Fail | Job has been repaired on 7/7/20 under work order Wa 343 2078. This was a secondary call out for the same job.
MSA-DCS | WA3432109 | Required a Locksmith for Cashier office in the Main gate | Hakea Prison-Main Gatehouse | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 1 | CLOSE | 04 Jul 2020 | 2020-07-05 08:37:37 | 2020-09-06 07:30:00 | Fail | Obtained key to test lock. Unable to find fault - operation normal
MSA-DCS | WA3432136 | Energised fence test has failed | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Jul 2020 | 2020-07-04 14:25:35 | 2020-07-04 13:12:00 | Pass | Contacted site, who advised Gallagher fence showing 0V.Officers had attempted to reset PC but accidentally switched off.Attended site, switched workstation back on.All fence zones showing 0V, asked if anyone was or been working on the system. Officers advised no.Rearmed electric fence controllers, all showing 7kv or above. Ran report to find officers had accidentally switched alarm zones off at 5:50am 4/7/2020
MSA-DCS | WA3432159 | unit5 B15 unable to unlock the main lock of the cell | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 04 Jul 2020 | 2020-07-04 17:10:50 | 2020-07-06 15:00:00 | Fail | Job completed - After Hours attendance 04/07/2020. Gained entry to cell. Parts required.On site 06/07/2020. Supplied and installed replacement lock
MSA-DFES | WA3434159 | Retrospective work order - Z22 REED AT BAY 1 REAR DOOR. | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 04 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-04 12:03:00 | Pass | EXTERNAL CHECK CARRIED OUT. NO OFFENCE DETECTED. ALL APPEARS SECURE. NO PERSONS FOUND ONSITE.
MSA-DCA | WA3432291 | State Library of WA - Lift 6 srruck in mezzannine level | State Library of WA | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 05 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-05 10:52:00 | Pass | Lift at M, No T3A, 146 error. Found gov electrical tripped. Reset and tested. Visit completed
MSA-DCS | WA3432292 | SITE COST Unable to use Security monitors & Screen because Mouse is faulty | Wooroloo Prison Farm-Gatehouse | WSM-BR-SITE | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Jul 2020 | 2020-07-05 12:44:17 | 2020-07-05 10:11:00 | Pass | Mouse not working, reinstalled driver and tested CCTV system.All working
MSA-DCS | WA3432318 | Day Room Unit 4 The fire alarm keep going off | Karnet Prison Farm | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Jul 2020 | 2020-07-05 17:03:17 | 2020-07-05 15:13:00 | Pass | Attended site for fire alarm. When arrived found manual call point broken reset and all back to normal working condition when left
MSA-DCS | WA3432329 | Watertank leaking in the kitchen | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 05 Jul 2020 | 2020-07-05 18:38:16 | 2020-07-06 11:30:00 | Fail | Supply and install new pressure vessel on hot water supply in kitchen plant room.
MSA-DCS | WA3432336 | zone 9 IM, zone 9 OX, zone 11 OM and zone 13 OX constantly activating by itself | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Jul 2020 | 2020-07-06 15:29:12 | 2020-07-08 15:30:00 | Fail | Rectified and fixed multiple internal zones problem, job completed.
MSA-DCS | WA3432337 | zone 3 IM has broken cables | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Jul 2020 | 2020-07-06 15:35:04 | 2020-07-07 13:30:00 | Fail | Rectified and fixed damage microphonics cable, job completed.
MSA-DCA | WA3432526 | main fire panel needs to be isolated-Please call Reese with ETA | King Street Arts Centre-Main Building-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 06 Jul 2020 | 2020-07-06 11:24:46 | 2020-07-06 14:50:00 | Fail | 8.15am 6/7/20 MBIsolate whole system at customers request to allow entire building sanitisation spraying.Re-visit required around midday to de-isolate.6-7/20 MBDe-isolated all zones and returned system to normal working order.
MSA-DCA | WA3432561 | Main Reception - Fire Panel Fault on Fire panel due to Power Surge -see notes | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 06 Jul 2020 | 2020-07-06 17:00:00 | 2020-07-06 08:30:00 | Pass | Performed loop test on panel and reset FIP.Fault caused by power surge.
MSA-DCS | WA3432528 | main control room monitor for cell call is down | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jul 2020 | 2020-07-06 11:25:17 | 2020-07-06 09:00:00 | Pass | Attended Control Room, Monitor showing blue screen and “No input signal” message. Checked output signal from Tacera PC in Crypt Equipment room, signal displayed on local monitor. Returned to control room checked monitor “Input” setting and found the monitor set to video, changed to PC and restored picture to screen.
MSA-DCS | WA3432534 | unit 10 B10 cell door cannot be opened - prisoners in cell | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 06 Jul 2020 | 2020-07-06 11:33:05 | 2020-07-06 15:30:00 | Fail | job completed - 06/07/2020. Forcibly open cell door to enable access. Parts required.On site 06/07/2020. Supply and install replacement lock.
MSA-DCS | WA3432539 | kitchen sink near urn leaking from seal | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-13 08:41:00 | Fail | nil
MSA-DCS | WA3432547 | House 11 bathroom Unable to turn light off – switch faulty | Boronia Pre-release-AP23 - Prisoner Accommodation House 10 and 11-Ground Floor | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-08 08:30:00 | Pass | Investigate and replace house 11 bathroom switch
MSA-DCS | WA3432602 | Unit 2 - B & D Hot water urn is not heating the water. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-06 10:23:00 | Pass | All working on arrival and working after testingCould be a usage issue
MSA-DCS | WA3432607 | Unit 6 - C7 Toilet barely flushes and takes 40 minutes plus to refill | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 13:00:00 | Pass | Replaced blocked inlet valve
MSA-DCS | WA3432613 | Unit 13, B & D - 5 X Windows in B/D dayroom smashed including wing office window and interview room | Casuarina Prison | SPA-BR | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 0 | CLOSE | 06 Jul 2020 | 2020-07-06 12:24:09 | 2020-09-15 12:00:00 | Fail | ALL BROKEN WINDOWS REPLACED
MSA-DCS | WA3432635 | Unit 14, D12 - shower leaking between glass and tiling onto bottom bunk | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-27 15:00:00 | Fail | RESEALED SHOWER SCREEN
MSA-DCS | WA3432645 | CCU (11) - D4 Cell D4 drain is flooding all the time. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 15:00:00 | Pass | Cleaned shower head and adjusted water pressure.
MSA-DCS | WA3432666 | turner B wing smashed window on door ( rear of living area) approx 650x650 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-20 11:15:00 | Fail | RE-GLAZE SMASHED WINDOW
MSA-DCS | WA3432670 | Turner B wing-smashed window approx 450x300 | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-20 13:00:00 | Fail | RE GLAZE SMASHED WINDOW
MSA-DCS | WA3432680 | Gate House - West door 7 is closing too hard, needs adjustment to prevent damage | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-13 11:30:00 | Fail | Attend site adjust door closer settings.On site recheck door and closing settings.
MSA-DCS | WA3432690 | Market Gardens back gate locked jammed | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 12:30:00 | Pass | Open jammed lock and service
MSA-DCS | WA3432698 | Unit 3 - C7 Sink drain blocking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 17:00:00 | Pass | Plunged basin to clear blockage blockage.
MSA-DCS | WA3432715 | Unit 13, B/D dayroom - regir oven damaged | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-07 09:55:00 | Pass | Straighten Door lock mount, reassemble doorlock. straighten top right hinge plate, refit door, adjust hinges & door lock/strike. Check door is sealed to door seal ok. Test Control panel operation ok. Left unit operational & useable.
MSA-DCS | WA3432716 | Unit 13, Single side gate - lock jamming | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-22 12:00:00 | Fail | Spray lock with anti seize.Open jammed lock and service.
MSA-DCS | WA3432717 | Unit 2 - B & D Floor polisher/ buffer electric cord ripped out. | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-06 15:00:00 | Pass | Investigate and repair Unit 2 B&D floor polisher
MSA-DCS | WA3432737 | Amenities, Gym, male toilet - lekaing from bae of bowl | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-14 14:00:00 | Fail | Inspected job. Collected parts. Installed new cistern and tested.
MSA-DCS | WA3432752 | Amenities, male change rooms - shower taps male side constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-13 13:00:00 | Pass | Installed 2 x new spindles in shower taps
MSA-DCS | WA3432771 | unit 14, B/D - kitchen tap handle comes off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-08 17:00:00 | Pass | Reattached and retightened all kitchen taps.
MSA-DCS | WA3432772 | Amenities,Gym, Male Changeroom- Light out in shower | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-07 08:30:00 | Pass | Repaired faulty lights in amenities building make toilets
MSA-DCS | WA3432776 | Unit 1, A Wing, Cell A13- toilet running constantly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 14:00:00 | Pass | Adjusted flush button. Changed outlet rubber.
MSA-DCS | WA3432777 | Unit 4, A12 - toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 10:00:00 | Pass | Replaced blocked inlet valve in cistern.
MSA-DCS | WA3432781 | Unit 2, A wing, A13 - window in A13 is broken doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-08 15:00:00 | Pass | WINDOW MECHANISM REPAIRED
MSA-DCS | WA3432782 | Kitchen- Mixer tap broken at base, fell apart | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-13 12:00:00 | Fail | Investigate job. Collected parts. Replaced broken mixer with new one.
MSA-DCS | WA3432787 | Visits SW camera not recording or not correclty configure for viewing recordings | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 09:53:24 | 2020-07-07 08:00:00 | Pass | Attended Security SO Office Checked Workstation and confirmed that staff were able to review / playback previously recorded video.
MSA-DCS | WA3432791 | Security cameras keep dropping out | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 09:18:00 | Pass | Investigated fault, repaired multiple camera digital feed network faults and recording faults.monitored for correct operation and tested OK.Job Complete
MSA-DCS | WA3432793 | Unit 13 - A1 Sink in A01 leaking sink badly. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 09:00:00 | Pass | Replaced leaking spindle in shower.
MSA-DCS | WA3432820 | Unit 4,B Abloutions - toilet pan is cracked (bowl) | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-14 11:00:00 | Fail | Complete
MSA-DCS | WA3432829 | reset building outside prison HWS faulty-contractor on site | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 10:12:04 | 2020-07-06 14:15:00 | Pass | COMPLETED
MSA-DCS | WA3432871 | staff lunch room Bain marie keeps tripping out | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 10:37:11 | 2020-07-07 10:00:00 | Pass | Replaced faulty rcd
MSA-DCS | WA3432891 | Unit 14, Cell A5- Toilet is not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 10:00:00 | Pass | Flushed and debris from inlet valve and cistern.
MSA-DCS | WA3432894 | Unit 14, Cell C1- sink tap no pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-14 20:00:00 | Fail | Unblocked strainer inside basin tap.
MSA-DCS | WA3432946 | Unit 1, Cell C4- Sticky toilet button | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 16:00:00 | Pass | Realigned flush button. Tested
MSA-DCS | WA3432952 | B1 & B2 service duct - hot water mixer has failed / temp can not be adjusted | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 11:26:53 | 2020-07-06 14:14:00 | Pass | Renew tmv valve
MSA-DCS | WA3433109 | Central control room - zone 8B microphonics in constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 12:27:29 | 2020-07-06 15:30:00 | Pass | No 1M Ohm resistance measured at IF cabinet. Traced fault to a break in the cable. Repaired cable join. Replaced cable ties. Tuned and tested ok. Parts used:Consumables
MSA-DCS | WA3433114 | No power in half of building | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 06 Jul 2020 | 2020-07-06 16:31:08 | 2020-09-04 09:00:00 | Fail | Install new upgraded sub mains from main office dB to db3 and upgrade main switch for new sub mains.Carry out all electrical tests
MSA-DCS | WA3433131 | Unit 6, Plant Room- Burst pipe in roof space | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-06 16:10:00 | Pass | Investigated leak. Collected parts. Repaired burst hot pipe. Tested. Relagged pipe. Bleed air from system.
MSA-DCS | WA3433133 | L4 Door slamming on Level 4 - Meeting Room | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 13:00:00 | Pass | Attended site and carried out repairs to the hydraulic door closer which was not operating correctly
MSA-DCS | WA3433135 | Unit 6, Plant Room- disconnect pump motor on hot water circulating system for repairs | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-08 13:30:00 | Pass | Disconnected reconnected and tested pumps in unit 6 plant room.
MSA-DCS | WA3433176 | mens toilet - leak in roof. there is a slow leak in the ceiling of the men' toilets, | Rockingham Justice Complex | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-23 15:00:00 | Fail | Attended site and assessed what repairs where required.Obvious roof leak but due to height and pitch of roof EWP required to carry out inspection and repair.Reattended site with EWP and carried out inspection and repairs to damaged and cracked roof tiles.
MSA-DCS | WA3433177 | ground kitchen Hydro tap(hot/cold filtered water unit) does not dispense hot water. | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-07 17:00:00 | Pass | replaced hot pumpREPLACED ZIP HOT PUMP AND PERFORMED MINOR DESCALE ZIP HYDROTAP A40191322B GWYNNE LEA BUILDING
MSA-DCS | WA3433232 | Unit 14, Cell D13- bottom bunk light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-08 11:30:00 | Pass | Repaired faulty lights in unit 14 d13
MSA-DCS | WA3433241 | Ladies toilet - one of the toilets not flushing | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-06 15:19:00 | Pass | COMPLETED
MSA-DCS | WA3433249 | Unit 14, D13 - has a blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 11:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3433256 | Unit 6, Control Room - Pipe burst causing possible water damage on electrical panels & cameras | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 08:00:00 | Pass | Replaced water damaged MDAS Receiver once enclosure and conduit dried out. Installed new CAT 6 cable to replace water damaged Coaxial cable & connectors. Used silicon sealer to seal around conduit floor penetrations in area affected by water leak to try and prevent reoccurrence.
MSA-DCS | WA3433257 | female toilet - Sink keeps getting blocked/clogged (faulty drain pipe) | Walcott Centre (Central West Metro ) | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 13:15:00 | Pass | Complete
MSA-DCS | WA3433263 | Omnitrax zone 4,5,10,11,16,22 not activating | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-15 18:48:00 | Fail | Checked OT zones and found zone 4 and 11 have been disarmed.rearmed and conducted periemter test, all OT zones activated.calibrated all zones and confirmed correct operation of OT from control room
MSA-DCS | WA3433268 | Unit 6, Control Room - Pipe burst causing possible water damage on electrical panels & cameras | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-06 15:00:00 | Pass | Investigated and repaired water logged electrical equipment in unit 6 after flood
MSA-DCS | WA3433303 | Unit 14, A6 - hot water tap loose, spinning around. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 12:00:00 | Pass | Realigned and retightened hot tap spindle.
MSA-DCS | WA3433378 | Pod, no cameras or cell calls activating | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Jul 2020 | 2020-07-06 20:39:34 | 2020-07-06 20:15:00 | Pass | Attended site and investigated the faults.Rectified the network problem on IndigoVision Video Wall in Control room.Rectified problem with system error on officer cell call unit CI-3210 in CCU.Conducted test.All ok at departure.
MSA-DFES | WA3432592 | door between duty room & engine room - Door is broken, isnt closing | CFRS Maddington | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 17:00:00 | 2020-08-10 15:30:00 | Fail | 7/8/20 -Works were scheduled for Thursday 6/11/20 - unfortunately the team member scheduled to do the job was off sick - Station advised and works rescheduled for Monday Aug 10Works now complete
MSA-DFES | WA3432804 | Kitchen, Room 15 - Fluro light is flickering | CFRS Perth | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 16:00:00 | Pass | Complete
MSA-DFES | WA3432808 | Retic broken under pavers in yard | CFRS Perth | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-07 08:15:00 | Pass | Dom Coniglio 6/7/20 4.05 pm - 5pm & Call OutDom Coniglio 7/7/20 7am - 8.15 am & Call OutRetic Parts $97
MSA-DFES | WA3432819 | Engine Room Bay 1 rear door- is not operating correctly | CFRS Welshpool | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-13 12:00:00 | Fail | Technician attended the site of 380 Welshpool Rd, Welshpool, WA, Engine room on 06/07/2020. Following full test and inspection of door components found fault to be broken spring on RHS of rear engine room door bay 1, quote for replacement. While on site client asked to have a look at the remote setup as none of their remotes are working, however the technician wasn't able to rectify the issues with the remotes. Electrician to attend ASAP.07/07/2020 Technician Re-attendedAttended site to investigate why remotes were not working for doors and has found out that receiver card is not operational. It was strange to have power but no LEDs to 2 cards. So he changed where the power supply was coming from and card was working as it should. Technician then reinstalled existing card to alternative power supply and it also worked fine.Technician retured on 13/07/2020 and removed damaged components, S&I new springs and retention. Full test and inspection of door components completed p
MSA-DTAG | WA3432656 | comms room Power issue to AV rack-see note | Armadale Courthouse | GMP-BR-HO | Security | Monitoring (SE) | AWB Co. | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 14:00:00 | Pass | Attended site and signed in. Checked UPS system I’m Comms room. Found ups was off. Rest and ensured all plugs are connected corrected. No other faults where found. All now up and running. Informed staff
MSA-DTAG | WA3432675 | DMJC intercom fault, flashing no sound | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-06 10:00:00 | Pass | All Intercoms offline. Checked Interface Unit on Level 9 at SAT and Level 10 DMJC, reset Intercom Serverand checked. (Faulty with VM at SAT).
MSA-DTAG | WA3432792 | Basement, custody - Pacom cameras not working after power failure Friday | Perth Children's Court | GMP-BR-HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 15:00:00 | Pass | Power failure reported on arrival. System Reset. Test OK.
MSA-DTAG | WA3433193 | Service duct behind door in the ambulant toilet Water dripping/leaking out of the pipes | Armadale Courthouse | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 10:30:00 | Pass | COMPLETED
MSA-DTAG | WA3433376 | Kitchen tap faulty, due to electrical shock, further info below | Rockingham Justice Complex | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 09:15:00 | Pass | Tested tap and added new earthing to sink and water pipes - all safe
MSA-DTWD | WA3432568 | No 1 lift in the Tower Block is stuck on level 2 | West One Services | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 09:30:00 | Pass | Job completed - Upon arrival at site, the technician performed the following: DOORS/ENTRANCES - DOOR SILL - COMPONENT DUSTY, CLEANED
MSA-DTWD | WA3432605 | A block, level 3, A311, A316 - Repair faulty/damaged cupboard doors in Laboratory Operations lab | East Perth Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-15 10:30:00 | Fail | Attend site and inspect cupboardsneeds new hingesleave site and source hingesreturn to site and install hingestest and commission everything in good working order
MSA-DTWD | WA3432728 | D block, room DG27 - air con leaking amounts of water through roof. Ceiling ect all saturated | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-07 09:00:00 | Pass | Arrived on site and signed in. Completed SWMS, assisted by Dave, Started Checks on operation and controls, cleaned filters where required, on Blocks A,B,D,F &H Block, cleaned up and completed paperwork and signed out.
MSA-DTWD | WA3432813 | Lvl 1 - Security light damaged | Perth Campus B7 | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 09:51:00 | Pass | Been advised by site to isolate and make safe of light. Light been vandalised by vandals
MSA-DTWD | WA3432827 | Lvl, Laneway - Security light blown | Perth Campus B3 | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 09:15:00 | Pass | Attended site and signed in. Located faulty light. Tested and found light not repairable. Picked up a new light and replaced. Tested all now working. Informed site
MSA-DTWD | WA3432834 | F Block, F001 Library - 2x roof leaks | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 15:05:00 | Pass | Leaks to library x 2 - found box gutter sumps blocked and box gutter holding water - cleared blockages.
MSA-DTWD | WA3432893 | D block, Ground - Lift went to level 2 Fell to ground level and stopped about 6 inches from floor | Joondalup Kendrew Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 06 Jul 2020 | 2020-07-07 17:00:00 | 2020-07-06 12:03:00 | Pass | CONTROLLER - RELAY - BAD CONTACT CORRECTED
MSA-DTWD | WA3432903 | E block, Ground level, External west side of E block- Multiple graffiti to be removed | Joondalup Kendrew Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-07 10:30:00 | Pass | REMOVAL OF GRAFFITI FROM E BLOCK GROUND LEVEL WEST SIDE E BLOCK
MSA-DTWD | WA3432938 | G block, G level, left Male toilet - Male toilet on left not flushing properly | Fremantle Campus (formerly WA Maritime) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-07 11:30:00 | Pass | Adjusted water level in cistern.
MSA-DTWD | WA3433003 | Centre block, LIFTS 5,6 & 7 - Lifts not operating following power shutdown | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-06 16:00:00 | Pass | On arrival Lift 5 in fire service, lift 6 normal operation without AUX COP functional, lift 7 out of group. Reset all lifts &tested. All COP’s functional & all lifts back in group. As per previous callback, group requires UPS. Lifts in service.
MSA-DTWD | WA3433088 | D110 & D111 Jewellery Workshops - Blown fluoro's | Perth Campus B4 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 13:30:00 | Pass | Job complete
MSA-DTWD | WA3433097 | Level 1, A107 & A114 - Blown fluoro's | Perth Campus B5 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 16:30:00 | Pass | Job complete
MSA-DTWD | WA3433117 | F Block, FT03- Damaged AC Filters | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-07 13:30:00 | Pass | Job completeAwaiting return of signature slip via email due to covid 19
MSA-DTWD | WA3433154 | L3 fashion department Blown fluoros | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-13 10:30:00 | Pass | Replaced faulty lights in B6 Level 3
MSA-DTWD | WA3433157 | L1 Replace damaged lighting diffuser & blown tubes | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 12:00:00 | Pass | Replaced faulty lights b6 L1
MSA-DTWD | WA3433236 | L1 B block B103 & B11 lights blown | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 16:00:00 | Pass | Job complete
MSA-DTWD | WA3433255 | B block L1 B111 repair flexible welding extraction arms | East Perth Campus | GMP-BR | Equipment | Handtools (EQ) | Ronley Holdings Pty Ltd | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-08-20 12:30:00 | Fail | 07/07/20 Attended site to inspect flexible welding extractions arms. 20/08/20 Attended site to dismantle, clean and repair fractured welds on 7 x flexible welding extractions arms.
MSA-DTWD | WA3433264 | B and D block L1 & 3 B104..B107.3. D309 D307 ceiling damage | East Perth Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-08 15:30:00 | Pass | Attend site and inspectLeave site to collect material Return to site and replace affected ceiling tiles
MSA-DTWD | WA3433291 | L1 laneway Replace missing rain water downpipe | Perth Campus B6 | GMP-BR | Building | Steel Work (BU) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-13 11:45:00 | Pass | Inspected missing downpipe and sourced replacement off site. returned and installed
MSA-DTWD | WA3433307 | D block D009 faulty push button lock | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 06 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-07 12:45:00 | Pass | Removed broken disc from a lockwood digital lock on door D009 to allow it t o work again using existing code
MSA-DTWD | WA3433353 | Block 6, Painting & Decorating- Heater banks 7 & 8 is not working | Thornlie Campus | GMP-BR | Equipment | Electrical Equipment (EQ) | AWB Co. | 3 | CLOSE | 06 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-07 12:30:00 | Pass | Replaced faulty contactor to heaters in painting and decorating. Job complete.
MSA-MRWA | WA3432572 | lift No1 non operational | Don Aitken Centre MRWA Head Office | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 06 Jul 2020 | 2020-07-06 12:07:54 | 2020-07-06 10:49:00 | Pass | Work order to be closed out at $0
MSA-DCA | WA3433894 | number of LED fluro's flashing | Subiaco Arts Centre-Main Building-Level 1-Bar Area | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-21 09:00:00 | Fail | Arrived at site at 7 to repair two LED panel lights in second level foyer. Could not find register but signed in on paper. Fill in SWMS. Locate lights and removed old ones. Found new models are the wrong size fittings, due to defuser being to big and fitting being to thick. Also lights are on a hold down dimmer switch so when lights are dimmed down low then new LED slightly flash and are double the brightness of the old units. But when at 100% they look the same colour. Informed Tony of issues and done paperwork.
MSA-DCS | WA3433552 | D13 cell hatch wont lock shut flap open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 07 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 10:15:00 | Pass | Replace lock and adjust strike
MSA-DCS | WA3433563 | Unit 1 - A5 cell door viewing hatch broken , & cell window broken | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 07 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-10 14:00:00 | Fail | CELL WINDOW & VIEWING HATCH REPLACED
MSA-DCS | WA3433591 | Main building, Main kitchen, Commerical steamer/oven combo | Nyandi Training Academy | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 09:00:00 | Pass | Replaced oven interior lamp and socket, fitted and tested ok.
MSA-DCS | WA3433611 | Damaged head board to Unit 5 Cell D7-see notes | Casuarina Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-16 11:15:00 | Fail | head board removed for matv point install & re installed
MSA-DCS | WA3433637 | Vaulted ceiling area Uplights flickering/not working | Boronia Pre-release-AK19 - Library, Education Personal Development-Ground Floor | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-16 10:00:00 | Fail | Investigate library lightsSource partsRepair lights in library area
MSA-DCS | WA3433641 | Cafeteria area Lights flickering/not working (x 4)-see notes | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-16 08:30:00 | Fail | Investigate cafeteria lightsSource partsRepair lights in cafeteria area
MSA-DCS | WA3433664 | PA system is not working | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-17 08:45:00 | Fail | PA Mic had been damaged, replaced and tested with redback 3pin desk mic.Tested PA, unable to hear im dinning room, checked speakers and found one speaker disconnected. Reconected and tested. Loud and clear
MSA-DCS | WA3433673 | Unit 2, D Wing- Shower furthest from door will not turn off, hot water tap is broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 11:00:00 | Pass | Replaced broken spindle.
MSA-DCS | WA3433701 | Cool Room is not cooling | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 07 Jul 2020 | 2020-07-08 09:39:59 | 2020-08-05 10:30:00 | Fail | essential ref. attended , found coolroom coil iced up. due to door being left open .De-ice coil and clear drain , monitor system and returned the next day ,found system to be operational.
MSA-DCS | WA3433787 | A-wing -Training Security system - Computer for PDA training in A-wing cell is not working properly. | Nyandi Training Academy | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-07 16:00:00 | Pass | Sourced new PSU and fans.Installed and tested workstation.Workstation starts up correctly and fans running at full capacity with little noise
MSA-DCS | WA3433812 | reception outside lights on the timer need to be reset | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-07 12:00:00 | Pass | Reprogrammed and tested light
MSA-DCS | WA3433824 | Upstairs main office light is flickering on and off | Midland (North East Metro) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-13 09:30:00 | Fail | Replaced lamps and starters as required.
MSA-DCS | WA3433839 | unit 1 A25 and A28 doors are rotten and may need replacing | Bandyup Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 07 Jul 2020 | 2020-07-08 11:10:05 | 2020-07-07 13:30:00 | Pass | Attended site and carried out inspection of damaged doors.
MSA-DCS | WA3433842 | Unit 4 J, K and L block HW to kitchen and not hot to showers | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-14 14:00:00 | Fail | COMPLETED
MSA-DCS | WA3433857 | Paint shop - 2x high bay lights faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-21 13:30:00 | Fail | Replaced faulty hi bay lights in paint shop Required scissor lift booked in 21.7.20
MSA-DCS | WA3433907 | Unit 2, A & B wing - unable to lock cell door | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 07 Jul 2020 | 2020-07-07 16:00:19 | 2020-07-07 14:30:00 | Pass | Job completed - service main lock
MSA-DCS | WA3433925 | Reset Entry security systems- attendance for 08.07.2020 at 8.30am | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Jul 2020 | 2020-07-08 12:14:57 | 2020-09-16 11:56:00 | Fail | Repaired multiple system faults after power outage caused by RCD testing. Restored all systems, replaced faulty PSU and tested OK.Job CompleteParts:12V 8Amp Powerbox PSU - PFM Hakea Stores StockConsumables - SEME Stock
MSA-DCS | WA3433994 | Unit 3, B & D- Grill buttons not functioning correctly | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-07 15:30:00 | Pass | Attended unit 3, found only B Wing grill giving problem. Pressing “Stop” Button would cause Grill to close when until operated a second time. Checked the programming and found one logic Block latched on an “unknown” state. Reset the logic block and tested operation of the grill. Unable to reproduce Fault.
MSA-DCS | WA3434003 | Unit 13, Cell B13- Shower screen is leaking water onto mattress | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-22 14:45:00 | Fail | REMOVE OLD SEALER AND RESEAL WITH NEW SILICONE
MSA-DCS | WA3434008 | Recovery west office - Lock is faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Jul 2020 | 2020-07-08 12:56:36 | 2020-07-07 15:30:00 | Pass | Rectified issue with lock as required.
MSA-DCS | WA3434009 | Cleaning workshop Lock between cleaning and cabinet shop faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Jul 2020 | 2020-07-08 12:56:53 | 2020-07-07 16:30:00 | Pass | Serviced lock as required.
MSA-DCS | WA3434021 | Kitchen- Meat slicer jammed & not working | Banksia Hill Detention Centre | WSM-BR-SITE | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-08-03 15:00:00 | Fail | Kitchen meat slicer jammed & not working. Check slicer, remove for repair. Dismantle, replace rubber feet & buffer, new power lead. Repair seized carriage, clean off cooking oil, sharpen blade.
MSA-DCS | WA3434029 | Medical centre, consult room 3 - replace/repair faucet in sink | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-29 11:35:00 | Fail | Replace basin set in medical centre consult room 3.
MSA-DCS | WA3434034 | WWTP - faulty clarifier sprinklers | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-28 13:00:00 | Fail | Repair pipe work at waste water treatment plant..
MSA-DCS | WA3434082 | CCTV system - not showing on screen in reception and level 2 | East Perth | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Jul 2020 | 2020-07-07 18:02:37 | 2020-07-07 14:30:00 | Pass | Phone supported sue to bring cameras up on second screen
MSA-DCS | WA3434094 | Unit 5, Cell C5 - water leak from shower though wall, tiles need regrouting | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-09-11 14:30:00 | Fail | SHOWER RECESS RE GROUTED & RE SEALED
MSA-DCS | WA3434109 | Unit 5, Cell C2 - water leak from wall outside shower | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-08 11:17:00 | Pass | Re-silicon shower screen
MSA-DCS | WA3434127 | Education 1, lower female toilet (new office space) - lock is still stiff and very hard to operate | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 11:00:00 | Pass | Gained entry and replaced faulty lock.
MSA-DCS | WA3434149 | laundry main dryer - fixed dyer as not working | Bandyup Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-10 09:10:00 | Pass | No display on machine. Traced to overload tripped. Reset and test motor OK. Tested Contactors OK. Test with load OK
MSA-DCS | WA3434150 | Unit 1, cell A17 - hot water not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-14 13:00:00 | Fail | COMPLETED
MSA-DCS | WA3434154 | Laundry- Red tap to rheem urn is broken | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-17 14:40:00 | Fail | Drained unit and replaced RHEEM tap and tested
MSA-DCS | WA3434245 | Power outage, electrician to check if network or internal fault | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 07 Jul 2020 | 2020-07-08 01:13:35 | 2020-07-08 00:30:00 | Pass | Waited on site for western power, reset and tested power
MSA-DFES | WA3433707 | Payroll - Light above Valerie Wong's work station has gone out | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-10 14:45:00 | Pass | Located faulty light above Valeries Desk. Repaired with new globe and tested for function.
MSA-DFES | WA3433746 | level 2, recovery team - Possible electrical fault, check and test power point at desk work station | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-10 15:15:00 | Pass | Located reported faulty powerpoints. Client reported the powerpoints because they had 2 laptops that broke. I tested for funtion, polarity and the voltage. Powerpoints are in perfect working order. Notified staff of works.
MSA-DFES | WA3433955 | Outside front applicance bay - flood light not working | CFRS Wangara | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-28 13:45:00 | Fail | Investigated fault with light. Led flood light has blown and will need to seek approval for replacement.12ft ladder required CompleteCollected gear and attended site, replaced faulty flood light and tested all in working order
MSA-DFES | WA3434142 | rear engine room roller door - sticking approximately half way when the door is opening | CFRS Osborne Park | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 14:00:00 | Pass | Adjusted RHS bottom wheel and track Minor impact damageonly adjust required to repair
MSA-DFES | WA3434163 | Retrospective work order - SINGLE ZONE 22 R/S BAY 1 REAR DOOR | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 07 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 12:05:00 | Pass | EXTERNAL PATROL ONLY STAFF ONSITE TRUCK OUT ON A JOB NO SIGNS OF DAMAGE OR FORCED ENTRY
MSA-DTAG | WA3433762 | Pacom PC, Registry- PACOM PC not allowing any credentials to sign in | Perth Children's Court | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-07 11:15:00 | Pass | Pacom Server unable to login to any accounts. Operator.cfg is corrupt so copied new file and obtained reset password. Logged in and adjusted all user accounts.
MSA-DTAG | WA3433900 | Level 4, Panel missing from wall where old phone connection used to be | Central Law Courts | GMP-BR-HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 15:00:00 | Pass | PANEL REPAIRED & RE INSTALLED
MSA-DTAG | WA3434162 | CCTV secured waiting room- light not working | Rockingham Justice Complex | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-15 08:15:00 | Fail | Inspected lighting and replaced faulty light fitting
MSA-DTWD | WA3433622 | L1 A113 Wood Workshop Failed exit light | Perth Campus B5 | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-13 11:00:00 | Pass | Replaced blown faulty Fluor.
MSA-DTWD | WA3433681 | B block ground floor Lights require repair in this room some not operating | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 15:45:00 | Pass | Attended site and signed in. Located room with facilities. B29. Advised to replace and relamp the whole room. Site supplied tubes and starters. Replaced 18 tubes and starters. Replaced 1 x 36w ballast. Tested all okay. Job complete
MSA-DTWD | WA3433689 | level 6, room W606 - Re-attatch electrical skirting | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 10:30:00 | Pass | Attended site. Located w606. Found skirting duct off the wall. Remounted and made safe.
MSA-DTWD | WA3433786 | A block, toilets - 10 Cistern outlets found faulty A Block requiring repairs | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-09 13:45:00 | Pass | COMPLETED
MSA-DTWD | WA3433851 | E Block - 2x Alarm panels not working | Bentley Campus | GMP-BR | Security | Monitoring (SE) | CONNECT SECURITY SYSTEMS | 1 | CLOSE | 07 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 13:15:00 | Pass | Found Circuit Breaker Red 7 Tripped in Pines Cafe Bar Area Switchboard. Reset breaker and replaced dead backup battery. Keypads operating as expected when departing
MSA-DTWD | WA3433881 | U015 glazing workshop - faulty fluro lights | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-09 15:00:00 | Pass | Replaced faulty lamps to lights u015. Job complete.
MSA-DTWD | WA3434133 | B Block, level 2, B208 - Ladies toilet B208 faulty light | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 16:30:00 | Pass | Job complete
MSA-MRWA | WA3433399 | Don Aitken Centre - Basement Server Room - AC 2 Fault | Don Aitken Centre MRWA Head Office-Main Building-Basement-IT Server Room | GMP-BR | Electrical | General Electrical (EL) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 07 Jul 2020 | 2020-07-07 08:43:23 | 2020-07-07 08:00:00 | Pass | Attended site 7-7-20 0500 for an after hours call out. CRAC server room systems in fault. Applied tests and checks to find system to have faulted on a communication error. Checked incoming power and control voltage (ok). Carried out reset procedure to system and monitored operation. System reset and operating correctly maintaining conditions. Left site 0800.
MSA-MRWA | WA3433579 | ground/warehouse male toilet blocked | Neerabup Depot | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-07 15:49:00 | Pass | Clear blockage to pan line
MSA-MRWA | WA3433625 | ground floor kitchen Hot Water Flick tap, in the main Kitchen -see notes | Jandakot Depot | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 09:42:00 | Pass | Refrigeration u/sRecommend new unitA40149088M Zip Hydrotap 2014 - compressor over-run diagnosed quoted to replace unit
MSA-MRWA | WA3433659 | court yard emergency and external light repair-AWB on site | Materials Engineering Branch | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 1 | CLOSE | 07 Jul 2020 | 2020-07-08 17:00:00 | 2020-07-07 10:30:00 | Pass | Replaced faulty exit light and night light. All now working.
MSA-MRWA | WA3433927 | Level 1, Office Bitumen and paint lab - Inner door leading from office to lab will not open. | Materials Engineering Branch | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 07 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-08 13:30:00 | Pass | Repair lock and install mew spring and clip
MSA-DCA | WA3434887 | freezer keeps tripping and requires resetting re occures every 6 to 7 days | Perth Concert Hall-Main Building-Basement-Storage Area | GMP-BR | Refrigeration | Freezers (RE) | Precise Air Group | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-16 13:52:00 | Fail | Inspected freezer room and found compressor shortcycling.Carried out tests and found the lp switch appears to befailing and cutting out causing the compressor to shortcycle.Sent through braf for approval.Once approved picked up parts.Isolated power to freezer and replaced the dual pressurecontroller.Replaced the contactor and overload for the compressor asthis was likely damaged from the short cycling.Also replaced the fan speed controller as there was noadjustment in speed when the adjustment dial was turned.Replaced parts and turned on.Set new pressure switch and fan speed controller.Monitored and found operating ok
MSA-DCS | WA3434315 | control room cardex system on hold and some doors cannot be operated | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 07:14:02 | 2020-07-08 21:19:00 | Pass | Attended site, all controllers showing offline on system.Controllers have power and communication.Checked Gallagher services and restarted.Controllers back online. Re-synced all controller databases and tested gate inputs and outputs.Canteen alarm zone now arming.
MSA-DCS | WA3434323 | MPU (8) - M10 Electrics keeps tripping in cell | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-09 10:30:00 | Pass | Repaired damaged cell gpos in mpu m10.Waited access for cell
MSA-DCS | WA3434324 | Unit 5 - A9 Toilet is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-13 15:00:00 | Pass | Installed new outlet rubber in cistern.
MSA-DCS | WA3434325 | Unit 4 - A12 Toilet not flushing properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 17:00:00 | Pass | Plunged toilet to clear blockage.
MSA-DCS | WA3434331 | Unit 2 Cell D10 check electrical outlets and lighting after cell fire | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 07:34:13 | 2020-07-08 16:00:00 | Pass | Unit 2 D10 Cell fire damage , Replaced all burnt GPO's and lights switches
MSA-DCS | WA3434340 | Unit 2 Cell D10 check fire detection system after cell fire | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 07:44:36 | 2020-07-08 15:22:00 | Pass | Attended site due to fire on unit 2 cell 10. Found sample point melted. Staff mentioned no fire alarm activation during event.Replaced D10 sample point.Upon investigation found sample tube above D10 and other cells snapped off inside roof space. Also found D6 sample point melted and replaced whilst on site.Replaced 8x broken sample tubes in D wing.Tested fire alarm with smoke pen, activated accordingly.
MSA-DCS | WA3434352 | Unit 1 - C6 Toilet in C6 is blocked and wont flush properly. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 08 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-10 09:00:00 | Pass | Removed rubbish from blocked toilet. Plunged to clear blockage.
MSA-DCS | WA3434357 | security office ISU camera's off line-SEME on site | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 08 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-08 15:00:00 | Pass | Checked security workstation, unable to connect to Geutebrück cctv server.Checked network setting, traced network and powercycled 4 port switch.Server connections re-established. Checked cameras and confirmed all cameras are viewable and recording
MSA-DCS | WA3434409 | Unit 10, Front door, entrance to unit - lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 08:44:10 | 2020-07-08 15:00:00 | Pass | Lock issue caused by hinges. Adjusted/repaired as necessary
MSA-DCS | WA3434416 | Unit 9, Control Room Lock to enter C/D Dayroom - Key Barrel Loose | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-08 14:00:00 | Pass | replaced faulty cylinder
MSA-DCS | WA3434425 | Unit 9, D wing - Glass Window and Frame pulled out at end of Wing. Needs refitting | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 08:53:38 | 2020-07-09 11:15:00 | Fail | WINDOW REMOVED /REPAIRED & RE FITTED
MSA-DCS | WA3434436 | Unit 7, Control room - Urn leaking water | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 09:00:44 | 2020-07-08 13:45:00 | Pass | Unable to access urn as shelf across topSite advised they will get a carpenter in to remove the shelf and rework area so that the Rheem can be worked on - they asked us to close out work order for now which we have done. The unit requires main PCB, Solenoid and Level sensors.
MSA-DCS | WA3434479 | Check fire pumps and top up diesel after fire in Unit 2 Cell D10 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 09:15:22 | 2020-07-09 09:00:00 | Pass | nil
MSA-DCS | WA3434505 | Unit 6, plant room - cupboard above control room light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-08 15:00:00 | Pass | Repaired multiple faulty lights in unit 6 plant room
MSA-DCS | WA3434584 | SITE COST Kitchen- Extraction fans not working | Wooroloo Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 0 | CLOSE | 08 Jul 2020 | 2020-07-08 14:24:09 | 2020-07-08 15:00:00 | Fail | Kitchen Exhaust fans Hoods faulty. Check fan & controls. Open switch covers, locate contactors. Both tripped, reset. Run fans, test switch. All working correctly.
MSA-DCS | WA3434596 | Unit 6, A wing - landing light faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-10 22:00:00 | Pass | Repaired faulty lights in unit 6
MSA-DCS | WA3434622 | Unit 2, A13 - Window function is broken, window keeps dropping down | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 08:45:00 | Pass | REPAIR CELL WINDOW
MSA-DCS | WA3434687 | various levels faults with lights see notes-Refer work order WA3400496 | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-08-27 10:00:00 | Fail | Replaced broken light switches
MSA-DCS | WA3434694 | Unit 14, B13 - main light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 08:30:00 | Pass | Repaired faulty lights in unit 14 b13
MSA-DCS | WA3434702 | Unit 14, A & C - Toaster requires new lead , Needs lead approximately 1.5 meters long. | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 11:30:00 | Pass | Replaced damaged commercial toaster lead in unit 14
MSA-DCS | WA3434820 | Garments, Skylight is cracked leaking onto mezzaine & office | Casuarina Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-15 10:15:00 | Fail | CLEANED SKYLIGHT - SKYLIGHT HAS BEEN QUOTED TO REPLACE - TEMP REPAIRS MADE
MSA-DCS | WA3434916 | Rear of House 6 Shade house - Termite activity | Boronia Pre-release-External Area-Ground Floor-Shade House | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 14:00:00 | Pass | Treatment for active termite area at the rear of house shade 6
MSA-DCS | WA3434922 | Unit 2, Cell C10 - No water to cell, only slight trickle | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 14:33:58 | 2020-07-09 09:05:00 | Pass | Water supply was blocked replaced inlet valve outlet washer new Flexi and union and new pillar tap
MSA-DCS | WA3434983 | Visit Reset Centre, visitors toilets - Toilet Blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 15:23:07 | 2020-07-09 07:45:00 | Pass | unblocked toilet
MSA-DCS | WA3434988 | Unit 10, C16 - Bed light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 12:00:00 | Pass | Repaired light
MSA-DCS | WA3434991 | Reception, Kitchenette - Exhaust Fan broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 13:30:00 | Pass | Repaired light
MSA-DCS | WA3435030 | Unit 2, no hot water | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 15:58:34 | 2020-07-09 12:15:00 | Pass | Job to be completed on different work order.
MSA-DFES | WA3434412 | kitchen zip boiler has sprung a leak | CFRS Canning Vale | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 11:44:00 | Pass | Unit full of water dried, pressure tested ok Replaced safety solenoid - leaks not coming from Zip reported plumbers required as pipework to actual sink leaking
MSA-DFES | WA3434723 | Under the sink - sink drain pipe is leaking. unable to use sink due to leak | CFRS Canning Vale | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 15:00:00 | Pass | Replaired two leaks, one with plug and waste the other with mini stop.
MSA-DTAG | WA3434529 | Level 5, family Voilence - White board coming off wall | Central Law Courts | WSM-BR-SITE | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-09 15:00:00 | Pass | WHITE BOARD RE SECURED
MSA-DTAG | WA3434579 | Level 5, outside court 52 - loose chairs | Central Law Courts | GMP-BR-HO | Furniture | Indoor Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 12:00:00 | Pass | LOOSE CHAIRS REPAIRED
MSA-DTAG | WA3434821 | L10 lift 3 is stuck on level 10 and doors keep opening and closing | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 17:00:00 | Pass | Lift stuck lvl2A, err207 xx05. Investigated & found lvl2A RH landing door rollers worn out causing door to stick at points whileopen/closing. Replaced rollers. Adjusted landing door pick up rollers. Tested. Operating correctly. Lift in service.
MSA-DTAG | WA3435043 | Hot water system in the custody control areas has ceased working correctly | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-10 15:00:00 | Pass | COMPLETED
MSA-DTWD | WA3434444 | Level 5, plantroom - AHU1N not re-starting following power shutdown | Perth Campus B1 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-08 16:30:00 | Pass | COMPLETED
MSA-DTWD | WA3434445 | Lvl 3, Female Toilet- Flushing system faulty | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-09 09:34:00 | Pass | Fix toilet
MSA-DTWD | WA3434477 | E block E622 DB2 Light side of the distribution board is hot requires a thermagraphic survey | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 08 Jul 2020 | 2020-07-08 13:11:21 | 2020-07-21 12:00:00 | Fail | Attended site and signed. Rechecked DB. Found the temperature has improved but still slightly high. Found R2 drawing 17.5A on a 16A RCD and W6 drawing 15A on 16A RCD. No other faults were found. Attended site and signed in. Located switchboard. Found light chassis warm. Inspected and tested all connections and loads. AJ to write report and has images taken of switchboard. Submit BRAF
MSA-DTWD | WA3434496 | TA12 - faulty lock | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 15:05:00 | Pass | Service lock to TA12
MSA-DTWD | WA3434550 | Building 7, ground level, student common room - water leak near TV | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-09 16:00:00 | Pass | Works completed - sealed leaks with roof and gutter sealer - site confirmed leak has been resolved
MSA-DTWD | WA3434558 | Building 12, Ground level, 12G1 - Water leak in center of room | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-09 15:00:00 | Pass | As per Dom Gileno - Have closed off job and charged costs to date
MSA-DTWD | WA3434586 | building 7, Ground level, Kitchen - Ceiling light not working in second chiller room. | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-20 09:00:00 | Fail | Attended site and signed in. Located second coolroom and faulty light. Isolated coolroom and disconnected and removed light. Replaced with new weatherproof batten. Tested all okay. Job complete
MSA-DTWD | WA3434647 | A Block, Level 1, Room A138 - barrel in door lock broken | Leederville Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-09 11:20:00 | Pass | replace cylinder components to room A138
MSA-DTWD | WA3434679 | F Block, F14- Roller door is not functioning | Bentley Campus | GMP-BR | Building | Automatic Doors (BU) | UNIVERSAL DOORS | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-08 13:30:00 | Pass | ADJUSTED SPRING TENSION, SECURED SHAFT BUSHES, CHECKED OPERATION, ALL OK.
MSA-DTWD | WA3434682 | B Block, B2423- faulty 3 gang light switch | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-13 13:15:00 | Pass | Replaced 3x faulty switch mechs in B2423
MSA-DTWD | WA3434685 | E Block, Bentley pines restaurant - roof leak | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-23 15:45:00 | Fail | Lift roof sheets and flashing on roof at leak locations - cleanout and reseal with silicone. Leak resolved. Patch holes in bulkhead, seal stains on ceiling with stain block, patch & paint ceiling. Job complete.
MSA-DTWD | WA3434756 | Building 8, ground level, KOORAMAR aboriginal Services entrance - door lock falling apart | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-09 12:00:00 | Pass | Building 8 - KOORAMAR - Entry door locks faulty.Locks repaired.
MSA-DTWD | WA3434767 | North Block, Level 2, N222 - Door lock faulty | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-08 16:05:00 | Pass | repair to lock and replace cylinder components to door N222
MSA-DTWD | WA3434772 | Block 3, Ground level, male toilets - Door lock wont unlock from inside. | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-09 12:00:00 | Pass | Block 3 - Male toilets locks faulty.Locks repaired.
MSA-DTWD | WA3434778 | D block - Underground gate valve leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-13 16:12:00 | Pass | Replace water valve once able to turn water supply off
MSA-DTWD | WA3434782 | E block, E75 kitchen - 2x damaged mini stop taps | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-13 16:13:00 | Pass | Replaced to ware in kitchens that was leaking and not working properly
MSA-DTWD | WA3434794 | F Block, FG35- 2x LED panel Lights not working in customer service back office | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 14:15:00 | Pass | Attended site and signed in. Located 2x lights not working. Located a second switch that controls the lights. Showed staff. All now working
MSA-DTWD | WA3434863 | Landscaping outdoor area, all lights need to be checked for faults | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 08 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-20 12:15:00 | Fail | Attended site and signed in. Accessed faulty light in undercover area. Disconnected and removed from roof. Installed new weatherproof LED fitting. Sealed from water ingress. Tested all okay. Clean and tidy site. Job complete
MSA-DTWD | WA3435054 | North Block, N226 - Door locks faulty | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 08 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-08 16:58:00 | Pass | N226 - repairs to locks and replace 4x cylinder components
MSA-MRWA | WA3434494 | Level 8, Zip hot water unit not working | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 08 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 14:15:00 | Pass | Replaced A402020287 - Zip Hydrotap parts:-Hot external Level sensor kitplv kit and LCD Assy Kit
MSA-DCA | WA3435483 | Damage to front wire fence. Please repair and make secure. Security risk. | State Archives Repository Dianella-Main Building-External Area | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-10 09:00:00 | Pass | Repair damaged section of the fence
MSA-DCS | WA3435143 | L2 Cold tap leaking in ladies toilet (right hand sink) | East Perth | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-10 12:50:00 | Pass | COMPLETED
MSA-DCS | WA3435164 | Gascoyne kitchen hot water tap leaking and pvc pipe under sink | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 09 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-14 12:46:00 | Pass | Renew spindles to kitchen sink Repair waste pipe
MSA-DCS | WA3435170 | control camera 115 not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 07:20:05 | 2020-07-09 12:00:00 | Pass | Job complete
MSA-DCS | WA3435209 | control cardex system cannot open doors | Karnet Prison Farm | SPA-BR | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 07:44:17 | 2020-07-09 16:40:00 | Pass | Job recalled, controller #2 went offline at 4am, 4:45am controller #3 offline and 5:40am controller #1 offline, control still able to control doors that use a macro.checked network switch, no faults. CCTV system and security system share network switch, checked cameras for any faults around the same time the controllers started to fail.no faults on the CCTV system.ran report and found #2 has been dropping offline daily and #3 every few days. checked controllers setting and software versions. replaced #2 controller (3000 model) with new Gallagher 6000 and 8R module, monitored while onsite, controller has been stable with no comms loss on any controller.
MSA-DCS | WA3435217 | control room camera 22 PTZ no control | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 07:48:14 | 2020-12-11 08:00:00 | Fail | Tested camera, all ok, check settings and connection, test at gate house, client can control fully, all ok
MSA-DCS | WA3435223 | Unit 1 out side cell 20 & 21 water cooler keeps short circuting | Karnet Prison Farm | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-23 15:00:00 | Fail | Investigate unit 1 tripping circuit. Found fault on compressor of water cooler
MSA-DCS | WA3435226 | Unit 14 - B12 Cell B 13 cell light has blown. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 09 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 10:00:00 | Pass | Repaired faulty lights in unit 14 b12
MSA-DCS | WA3435232 | Gate House - Front Entrance walkthrough metal detector not working-see notes | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-09 10:00:00 | Pass | Mr Booth (Asst Supt Security) advised Randomised counter mounted on this device did not appear to be working. Found metal cover plate had lost one retaining screw and fallen over PE beam causing it not to work. Located and installed replacem3nt screw, confirmed operation of randomised counter. Advised Security Manager.
MSA-DCS | WA3435249 | Vegetable preparation -check circuit breaker point as damaged by external stores this morning | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-15 10:30:00 | Fail | Isolated damaged 3 phase gpo in veggie prep. Picked up replacement rcd combo and installed
MSA-DCS | WA3435269 | Unit 14, B & D store room - tap broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 16:00:00 | Pass | Located tap and reinstalled missing the tap handle.
MSA-DCS | WA3435310 | Unit 1, B wing - door to wing shower is jammed and not opening | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 08:54:00 | 2020-07-23 13:30:00 | Fail | Open jammed lock and temp. repair.replace face plate and hinges.
MSA-DCS | WA3435316 | SHU visits - camera no singal | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-10-27 16:30:00 | Fail | Suspect camera damaged by water ingress in ceiling area above camera. Camera not operating on assessment. Installed new cable and replaced faulty camera with Digital camera. See log for details.
MSA-DCS | WA3435327 | Unit 1, A9 - cell window has been shattered and | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 13:00:00 | Pass | ALL BROKEN WINDOWS REPLACED
MSA-DCS | WA3435332 | Unit 1, D9 - window frame broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-20 11:00:00 | Fail | REPAIR AND REPLACE WINDOW FRAME
MSA-DCS | WA3435338 | Unit 1, A4 - toilet wont stop flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 10:00:00 | Pass | Replaced leaking outlet rubber on cistern.
MSA-DCS | WA3435342 | SOP, Cell 10 - toilet flusher button not depressing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 11:00:00 | Pass | Installed new isolation valve. Installed new inlet valve and spring in cistern button.
MSA-DCS | WA3435346 | gate house cashier door lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 09:23:54 | 2020-07-09 16:10:00 | Pass | Repaired door seal and lock as required.
MSA-DCS | WA3435347 | External stores - vinyl lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-24 18:00:00 | Fail | VINYL FLOORS REPAIRED
MSA-DCS | WA3435351 | Unit 1, A wing - showers broken taps, not turning off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 12:00:00 | Pass | Replaced 2 x new spindles in shower taps.
MSA-DCS | WA3435369 | Unit 1, C wing - showers window metal exposed, broken stays. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 09:30:00 | Pass | SPIRAL BALANCES RENEWED
MSA-DCS | WA3435390 | Unit 6, Cell B10 - OBS lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 08:30:00 | Pass | Repaired faulty lights in unit 6 b10
MSA-DCS | WA3435434 | SITE COSTED Visits - CCTV Cameras are down | Bandyup Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Jul 2020 | 2020-07-09 14:10:22 | 2020-07-09 16:26:00 | Fail | Attended site, repaired multiple CCTV faults in visits and security, repaired faults with CCTV storage NVRs.Tested OKJob Complete
MSA-DCS | WA3435495 | Grounds maintenance cold water fountain not working | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 10:55:00 | Pass | attended checked unit blocked required new filter change flushed tested checked fountain all ok A40191325E
MSA-DCS | WA3435515 | Welding shed, power board faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 14:30:00 | Pass | Relocated power supply
MSA-DCS | WA3435516 | Section 95 shed- 3x fluro lights are faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-13 10:30:00 | Pass | Replaced 3x batten lights with LEDs
MSA-DCS | WA3435535 | Unit 1, Cell A16 - faulty cord, there is not signal from the ariel cable | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-15 13:30:00 | Fail | Repaired tv outlet
MSA-DCS | WA3435542 | Unit 8, A/B wing, Regi Area - 4 Way GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-09 15:00:00 | Pass | Replaced gpo
MSA-DCS | WA3435549 | 2 x faulty lights 1 out and 1 flickering (see notes for location) | Mandurah | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-15 11:30:00 | Fail | Investigate and repair lights in office areaContacted site - approved to attend 15/07/20
MSA-DCS | WA3435552 | Unit 1, control room - Vesta fire panel not working | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 09 Jul 2020 | 2020-07-09 15:35:06 | 2020-07-09 14:11:00 | Pass | GA BG 9/7/20On arrival found unit 1 vesda with no display. After investigation found no 24v being supplied. PSU mains okay. Disconnected PSU batteries,vesda powered on. Batteries showing 4v, dragging down PSU output. Replaced with new 2x12v 12Ah batteries.Checked all flows whilst on site. All reading okay.System operating as normal at time of departure
MSA-DCS | WA3435586 | Repair 1x small pothole on ring road and 1x depression on bitumen surface in car parking bays | Nyandi Training Academy | GMP-BR- HO | Paving & Roadworks | Paving (PR) | AFD Contracting | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-09-09 12:30:00 | Fail | 14/07/20Cut out small pot hole to find old tree stump. Needs more cutting and excavation, refilling, compacting. Inspection of second depression looks to be the same and needs more dramatic works.09/09/20Excavate out tree stump.Cut road and recompact.Lay new hot mis asphalt.Workshop - Pick up & drop off hired excavator. Pick up asphalt. Load up tools and trailer.
MSA-DCS | WA3435592 | Unit 5, Control- Zip hot water system not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-17 13:45:00 | Fail | Reset thermal overload and tested
MSA-DCS | WA3435596 | Paint Shop - staff toilet not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 13:00:00 | Pass | Adjusted and cleared blockage from flush valve inside cistern.
MSA-DCS | WA3435598 | CCU (11), Cell C3- no hot water in shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 14:00:00 | Pass | Adjusted valves and tested water temp.
MSA-DCS | WA3435600 | Vegetable Prep- cryvac machine not sealing properly ( possible faulty fuse ) | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 15:00:00 | Pass | Vegetable Prep - Cry vac machine faulty. Check machine & controls. Remove bag sealer for repairs. Replace heater cable to bag sealer.
MSA-DCS | WA3435605 | Entry Pod- Fire alarm fault | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 12:29:10 | 2020-07-09 15:30:00 | Pass | System status displaying normal on departure
MSA-DCS | WA3435643 | kitchen brat pan not staying on when lit | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-08-24 18:30:00 | Fail | 15/07/20Attended Bratt Pan - installer of the burners, put a thermostat in, but wasn't sure it was the correct one. Found the ignition probes not in flame and upside down and one screw securing it. Bent probes into flame, that fixed the ignition problem, but recommend replacing probes. Recommend replacing thermostat and overtemp with genuine parts.24/8/20Fitted parts to Bratt Pan Unit is lighting and thermostat is operational.
MSA-DCS | WA3435663 | Blocks 2D & 4B- heating timers not coming on | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 10:30:00 | Pass | Replaced 2x contactors
MSA-DCS | WA3435677 | mitchell house blocked female toilet drains | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 13:18:03 | 2020-07-10 14:30:00 | Fail | Complete
MSA-DCS | WA3435728 | Unit 3, cell 10 - cell call can not be heard in the cell | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 13:52:34 | 2020-07-10 07:55:00 | Pass | Rectified the cell call audio fault, job completed.
MSA-DCS | WA3435730 | Unit 2, Cell 8 - cell call not very loud may have had stuff psuhed into it | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 13:55:36 | 2020-07-09 15:30:00 | Pass | Tested, static sound heard in the background at the control room end. Removed intercom and replaced with a new one. Tested loud and clear in the cell and in U2 control. Parts used:Cell Guard intercom RJ45 wiring adapter Consumables
MSA-DCS | WA3435733 | Perimeter, zone 6, omnitrax in constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 13:56:54 | 2020-07-10 07:56:00 | Pass | Rectified and fixed the constant alarm, walk test from zone 6. System back to normal operation , job completed.
MSA-DCS | WA3435764 | INF (10) OBS cell 2 - the cell call has lots of interference and echos. | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 10:00:00 | Pass | Attended site and investigated the fault.Checked AUSTCO system.Checked wiring (located in roof space of infirmary) and reseted power to unit.Dismantled unit in OBS cell 2 and resecured.Conducted test.Received loud and clear response from control room.
MSA-DCS | WA3435786 | gate house alarm PTZ for PTZ 25 it is not activating or paning when zone is activated | Roebourne Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 14:10:43 | 2020-08-18 17:00:00 | Fail | All PTZ functions ok. Traced fault to lost settings for PTZ 25 which affected alarm presets for zones 15, 16 19, 20 and 22. Reprogrammed settings on Indigo for all mentioned zones. All zones tested ok.
MSA-DCS | WA3435791 | MPU (8) - Desk in cell ripped from wall, Requires removal of remaining support bars. | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-13 13:00:00 | Pass | REMOVE DESK/BRACKETS - FILL/PATCH/REPAIR HOLES
MSA-DCS | WA3435796 | Main kitchen & office - fluro lights not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-10 12:00:00 | Pass | Replaced light fittings in kitchen office
MSA-DCS | WA3435801 | Unit 3, Cell C5 - cell call not working properly, cant hear and makes a buzzing noise | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 14:29:17 | 2020-07-09 17:30:00 | Pass | Attended site and investigated the fault.Checked connections,wiring,input on CI-8A board and found that cell call intercom is faulty.Replaced with new CellGuard CI-CC/270/120 intercom ( critical spare from site).Used sundries.Tested.All ok at departure
MSA-DCS | WA3435814 | Staff & prisoner toilets near Staff kiosk &Laundry/Clothing Store-Toilet exhaust fans noisy,bearing? | Boronia Pre-release-AK19 - Library, Education Personal Development-Ground Floor-Staff Toilet | GMP-BR- HO | Electrical | General Electrical (EL) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-08-06 11:27:00 | Fail | Fixed the rewound motor and replaced step relay.
MSA-DCS | WA3435831 | Lost power to whole building | East Perth | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 09 Jul 2020 | 2020-07-09 19:09:40 | 2020-07-09 18:00:00 | Pass | Traced out building switchboard location and reset “ rising mains” cct breaker . Checked power now available on each floor . Could find no apparent cause for trip . Load on each phase was only 60 amps on a 400 amp cct breaker.
MSA-DFES | WA3435174 | septic pump tank alarm at the front right hand side engine room doors | CFRS Welshpool | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 09 Jul 2020 | 2020-07-09 17:00:00 | 2020-07-09 14:00:00 | Pass | Repair pump pit
MSA-DFES | WA3435267 | radio comms services section door lock hard to open keeps turning | DFES Regional Office - Belmont | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-09 09:20:00 | Pass | Repair to lock on comms room door
MSA-DFES | WA3435429 | Ground level, FF dorm 3 - 350mm LED circular light not working | CFRS Duncraig | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-22 15:00:00 | Fail | Faulty light in Dorm 3 needs replacement. Have ordered new a new LED and will return to complete works Completed
MSA-DFES | WA3435444 | ground level - damaged data terminal and GPO (see notes for location) | CFRS Belmont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 10:45:00 | Pass | Locate faulty data point. But the data mech back into place. Test the data port it passed. Replaced damaged gpo with new.
MSA-DFES | WA3435447 | ground level, FF dorm 1 - Shower head is leaking and also leaking through tap | CFRS Belmont | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 11:45:00 | Pass | Investigate leaking shower and basin located dorm 1Isolate water mains from meter and remove shower iced cartridge and basin mixer,supply and install new shower mixer cartridge and complete new basin mixer Connect fixtures to water and turn on water mains, test operation and check for leaks Pack up and clean up worksite
MSA-DFES | WA3435454 | 26, ground level, female toilets - door handle to bathroom broken | CFRS Daglish | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-13 10:15:00 | Pass | Liam Hanlon (13/07/2020) - Work NoteAttend site Sign in and speak to CO Door handle to toilet/shower missing latch Remove handle Left site to get replacement handle set Return to site Fit new lock set and test working correctly Clean upSign out
MSA-DFES | WA3435460 | Gym - large section of flooring (lino type) at entrance of gym has lifted away | CFRS Wangara | GMP-BR | Flooring | Vinyl (FL) | MALCO FLOORING PTY LTD | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 09:00:00 | Pass | Flooring at entrance of gym has lifted. Removed lifting flooring and installed matting.
MSA-DFES | WA3435590 | Numerous lights not working on the outside of the building perimeter | CFRS Malaga | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-08-14 09:30:00 | Fail | COMPLETED
MSA-DFES | WA3435599 | 8, 11 & Courtyard area - mutiple lights out (see notes) | CFRS Malaga | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-28 15:15:00 | Fail | Complete Attended site and replaced broken lights in both rooms 8 and 11 all in working order
MSA-DFES | WA3435607 | Dorm 9 – Venetian blinds are damaged. Multiple bend fins. | CFRS Malaga | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-08-14 13:35:00 | Fail | Installation completed all work orders & invoice attached
MSA-DFES | WA3435611 | Bathroom 4 – Shower bench detaching from the wall. | CFRS Malaga | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 14:30:00 | Pass | Liam Hanlon (13/07/2020) - Work NoteRemove old fixings Drill out plugs Fit new anchor plugs and re fix brackets to wall Check securely Clean up Notified staff Left danger tag as to be removed by person who ‘tagged it out’ Took photo of sign in book as staff meeting in progress
MSA-DFES | WA3435619 | Kitchen 3 – Draw set left of the oven in broken and not opening correctly. Requires repair | CFRS Malaga | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 13:45:00 | Pass | Liam Hanlon (13/07/2020) - Work NoteAttend site Station unattended Returned in afternoon Removed kitchen drawer Need new runners Will return with new runners Notified staff *took photo of sign in book for times etcLiam Hanlon (15/07/2020) - Work NoteGet materials from Bunnings Attend site Remove runners Mark and work out locations for new runner Pre drill and fix to cupboard and drawer Fit drawer and test working correctly Clean up Sign out
MSA-DFES | WA3435639 | ground safety shower 4 Only minimal water comes out, potential blocked pipe leading to unit | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-10 12:37:00 | Pass | Eye wash tap repair
MSA-DFES | WA3435687 | rear of yard - Fence behind clothes line and up to 1st tree is broken at the base | CFRS Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-30 15:00:00 | Fail | Replaced fence posts and patched brick wall.
MSA-DFES | WA3435707 | engine room - 6 lights require repairs/replacing and Middle row of lights which are the night lights | CFRS Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 13:30:00 | Pass | Locate faulty lights In The engine bay. Replaced faulty tubes and starters with new. The old tubes were 840 the new tubes are now 865 to the light should be better now.
MSA-DFES | WA3435726 | External Area Ground Car Park Gate Eastern Side-timer to gate needs adjusting - see notes | CFRS Fremantle | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 07:10:00 | Pass | Technician attended the site of Fremantle Fire Station to the Carpark Gate No. W21826 on 13/07/2020. Following a full test and inspection of door components found fault to be time clock for gate was out of sync. Technician has previously looked at this time clock during a service and identified it as needed to be replaced, time clock is old and digital screen is damaged, device is slow to react and requires upgrading to stop issues.Technician returned on site on 13/08/2020 and replaced faulty 7 Day timer and set times 7am to 9am and 5pm to 7pm. Test timer and all ok. Full test and inspection of door function completed prior to leaving site.Breakdown of cost: Labour = $715.00Parts = $325.00
MSA-DFES | WA3435743 | engine room, Pump charging cable, 2x faults - Plug missing retaining clamp & Breakaway plug broken | CFRS Belmont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 11:30:00 | Pass | Locate faulty charger cable in the engine room. Checked the cable it is all good. Re connect the chain to the plug base. The ceiling is damaged and will need repair. Advised staff of work completed.
MSA-DFES | WA3435844 | Rear side gate to access bins needs new hinges | CFRS Belmont | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 15:30:00 | Pass | Liam Hanlon (15/07/2020) - Work NoteAttend site Sign in and speak to CO Inspect bin gate Left site and got parts Return to site and drill new fixing into post to brickwork fit hinges in new position mount to postAdjust non active gate and re fit top hinge for margin Check bolt working and closing speed of hinges is adjusted Clean up Sign out
MSA-DFES | WA3436402 | Retrospective work order - APP BAY 1 REAR DOOR AREA 3 | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-09 15:49:00 | Pass | EXTERNAL CHECK CARRIED OUT. ALL APPEARS SECURE. NO OFFENCE DETECTED. STAFF ONSITE
MSA-DTAG | WA3435606 | Special clean for cell 4 - Faeces and urine on the floor | Midland Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | Six Seasons Resources Pty Ltd | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-09 19:30:00 | Pass | P1 Completed
MSA-DTAG | WA3435851 | Room 9.03, Member Elly Marillier’s office- Attach duress alarm to the desk & check | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-08-11 12:00:00 | Fail | Removed input from Unison and programmed back in and tested
MSA-DTWD | WA3435145 | A block L3 male toilet light not working west end | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 09 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-14 15:45:00 | Pass | Job complete
MSA-DTWD | WA3435182 | L1 IT office air con to hot | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 09 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-13 15:00:00 | Pass | COMPLETED
MSA-DTWD | WA3435270 | U015 glazing 6x light globes have blown | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 15:00:00 | Pass | Replaced 2x lamp holder to gig bags and replaced 1 x faulty fluro fitting to u015. Tested job complete.
MSA-DTWD | WA3435305 | LIFT NOT WORKING | Mount Lawley Campus | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 09 Jul 2020 | 2020-07-09 12:55:37 | 2020-07-09 10:46:00 | Pass | Job completed - Lift1 MLT-Hydraulic :lift out of order with doors closed on investigation found main processor locked up with h2 error, stripped during up travel due to disappearance of speed signal. Found oilcold, reset processor and tested operation, lift running at a slower speed. checked relevant circuits all OK, tested operation for 20 minute and lift running normally, suspect oil temperaturecold and not allowing lift to run at normal speed. left in service
MSA-DTWD | WA3435487 | N Wing Passage Level 2 and S110 - Faulty lighting needing replacing/repairs | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 16:30:00 | Pass | Job complete
MSA-DTWD | WA3435501 | A block, A20 - Insufficient airflow through filters | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-09 15:30:00 | Pass | Traveled to supplier to pick up parts. Traveled to site and signed in. Removed old damaged filters and installed new washable filters.
MSA-DTWD | WA3435578 | C block, C50 - We have poor heating in C50 | Midland Campus | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 2 | CLOSE | 09 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-09 16:01:00 | Pass | Attended call, checked boiler & pump in c block found ok.tested ahu in plantroom 5 found heating actuator sticking with corrosion cleared corrosion & tested ok
MSA-DTWD | WA3435738 | L6 ground Bricklaying tool store 6CG25 Ceiling lights fallen and hanging by cable. | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 09 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-16 15:30:00 | Pass | Attended site and signed in. Located tool store, removed old lights, replaced with new led battens. Tested all okay, job complete
MSA-MRWA | WA3435694 | Level 1, west end - Port 155 and 156 non responsive, please investigate/remediate | Don Aitken Centre MRWA Head Office-Main Building-First Floor | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 09 Jul 2020 | 2020-07-10 17:00:00 | 2020-07-09 15:45:00 | Pass | Fault find, repair and test data
MSA-DCS | WA3435964 | Admin staff toilet Lights are damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 15:17:00 | Pass | Replaced faulty light fitting in ladies toilet in admin
MSA-DCS | WA3436066 | kitchen rational oven not working 34-16 (service 17) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 10 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-10 09:15:00 | Pass | Kitchen rational oven not working 34-16 (service 17). Check oven & controls. Repair leaking hand shower. Dry out parts. Replace I/O parts & lower ignition module. Dry lower blower. Assemble all & test.
MSA-DCS | WA3436069 | Unit 13 - A & C Cell lights for A and C wings from 5-8 will not turn on have tripped out. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-10 13:30:00 | Pass | Investigated and repaired faulty lights in unit 14
MSA-DCS | WA3436077 | Unit 14, B/D wing - regi fridge is tripping the RCD | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-14 15:30:00 | Pass | Fridge tripping due to infestation of cockroaches in compressor terminals. Removed what was there and cleaned unit. Fridge is running but pest control required.
MSA-DCS | WA3436081 | control lights on poles 23, 24,25,26 not turning off during the day | Hakea Prison | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 09:00:00 | Pass | Reset transformer and test lights
MSA-DCS | WA3436084 | Unit 4, C13 - cell sink not draining water, sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 08:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3436091 | Control room - 2 camera not working 30 and 155 | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jul 2020 | 2020-07-10 12:16:48 | 2020-07-10 12:45:00 | Fail | Attended site and investigated the faults.Found that there is no power in EC cabinet located on pole of PTZ camera 30 - required attendance by another contractor (electrician) to rectify the problem.Checked cam 155 in SPU cell B8 - fully operational.
MSA-DCS | WA3436135 | Unit 4, PRU - controller 28 offline | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-10 10:30:00 | Pass | Checked status of controller from service terminal and confirmed Controller was able to be pinged (192.168.0.80) from Gatehouse. Reset Controller and monitored operation, controller stayed “On-Line” with no error messages.
MSA-DCS | WA3436139 | Main prison, zone F2 - zone is alarming constatnly (2x inteliflex) | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-10 15:00:00 | Pass | Permanent alarm on Zone F2. Two techs attended zone and calibrated fence controller, tested operation of fence alarm and confirmed alarm activated correctly.
MSA-DCS | WA3436149 | gate house double sliding doors from reception to gate house will not lock | Karnet Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 08:46:04 | 2020-07-10 19:14:00 | Pass | Traced cable from automatic door back to control room, found cable in rack, not connected.Tested cable and reconnected. Programmed relay on Gallagher 6000 system. Tested auto door lock from control, door locked.Tested door open macro. Auto door now working correctly on Gallagher system
MSA-DCS | WA3436265 | Control room - camera PTZ 4 not responding to instructions correctly | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 09:44:06 | 2020-11-02 13:00:00 | Fail | Camera replacement and network issues has been rectified . Test all functions live view, recording and presets all back to normal operations. Job completed.
MSA-DCS | WA3436274 | Unit 6, Cell C9- Top bunk intercom not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 15:30:00 | Pass | Removed SLAVE intercom on the top bunk for testing. Traced fault to corroded CALL 2 terminals on the MASTER intercom. Replaced MASTER unit and ran in a new leg the of cable between the Maste4 and Slave intercoms. Secured and tested. Both intercoms tested ok. Parts used:Cell Guard CI-CC intercom5 metres of Cat 6 cable (site stock)Consumables
MSA-DCS | WA3436275 | MPU (8), M13 - Rear yard door does not secure properly. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 09:51:39 | 2020-07-10 15:00:00 | Pass | Attend site service lock, replace fixings and adjust wall mounted strike
MSA-DCS | WA3436277 | reception Fluorescent light (tube) needs replacing in the shower area in reception. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-13 13:00:00 | Pass | Repaired faulty lights in reception
MSA-DCS | WA3436279 | Unit 5, D Wing upstairs cleaning cupboard tap neck broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-13 17:00:00 | Pass | Reinstalled loose tap outlet in cleaners room.
MSA-DCS | WA3436282 | Facilities Managers Office - Fluorescent light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 09:00:00 | Pass | Replaced damaged light
MSA-DCS | WA3436287 | unit 1 C12 Observation light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 09:58:04 | 2020-07-10 14:30:00 | Pass | Replaced faulty lamp
MSA-DCS | WA3436336 | Unit 8 D9 when back light is turned on and touching tap recieving small spark | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 10:34:37 | 2020-07-10 13:30:00 | Pass | Tested cell due to reported shock
MSA-DCS | WA3436340 | Unit 5, Cell B7 - sink is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-14 12:00:00 | Pass | Changed leaking spindle in shower.
MSA-DCS | WA3436351 | Unit 4, PRU - PRU room CCTV montior not showing feed | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-09-10 11:24:00 | Fail | job completed under WA3592059
MSA-DCS | WA3436356 | Tearoom - Both sink taps leaking and toilet seat damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-14 14:59:00 | Pass | Renew kitchen and basin sets to tea room renew toilet seat
MSA-DCS | WA3436362 | West Admin Lunch Room, Lunch Room - Exposed Electrical Wires | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 10:55:21 | 2020-07-10 15:30:00 | Pass | Repaired damaged lead and tested appliance
MSA-DCS | WA3436369 | West Admin, Mens Urinal - Urinal blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 10:59:57 | 2020-07-10 15:00:00 | Pass | No escort available
MSA-DCS | WA3436375 | CCU, D7 - had blocked sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 09:00:00 | Pass | Plunged basin to clear blockage. Cleaned basin strainers
MSA-DCS | WA3436380 | Unit 4, Cell C9- Sink tap broken leaking from underneath | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 09:00:00 | Pass | Replaced pillar tap
MSA-DCS | WA3436382 | Kitchen - BRAT pan not woking. | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 11:08:23 | 2020-08-05 16:30:00 | Fail | Kitchen Brat Pan faulty. Check pan & controls. Order new temperature sensor ex east. Return, dismantle pan and remove faulty part. Install new sensor. Assemble & test.
MSA-DCS | WA3436391 | Unit 14 B15 Striker plate for personal latch damaged | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-22 22:30:00 | Fail | Require parts.Replace mortise lock and install over sized strike.
MSA-DCS | WA3436562 | Visits Cameras, computer is not working | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jul 2020 | 2020-07-10 16:25:06 | 2020-09-16 16:10:00 | Fail | Investigated fault, found multiple faults with workstation, found computer is not on essential power and lost power multiple times during generator / electrical works. Repaired operating system and software, reloaded and reconfigured. Tested OK.Sourced UPS's, returned to site, installed UPS on Visits Workstation and a UPS on Visits network switch to protect against power fluctuations.Tested OKJob Complete
MSA-DCS | WA3436591 | CCU (11), Cell C5- Shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-13 10:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3436629 | Kitchen, oven door glass is loose | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-13 14:50:00 | Pass | Check both ovens , ensure mounts are tight & rubber stoppers in place. Left both ok.
MSA-DCS | WA3436631 | Reception office aircon filter is dirty--requires replacement | Wandoo Rehabilitation Facility | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-14 12:30:00 | Pass | Found return air filter and grille to be blocked, took out filter and grille and gave both items a thorough clean, put filter and grill back and unit runs correctly.
MSA-DCS | WA3436654 | Instrusties welding bay - Faulty GPO's | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 15:00:00 | Pass | investigate and replace faulty gpos in industries welding bay
MSA-DCS | WA3436656 | Maintance truck bay area- Fluro Lights broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 09:00:00 | Pass | Investigate and replace broken lights in truck bay
MSA-DCS | WA3436670 | Unit 1, A wing - Priority Main grill stopped opening/shutting | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 13:53:27 | 2020-07-10 16:45:00 | Pass | Attended site.Checked Gallagher system in unit 1.Checked connections and mimic panel in unit 1 control room.Conducted test.All grills in unit 1 are operational
MSA-DCS | WA3436673 | stores switch/mailroom Ceiling requires repair | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-14 15:00:00 | Pass | ACCESSED ROOF & CLEARED AWAY DEBRISLEAKS IDENTIFIED AND REPAIRED
MSA-DCS | WA3436686 | Unit 1, A5 - wall vent needs fixing/replacing | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-09-01 11:30:00 | Fail | NEW VENT FITTED
MSA-DCS | WA3436702 | Unit 5, D5 -main lock is stiff & the doorhinges stretched affecting the door & lock operation | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 10 Jul 2020 | 2020-07-11 14:12:00 | 2020-07-13 11:00:00 | Fail | Contact site, job arranged for 13/07/2020.Replace hinges, door plate, lock and adjust strike.
MSA-DCS | WA3436717 | kitchen - sliding door is broken on the warmer | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-30 11:00:00 | Fail | Kitchen sliding door is broken on the warmer. Check door & guides. Make up new bracket & wheels. Refit door & test. All Working.
MSA-DCS | WA3436721 | Yeeda - Dishwasher not draining (suspect pump issue) | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-30 10:00:00 | Fail | Yeeda Dishwasher faulty, not draining. Check machine & controls. Dismantle, replace faulty water pump. Assemble & test.
MSA-DCS | WA3436764 | Emergency Generator - failed on test | Boronia Pre-release | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-27 10:29:00 | Fail | Batteries replaced
MSA-DCS | WA3436790 | PDA Transponder 2 is not working. | Karnet Prison Farm-Main Complex External Area | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jul 2020 | 2020-07-11 01:19:15 | 2020-07-11 00:45:00 | Pass | Attended site and investigated the fault.Checked connections and wiring on Transponder 2.Restarted MDAS master PC.Cleared all transponder errors and done stress test.Tested PDA 162.All ok at departure
MSA-DCS | WA3436791 | Cardex doors at main gate are not opening - system has gone down. | Karnet Prison Farm-Main Complex External Area | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Jul 2020 | 2020-07-11 01:12:01 | 2020-07-11 00:00:00 | Pass | Attended site and investigated the fault.Found that there is no signal on Gallagher monitor in control room.Reseted power on KVM extender and restarted workstation.Conducted test.All back to normal and operational
MSA-DFES | WA3436295 | ground front grass 2x sprinkler heads are broken one near mail box and front carpark space | CFRS Kiara | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-08-03 09:10:00 | Fail | Works completed once BRAF was approved.
MSA-DFES | WA3436464 | Engine Room light switch not turning off. | CFRS Osborne Park | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-14 09:15:00 | Pass | Locate faulty light switch in the engine room. Replaced faulty light switches with new. Advised staff of work completed.
MSA-DFES | WA3436601 | staff dinning room external door is locking everyone out | FESA RHQ - Forrestfield | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 0 | CLOSE | 10 Jul 2020 | 2020-07-10 16:49:29 | 2020-07-10 15:15:00 | Pass | 10/07/2020 - Dylan ParslowInvestigate door issues on staff dining room. Terminal block for comms on door controller found to be faulty.Terminal block replaced and tested. All ok.
MSA-DTAG | WA3436271 | Front office - leak in roof above JSO desk 1 | Armadale Courthouse | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-08-06 12:25:00 | Fail | REPAIR BOX GUTTER FRAMEWORK
MSA-DTAG | WA3436300 | Ground level, Admin - Custody Corridor camera not displaying on monitor. | Mandurah Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-17 12:45:00 | Fail | 13/7/20 - Ryan Vesty, Joshua ParkInvestigated fault with custody corridor camera.Camera faulty, requires replacement.BRAF submitted.17/7/20 - Ryan Vesty, Joshua ParkReplaced faulty camera and checked setup and recording, all working correctly.Extra time onsite due to prisoner transfer.
MSA-DTWD | WA3436111 | Level 3, A338 - Metal floor duct requires trimming as uneven | East Perth Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-14 15:00:00 | Pass | Liam Hanlon (14/07/2020) - Work NoteAttend site Sign in and get keys Locate room Gland plates for cabling has expanded and caused covers to rise Spoke to Steve Meyer and got room isolated Lifted carpet tiles and removed plates Cut to allow expansion in joints Replace tiles Clean up Let Steve know to arm smoke detectors Sign out and return keys*took photo of site time sign in sheet for hours
MSA-DTWD | WA3436268 | L1 print shop Air co in Print workshop doesnt fire up | Perth Campus B4 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-24 11:39:00 | Fail | Collected new UPS form supplier and brought to site. Gained access and isolated power and carried out install. Confirmed operation and HVAC plant operation restored to normal. Check and confirm constant supply through equipment. Work area has been left tidy. Plant operation is restored. Heating is working as required.
MSA-DTWD | WA3436284 | North Block, Room N222a - Faulty door lock | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-10 15:30:00 | Pass | replace cylinder components to door N222a
MSA-DTWD | WA3436292 | I Block, Room I005 - Faulty electrical hot water system (50L) | Balga Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-30 12:30:00 | Fail | Replaced faulty hot water unit
MSA-DTWD | WA3436481 | A block, level 2, A201 - Repair/ replace three faulty padlocks | Leederville Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-13 14:35:00 | Pass | deliver 3x replacement padlocks
MSA-DTWD | WA3436722 | A block, level 3, A310 - repair Eye wash station pressure lacking | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-15 12:53:00 | Pass | COMPLETED
MSA-DTWD | WA3436727 | F block, outside FG23 - Damaged Auto Air Vent on Condenser Water Line | Carlisle Campus | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-30 09:30:00 | Fail | Carried out works as per braf
MSA-DTWD | WA3436731 | Painting and Decorating main workshop - Heaters number 7 & 8 not working again | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 10 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-23 15:30:00 | Fail | Replaced faulty heater switch. All now working.
MSA-DTWD | WA3436770 | C Block, Room CG10 just outside CG18- Possible damage to wiring harness on crane hoist | Carlisle Campus | GMP-BR | Lifts | Vehicle hoists (LI) | SPECIALISED LIFTING SERVICE | 2 | CLOSE | 10 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-21 10:00:00 | Fail | DAS SUBMITTED FOR REPAIR TO BE COMPLETED AND REJECTED
MSA-DCA | WA3440934 | Perth Cultural Centre -25 James street light fault vandalised loose connection | Perth Cultural Centre Precinct-James Street Amphitheatre -Ground Floor | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 0 | CLOSE | 11 Jul 2020 | 2020-07-11 23:37:05 | 2020-07-11 22:00:00 | Pass | It was reported that a light was vandalized and it was a number from Parramatta that called me. I attended site and spoke to pcc SECURITY. They said that Jasmine reported the fault. I checked the orchard db, the pcs events db, and the Fuji room db all ccts were on and timeclocks functioning. I spoke with Senna while onsite and he said being the light so close to the pond at the art gallery that it would be fed from the db behind the art gallery. I asked the pcc security to call the art gallery security but there was only one of them and they couldn't let me into the db as they need to have at least to guards so one can escort me to the db. Pcc security understood that we attended and tried everything we could and were happy with our efforts.
MSA-DCS | WA3440875 | Unit MMU staff toilet light switch is faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 14:00:00 | Pass | Replaced cracked light switch
MSA-DCS | WA3440882 | Hakea perimter - Infer red beam 12 internal is in constant alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jul 2020 | 2020-07-12 08:55:38 | 2020-08-04 11:30:00 | Fail | Ran new security and power cable from Senstar SM in Obs post 4 to the receiver end of IRB 12. Aligned all beam pairs. Cleared weeds in between transmitter and receiver stacks. Tested ok to the gatehouse. Parts used:50m of underground 6 core security cable 50m of figure 8 cable
MSA-DCS | WA3440886 | Cell call 2.6 system in unit 1 not working.SJ | Roebourne Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Jul 2020 | 2020-07-12 09:16:08 | 2020-07-11 11:00:00 | Pass | *Phone support *Contacted site and found that problem with cell intercom in unit 1 is rectified and is fully operational.No attendance required.
MSA-DCS | WA3440908 | Melaleuca Prison-Unit 2 cell B5 can't open the door | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 11 Jul 2020 | 2020-07-11 17:17:44 | 2020-07-11 14:40:00 | Pass | After Hours attendance Saturday 11/07/2020. Repaired door as required
MSA-DCS | WA3440922 | cam 31 PTZ3 not working, no live feed | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 11 Jul 2020 | 2020-07-11 20:16:37 | 2020-11-25 10:55:00 | Fail | work order to be invoiced at cost to date.
MSA-DCS | WA3440933 | unit 1 - tap wont turn off, tap isolated at mains | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Jul 2020 | 2020-07-12 19:39:27 | 2020-07-13 11:24:00 | Fail | nil
MSA-DCS | WA3446104 | Unit2 cell 13 indicating Fire panel faulty fire alarm & it's not clear .Sj | Karnet Prison Farm-Dairy External Area | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 12 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 12:45:00 | Pass | smoke detector replacement
MSA-DCS | WA3446106 | Cowlling in zone 9 is say secure but stays in red & red not going off | Karnet Prison Farm-Administration, Stores Dairy Office | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Jul 2020 | 2020-07-13 07:14:53 | 2020-07-13 11:15:00 | Fail | Attended site and checked status and controller settings and logs. All had checked ok for zone9 cowling. Tested End of Line resistor and all had correct reading. Reset intelliflex controller and retested. Zone activation all tested ok. Job complete
MSA-DCS | WA3446111 | Intercom phone to the pedestrian gate is not working | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-13 08:00:00 | Pass | Attended and test Day/Night function, ok and working as normal.
MSA-DCS | WA3446116 | SITE COSTED CCU Cell 4 -Drains and the toilet blocked | Melaleuca Prison | WSM-BR-SITE | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 12 Jul 2020 | 2020-07-12 14:00:38 | 2020-07-12 12:50:00 | Pass | Clear blockage to shower waste
MSA-DCS | WA3446179 | Wooroloo Prison Farm - Gatehouse - Fire Panel - Smoke sensor alarm fault alert. | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 12 Jul 2020 | 2020-07-13 16:53:30 | 2020-07-13 14:07:00 | Pass | 12/7/20 JN - Wooroloo PrisonMaintenance fault in education computer room ceiling void. Could not reach detector with pole as detector mounted sideways in ceiling ontimber joist at the top of the ceiling. Will need 12ft steps to reach. Will need to return in the morning with 12ft steps.13/7/20 JN CMReplaced L4 S5 in ceiling performed loop test all ok
MSA-DCS | WA3446188 | UNIT 3 Cell Call system AMS error - not commuincating between control & cells | Albany Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-17 12:30:00 | Fail | Checked Cell Call consoles in all units and Gatehouse, all consoles showing error “ASM Receiver does not Respond” but all powered and on line. Checked status of all nodes by “Ping” command from workstation. Checked Site Management program and found it showing incorrect IP address. Change to correct IP address and changed priority of NIC for this address. Restarted all nodes and cleared alarms.
MSA-DFES | WA3450474 | RETROSPECTIVE WORK ORDER-EXTERNAL CHECK CARRIED OUT-Attended 12/7 | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 12 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-12 12:48:00 | Pass | Despatch Comments:Z22 REED SWITCH BAY 1 REAR DOORPatrol Resolution:EXTERNAL CHECK CARRIED OUT. NO PERSONS FOUND ONSITE BUT THERE ARE MULTI CARS PARKED ONSITE. ALL APPEARS SECURE.
MSA-DCA | WA3449919 | Fire Door between admin & main gallery wont release | Art Gallery of WA - James St - Main Building (Block B) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 13 Jul 2020 | 2020-07-13 17:00:00 | 2020-07-13 09:45:00 | Pass | Attended site & liaised with FM.On attendance found the sliding fire door between Admin & gallery wedged open due to the door holder magnet not functioning.Identified faulty door magnet which works but has an intermittently working release button switch.Currently the magnet is functioning but recommend a like for like replacement.On a Power outage the sliding fire door closes & staff re-instate the door by depressing this door release button & then proceed to push the door into the open position.Note:The sliding door is not designed to be battery backed and as a result on every power outage the door releases & requires re-instating.Photo attached. Passed to Passive/EELS Manager to provide quotation.
MSA-DCA | WA3450064 | Due to power cut - BMS alarms in fault | Art Gallery of WA - James St-Main Building (Block B)-Level 1 (Ground Floor)-Security Office | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-27 13:00:00 | Fail | Attended call. Power outage over wknd caused Pneumatic Air Station and stand alone unit to fault, requiring manual reset. In turn this caused Steam Boiler 1 and Steam Boiler 2 to trip on gas pressure alarm. Reset Air Stations and gas pressure switches. RO reverted to last backup save point which is manual off. Put in auto. New backup required to eliminate manual start up on power loss.0 alarms active.
MSA-DCA | WA3450823 | Fault on Munters De-hum unit | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 10:00:00 | Pass | Attended site 14-7-20 0800. Dehumidifier system servicing HBC wet store in fault. Applied tests and checks to find system SA fan VSD in fault. Reset VSD and checked incoming electrical voltage and current (ok) checked integrity of mechanical services switching contactors and relays (ok). Reset VSD and monitored systems operation. System operating correctly. Left site 14-7-20 1000.
MSA-DCS | WA3449860 | WWTP - FM101 meter faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 11:00:00 | Pass | Investigate and repair faulty meter at wwtp
MSA-DCS | WA3449862 | WWTP - electric sink valve faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-27 16:30:00 | Fail | Investigate faulty electric sink valve at WWTPRequires replacement parts
MSA-DCS | WA3449864 | WWTP - P105 clarifier drain pump faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 15:00:00 | Pass | Investigate and repair WWTP clarifier drain pump
MSA-DCS | WA3449866 | WWTP - external light faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 09:00:00 | Pass | Investigate and repair external light at WWTP
MSA-DCS | WA3449878 | Main Control Room- 2x monitors are not functioning | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 13 Jul 2020 | 2020-07-13 11:22:20 | 2020-07-13 11:00:00 | Pass | Restored alarms Video Wall. Tested alarm activation, all OK.
MSA-DCS | WA3449891 | Camera 19 is offline - Error message "Camera server failure" | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 07:27:27 | 2020-07-13 09:15:00 | Pass | Rectified and fixed the fault from DVM, camera back to normal operations.
MSA-DCS | WA3449929 | Unit 6, Cell A12- Flush button not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-14 09:57:00 | Pass | Replaced broken flush button
MSA-DCS | WA3449932 | Unit 6, Cell D1- Flush button not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-14 10:48:00 | Pass | Replaced outlet washer
MSA-DCS | WA3449934 | West Admin Dining Room- Fluro Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-15 10:00:00 | Pass | Replaced faulty lamps and damaged tombstones
MSA-DCS | WA3449936 | Unit 5, Cell C4- Fluro Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 13:00:00 | Pass | Replaced damaged tombstone
MSA-DCS | WA3449941 | Unit 1, Cell C16- GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 07:56:46 | 2020-07-13 12:30:00 | Pass | Replaced damaged blank plate
MSA-DCS | WA3449946 | Kitchen, Wash Area- GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 07:57:49 | 2020-07-13 11:00:00 | Pass | Replaced smashed blank plate
MSA-DCS | WA3449950 | Unit 4, Cell C13- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 15:00:00 | Pass | Replaced damaged light
MSA-DCS | WA3449952 | Stores- Roller Door is faulty/not staying up | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | UNIVERSAL DOORS | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-08-03 15:00:00 | Fail | ATTENDED SITE, SUPPLY & INSTALLED ONE (1) ROLLER SHUTTERDRUM & HANDCHAIN WINDER
MSA-DCS | WA3449958 | Unit 13, Cell D7- Shower screen leaks water onto bed & puddles onto floor under bed | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-22 13:00:00 | Fail | REMOVE OLD SILICONE REPLACE WITH NEW
MSA-DCS | WA3449967 | unit 4 B4 light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 13:00:00 | Pass | Replaced damaged light
MSA-DCS | WA3449974 | unit 10 B1 & B11 Toilets leaking, B4 Sink leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 09:06:00 | Pass | Replaced x2 orings on outlets Replaced x1 outlet washer on cistern
MSA-DCS | WA3449980 | front gate main sliding door Continually open and closing | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 08:12:42 | 2020-07-13 15:30:00 | Pass | Attended site and inspected auto door. Noted door turned off . Restored power to door and testedoperations . Located fault to safety beams holding door open . Required to clean beams andtested operations all ok without any further issues .
MSA-DCS | WA3449982 | Unit 6- Air Con in computer room has mould inside it | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 10:30:00 | Pass | Cleaned coil, scroll and drip tray to eliminate odor. OK at time of departure
MSA-DCS | WA3449988 | Reception, Female Toilet- Fluro globe flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-13 14:00:00 | Pass | Repaired faulty lights in female toilets in reception
MSA-DCS | WA3449993 | Unit 7, Control Room - Panel cover of the buttons requires repairing | Casuarina Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2021-03-22 12:00:00 | Fail | Console and obselete equipment in this unit have been replaced.
MSA-DCS | WA3449999 | Outpatients Area sink next to mental health room is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 11:00:00 | Pass | Plunged blockage sink and toilet to clear blockage.
MSA-DCS | WA3450000 | INF (10), Cell B1- 2x Observation lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 15:30:00 | Pass | Repaired faulty lights in infirmary B1
MSA-DCS | WA3450071 | Visit hall, Staff room, The boiler is not working.It controls the cold filter water & boiling water | Melaleuca Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 13:00:00 | Pass | AMS654289 / WA3450071Attended site to investigate fault on Hot Water Heater #2.
MSA-DCS | WA3450076 | Unit 14, Cell 16- Toilet is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 09:00:00 | Pass | Removed fruit from drain. Plunged drain to clear blockage.
MSA-DCS | WA3450080 | Unit 13, Cell D6- Shower is dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-14 10:00:00 | Pass | Replaced leaking spindle in shower.
MSA-DCS | WA3450084 | Unit 13, Cell A1- Water from basin squirts over basin & onto cell floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-14 15:00:00 | Pass | Cleaned strainer in basin tap.
MSA-DCS | WA3450087 | Unit 13, Cell C7- Basin continually blocks | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-14 16:00:00 | Pass | Plunged basin to clear blockage in basin
MSA-DCS | WA3450094 | MPU(8), Cell M16 - sink water tap has low pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-14 17:00:00 | Pass | Cleaned blockage from inside tap outlet. Test basin. Ok
MSA-DCS | WA3450115 | Kitchen- Brat Pan wont stay lit | Banksia Hill Detention Centre | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 10:00:00 | Pass | Brat Pan won't stay lit. Check pan & controls. Dismantle, remove faulty burner. Repair and replace parts (Pilot fitting). Assemble & test.
MSA-DCS | WA3450116 | Unit 7, Cell C4- Prisoners window requires new spiral balancers | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 10:00:00 | Pass | REPLACE SPIRAL BALANCES & WINDOW FEET
MSA-DCS | WA3450118 | unit 4A 18 vinyl on the floor lifting | Wooroloo Prison Farm | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-11-26 11:15:00 | Fail | new vinyl flooring installed 2x areas
MSA-DCS | WA3450124 | Unit 13 - D11 Light fitting cover has been painted and needs replacing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-22 10:00:00 | Fail | Repaired faulty lights in unit 14 d11. Site stock used from workshop
MSA-DCS | WA3450128 | Unit 7, C wing, SCU unit - Urn takes extermely long time to refill after approx 4 prisoners use it. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-29 09:00:00 | Fail | A40189258Q installed new Rheem Boiling Water Unit Wallmounted - SN 06479 removed old to tip
MSA-DCS | WA3450136 | Unit 1 - A9 During security checks, it was identified that cell call is not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 15:30:00 | Pass | Drilled out retaining Rivets, removed cell call from wall. Noticed that the button mechanism had become unseated from rear of push button. Reset button and tested cell call to gate control. Good audio both ways.
MSA-DCS | WA3450142 | Unit 13, B2 - Air vent will not open | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-16 13:30:00 | Pass | repair to air vent completed
MSA-DCS | WA3450146 | Unit 1 - A12 During security checks, it was identified that cell call was faint at receiver end (POD | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 14:30:00 | Pass | Cell call speaker grill full of foreign matter (tooth paste). Drilled out retaining Rivets, removed cell call from cell. Stripped down cell call, cleaned and reassembled, returned cell call to cell and tested to gate control. Good audio both ways. Resecurred Cell call into bed end.
MSA-DCS | WA3450177 | Unit 3, front entrance - Loud Speaker on East side of front Unit wall outside yard not working | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-10-06 10:30:00 | Fail | Attended unit 3, erected temp scaffold, removed existing failed PA Horn Speaker, mounted new horn speaker on wall, connected and tested. Tapped strip connector joint pushed back cable. Deconstructed temporary scaffold, loaded on transport trailer, departed site.
MSA-DCS | WA3450184 | Unit 14, A/C regi oven faulty (see notes) | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 09:50:00 | Pass | Replaced Contactor and tested ok
MSA-DCS | WA3450307 | Unit 3 D wing Light above kitchen broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 09:30:00 | Pass | Investigate and replace lights in unit 3 D wing
MSA-DCS | WA3450313 | Unit 1, Cell A9- Ceiling lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-16 08:30:00 | Pass | Repaired GPO and light in A9 Unit
MSA-DCS | WA3450322 | Unit 3, D Wing- Light above kitchen is broken, GPOs broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 12:00:00 | Pass | Investigate and replace gpo’s in unit 3 D wing
MSA-DCS | WA3450367 | Control Room - Monitor is not powering up | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 10:29:48 | 2020-07-13 15:00:00 | Pass | Travelled to site and found power supply to ISU monitor was faulty. Collected part and replaced with new 12vdc power supply. All replaced and tested working ok. Job completePart used. 1 x 12vdc 5ah used
MSA-DCS | WA3450377 | unit 1 Pod 9 and 6 heater timers are faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 12:00:00 | Pass | Replaced 2x contactors
MSA-DCS | WA3450379 | Unit 1 pod 4 heater timer faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 13:30:00 | Pass | Replaced contactor for heaters
MSA-DCS | WA3450381 | Unit 4A pod 4 and 5 heater timer fault | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 14:30:00 | Pass | Replaced damaged contactors
MSA-DCS | WA3450383 | Unit 2A cells 13 to 23 heater timers faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 15:30:00 | Pass | Replaced contactor for heaters
MSA-DCS | WA3450384 | Unit 4C heater timer faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-13 15:30:00 | Pass | Replaced contactor for heaters
MSA-DCS | WA3450422 | Unit 5, B&D - floor buffer has ceased working | Casuarina Prison | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-16 12:00:00 | Pass | Repaired faulty floor buffer and steam cleaner in unit 5
MSA-DCS | WA3450437 | Unit 5, B/D Wing- regethermic oven's steam pipe has broken loose. | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-08-07 10:35:00 | Fail | Fit door lock spring ok noted water pipe mounts now missing. Fit water pipe to fan baffle as required.
MSA-DCS | WA3450464 | Unit 5, Control room - PA system has stopped working | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 11:19:59 | 2020-07-13 13:00:00 | Pass | Checked with a Unit 5 Control. Advised that they got “Busy Tone” from telephone on pickup, unable to dial PA Access. Checked other units and telephones and identified problem as Site-Wide, with some telephones with displays showing “Congestion”. Problem related to the Ericsson PABX System. Contacted the NEC on-site DoJ techs for action by them. They advised that they had done a backup on the PABX, and the problem should be resolved. Test from various telephones on-site confirmed system operating correctly.
MSA-DCS | WA3450466 | Unit 2 A and B wing shower block shower room closes to control room shower rose fault- see notes | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 12:30:00 | Pass | COMPLETED
MSA-DCS | WA3450469 | Unit 2 cell D8 bed light faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 15:00:00 | Pass | Replaced led bed light
MSA-DCS | WA3450470 | Unit 3, B Wing, Cell B05 - Toilet doesnt flush fully | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-15 13:00:00 | Pass | Adjusted flush button assembly to operate correctly.
MSA-DCS | WA3450532 | Unit 4, D6 - Viewing Hatch Smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 11:59:16 | 2020-07-14 12:15:00 | Fail | RE GLAZE OBS PANEL
MSA-DCS | WA3450539 | Unit 3 A2 vinyl flooring damaged | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2021-04-14 14:30:00 | Fail | supplied and installed new vinyl flooring
MSA-DCS | WA3450540 | Unit 3, C5 - Cell Call Faulty | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 12:03:20 | 2020-07-15 16:00:00 | Fail | Monday 13/07/2020-phoned U3 to find out about the fault. Officer reported that the intercom CALL button needed to be pressed 2 or 3 times to get an activation. Officer said that the prisoner had been moved to another cell and they were not desperate to have the cell operational so attendance on Monday was not required. Wednesday 15/07/2020No fault found when tested. Intercom activated first time every time. I believe the officer that reported the fault thought the intercom was faulty because the LED on the newer intercoms will only illuminate once the call is answered in the control room, not as the call button is pressed. Audio test3 loud and clear in the cell and in control.
MSA-DCS | WA3450547 | Unit 3, d1 - GPO Smashed | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-16 11:30:00 | Pass | Replaced faulty gpo
MSA-DCS | WA3450570 | Unit 4 C6 cell light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 14:00:00 | Pass | Replaced damaged light
MSA-DCS | WA3450578 | Unit 4 C wing Grille Lock Plate Loose | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 12:19:18 | 2020-07-13 13:45:00 | Pass | Replaced screws to secure lock into door
MSA-DCS | WA3450603 | Unit 13, external lights faulty | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-09-23 12:00:00 | Fail | Repaired and replaced damaged external lights in unit 3
MSA-DCS | WA3450604 | Unit 4 D9 Tap Broken, leaking from below basin. | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 11:40:00 | Pass | Replaced pillar tap
MSA-DCS | WA3450616 | Unit 5 to Medical centre- 1st & 4th pole lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-08-12 09:30:00 | Fail | Replaced 2x pole lights in unit 5
MSA-DCS | WA3450623 | Mechanical Assessment to Male and Female Bathrooms- see further notes below | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 10:21:00 | Pass | Full report & remedial works issued to Niall Dwyer
MSA-DCS | WA3450635 | Vegetable Prep- Damaged copper pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 09:30:00 | Pass | Repaired damaged pipes and valves on air compressor line. Parts collected offsite
MSA-DCS | WA3450665 | laundry No2 unimac washer not spinning dry | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 13:17:01 | 2020-07-15 12:15:00 | Fail | Found left side drain valve faulty.
MSA-DCS | WA3450738 | Maintenance - Workshop Damaged Power point | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-15 12:00:00 | Pass | Repaired damaged gpo in maintenance workshop
MSA-DCS | WA3450815 | Kitchen sink tap leaking needs new spindle | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 11:30:00 | Pass | COMPLETED
MSA-DCS | WA3450817 | Kitchen - reverese osmosis connection on the pipe is broken | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 10:15:00 | Pass | COMPLETED
MSA-DCS | WA3450818 | Medical Centre - external tap on east end of building is leaking, needs washer | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 09:00:00 | Pass | COMPLETED
MSA-DCS | WA3450824 | unit 3, D3 - Sink leaking from underneath | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 13:10:00 | Pass | Replaced pillar tap
MSA-DCS | WA3450825 | Facilities Manager, Office - Fluorescent Light Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 11:30:00 | Pass | Replaced damaged light
MSA-DCS | WA3450829 | Official Visits, Prisoner Toilet - not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 15:37:10 | 2020-07-15 07:35:00 | Fail | Need to sorce new button 15/7/20 installed new button
MSA-DFES | WA3450339 | 1St Floor, gym- Aircon unit keeps going to fault | CFRS Perth | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-08-06 15:30:00 | Fail | Replace LP switch. Unit running good.
MSA-DFES | WA3450375 | Hallway to Dormitory 3 x lights not working | Success Career Fire Station (Temp Site) | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 10:30:00 | Pass | Arrived at 945 to repair 3 fluro fittings in upstairs office. Located repaired and tested Fluro fittings and signed out at 1021
MSA-DFES | WA3450376 | ground level - Disabled Toilets Sink tap mixer broken | CFRS Perth | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 06:57:00 | Pass | Investigate broken basin mixer located disabled toiletOn arrival inspected mixer and all in working order tested and checked for leaks Pack up and clean up worksite Start time 14/07/20 9:15amFinish time14/07/20 9:45am
MSA-DFES | WA3450478 | Side gate near under croft parking is not opening with swipe card | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 12:00:00 | Pass | 14/7/20 - Dean Simpson, Joshua ParkInvestigated issue with side gate.Checked reader operation.Checked operation of 2 door controllerChecked reader at 2 door controllerRestarted using latest firmware.Return required.15/7/20 - Dean Simpson, Martin Scott, Joshua ParkAfter more testing we replaced the chip on the 2 door controller, and gate started working.Fully tested operation and all ok.29/7/20 - Dean SimpsonAsked to return as gate not working again.Found gate was in unlocked state, restored the gate to the locked state in the system, and tested.All working ok.
MSA-DFES | WA3450494 | Bathroom FF’s Dorm 5- Water leaking from ceiling Fluro light above basin. | CFRS Osborne Park | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-22 15:56:00 | Fail | Roof leak rectified, job complete pending paperwork and photos.
MSA-DFES | WA3450712 | Ground floor engine room, Tunic room - Dryer cabinet electrical malfunction. | CFRS Hope Valley | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-08-31 09:30:00 | Fail | COMPLETED
MSA-DFES | WA3450820 | Admin, eAcademy - External eAcademy door is not unlocking with fob. Sontec required for Pacom system | FESA RHQ - Forrestfield | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 15:30:00 | Pass | 15/07/20 - Ryan VestyInvestigated issue with door not unlocking. Tested Reader 17.Found fault at cables for lock. Reterminated cables at lock.Tested all equipment. All working ok.
MSA-DFES | WA3450858 | Rear roller door No 3 - timer incorrect, coming down 2 quickly. | CFRS Malaga | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-17 09:00:00 | Fail | Technician attended the site of Malaga Fire Station, Engine Room Roller Shutter W22583 on 14/07/2020. Following a full test and inspection of door components found fault to be door timing was not correct and auto closing after 10 seconds and not 2 minutes as required. Upon further discussion with AAES techs and office, found that a new PLC is required to be installed if this ever became an issue again.Technician returned on site on 17/07/2020 and found out PLC timer on Door 3 was incorrect. He modified parameter to same figure as other doors, 3 mins countdown. Tested and working. Full test and inspection of door function completed prior to leaving site.Note: There was an error on FR's time on 17/07/2020, we followed CBRE time.Quote was not approved - to be invoiced at $500.
MSA-DTAG | WA3449902 | External - Sewer alarm has activated | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 13 Jul 2020 | 2020-07-13 17:00:00 | 2020-08-24 10:00:00 | Fail | COMPLETED
MSA-DTAG | WA3449908 | Hole above the wall footing needs to be re-plastered & whitewashed | Supreme Court | GMP-BR-HO | Building | Internal Walls (BU) | PPM Project Painting & Maintenance | 2 | CLOSE | 13 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 12:00:00 | Pass | Repair and Re-paint wall areas
MSA-DTAG | WA3450102 | L13 male toilet No lights working in the male toilets. | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 08:00:00 | Pass | Job complete
MSA-DTAG | WA3450241 | Pacom PC that monitors the gates isn’t working | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-13 16:00:00 | Pass | PC logged in OK and tested OK
MSA-DTAG | WA3450410 | Lvl 13, Conference Room - Replace 2 stained carpet tiles – stock tiles on level 6 | Central Law Courts | GMP-BR-HO | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 10:50:00 | Pass | Replaced 2 stained carpet tiles to level 13 conference room with stock tiles.
MSA-DTAG | WA3450427 | Investigation of FIP to determine that the unit responds correctly when in alarm mode- Info below | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-14 17:30:00 | Pass | Attended site and checked operation of fip system after repairs took place.
MSA-DTAG | WA3450459 | L5 court 56 Fountain near court 56 is not draining. | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-14 13:45:00 | Pass | Complete
MSA-DTAG | WA3450491 | Investigation of FIP to determine that the unit responds correctly when in alarm mode- Info below | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-08-29 16:30:00 | Fail | Attend site with fire contractor. Put fire panel into first floor alarm. Investigate first floor electric duct heater mssb fire relay not working. Found relay in mssb to remain energized in fire mode. Trace fire relay wiring back to DB3, found wiring to go through R6 fire relay first floor. Check relay voltage with fire alarm off, found contact to be closed. Check voltage with fire alarm on and still found contact closed. This contact should open and drop out fire relay. Existing R6 relay contacts have failed. Extra relay required. Isolate DB3 to install new relay, found all power to drop even ups backup. Found UPS battery to have failed and no longer works. Lost power to PC and all controls. New UPS required. Install new relay and wire off R6, run wiring through the normally open contacts. Turn power back on and had to reset UPS. Test operation of heater mssb, fire alarm on first floor found mssb to drop out as normal. Wire modifications complete and fire system working as normal.
MSA-DTAG | WA3450617 | Ceiling light brackets in custody interview room are loose – lawyers side | Joondalup Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-22 09:15:00 | Fail | Inspected fault to custody and refitted light and replaced missing speaker to interview room 1. Will return due to access and parts.Returned with parts and replaced damaged speaker and Resecured light+ found broken cable in roof and repaired.Tested all working
MSA-DTWD | WA3449847 | A Block, Repair leak to Expo in front of security desk | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-10-08 11:39:00 | Fail | REPAIRS MADE TO ROOF TO ELIMINATE LEAKING
MSA-DTWD | WA3449848 | A Block, Repair roof leak outside A338 in passage | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Jul 2020 | 2020-07-17 17:00:00 | 2020-11-23 09:00:00 | Fail | ROOF LEAKS LOCATED & REPAIRED
MSA-DTWD | WA3449915 | B Block, Carpark lights & external lights will not reset | Munster Campus (ACEPT) | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 13 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-14 10:30:00 | Pass | Attended site and signed in. Located switchboard that controls the carpark lights. Found faulty timer. Investigated carpark lights and found one footpath pole with a damaged pole top. Isolated light, replaced timer and re-energised. Lights all now work. Replaced globes and ballasts in various lights in A block and T block
MSA-DTWD | WA3450333 | N Block - Repair/makesafe brick wall on the eastside of N Block. | Midland Campus | GMP-BR | Building | External Walls (BU) | AWB Co. | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-10-08 15:30:00 | Fail | Costs to Complete: Specialist Contractor to attend and repair of the wall on N blockCutting & Demolition of the wall & Install Temp Fencing for Safe works and Skip Bin for waste removalRemove and lay aside existing gates for re useCut the wall at the gate where the pillar is and do colourbond from existing pillarsSupply and install of no more than 13 linear metres of colorbond fence at 2.1m high including coringIncluding 300mm extender pieces 13 linear metres supply and install option
MSA-DTWD | WA3450351 | Car park 1- Car park light #37 not working | Thornlie Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-14 11:45:00 | Pass | Found a faulty cabling on light pole. Site advised to install a solar instead. Will complete Braf. Braf declined. Invoiced costs to date.
MSA-DTWD | WA3450354 | level 1, Laneway Museum - Replace missing rwdp - storage unit in laneway | Perth Campus B7 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-13 12:45:00 | Pass | Found downpipe missing part in facilities officereinstalled with new rivets
MSA-DTWD | WA3450413 | H block, H006 (kitchen) - Leaking flickmixer | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-15 15:45:00 | Pass | Replaced leaking mixer
MSA-DTWD | WA3450416 | J Block, Room J011/J012 (external)- Security lighting not working (suspect faulty day/night sensor) | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-16 15:30:00 | Pass | Replaced faulty sensor, Fluor tube and starter. All now working.
MSA-DTWD | WA3450600 | F block, ground floor, ECO 1 - replace/repair 3 broken padlocks | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 13 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 11:25:00 | Pass | Replace 2 x 42886 padlocks & 1 site padlock
MSA-DTWD | WA3450609 | building 8, grounf level, 8G46 - Power point next to fridges pulled out of wall | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-13 14:30:00 | Pass | Attended site and signed in. Located faulty gpo. Re secured to wall as required. Tested all okay job complete
MSA-DTWD | WA3450620 | building 7, ground, Student Common Room - Light fitting full of water and hanging from ceiling | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-13 16:00:00 | Pass | Attended site and signed in. Located faulty light in common room. Disconnected and removed. Made safe cabling. Light not required anymore. All okay job complete
MSA-DTWD | WA3450627 | External - Pot holes to be repaired as per locations below | Balga Campus | GMP-BR | Paving & Roadworks | Asphalt (PR) | MR POTHOLE | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 10:00:00 | Pass | Repairs to potholes
MSA-DTWD | WA3450659 | M block ground M012 (Male student toilet) Both urinal buttons and surrounds missing | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-15 17:00:00 | Pass | Replaced flush buttons for urinal
MSA-DTWD | WA3450786 | Room A313- Repair leak | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-12-10 13:36:00 | Fail | Roof leak repaired
MSA-DTWD | WA3450945 | A block, roof level, toilet fans - Exhaust fans not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 13 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-14 09:30:00 | Pass | Job completed awaiting return of signature slip via email due to covid 19
MSA-DTWD | WA3451106 | C Block, customer service, Electric door - not working | Bentley Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 12:19:00 | Pass | On inspection, found unit in fault mode due to recent power failure/surge.Reset unit, tested and adjusted, all ok.Unit passed battery charge.
MSA-MRWA | WA3450476 | Level 1, Kitchenette - Boiled water unit not working please inspect and remediate Asset# A402020366 | Don Aitken Centre MRWA Head Office-Main Building-First Floor | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 13 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 10:20:00 | Pass | Replaced corroded tap assembly.
MSA-DCA | WA3454612 | Corporate Office Temperature Sensor sending incorrect temp to BMS | His Majesty's Theatre-Theatre Building-Level 2-Open Office Area | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Building Automation & Electrical Services Pty Ltd | 2 | SSP | 14 Jul 2020 | 2020-07-17 17:00:00 |  | Overdue
MSA-DCS | WA3451352 | EXT and INT perimetre not working - due to thunder strike. | Hakea Prison-Administration Block West | WSM-BR-RC | Building | General Building (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 05:10:15 | 2020-10-02 14:14:00 | Fail | Multiple systems down after lightning strike. Performed emergency temporary repairs after lightning storm damaged multiple systems including duress system, perimeter detection systems, CCTV and servers. Worked to restore systems and make permanent repairs. Tested all systems OK.Job Complete
MSA-DCS | WA3453699 | Control room and various locations - MDAS system not working | Banksia Hill Detention Centre-Gatehouse | GMP-BR-RC | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 09:26:24 | 2020-09-16 10:27:00 | Fail | Repaired multiple duress system faults after lightning strike, tested duress system OK.Parts Used:Consumables (SEME Stock)Job Complete
MSA-DCS | WA3453702 | Control room - Cameras around the centre are not working due to Lightning strike | Banksia Hill Detention Centre-Gatehouse | GMP-BR-RC | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 09:31:47 | 2020-10-08 14:29:00 | Fail | Repaired multiple system and camera faults caused by lightning strike.Tested OKJob Complete
MSA-DCS | WA3453735 | Fire pumps at zone 4 need to be shut down | Hakea Prison-Main Gatehouse | GMP-BR- HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 10:40:25 | 2020-07-14 09:08:00 | Pass | Isolate and refuel both fire pumps. Reinstate to “ready” status.
MSA-DCS | WA3453764 | Zone control 1, sally port doors not operational | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 11:07:40 | 2020-07-14 12:10:00 | Fail | 14/07/20Inspect power supply. Reset limits.
MSA-DCS | WA3453780 | Unit 14, C Wing, Cell C8 - Drain blocked in shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-15 14:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3453798 | Unit 14, Cell A11 - Shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-15 15:00:00 | Pass | Used acid and plunger to clear blockage in shower drain
MSA-DCS | WA3453802 | CCTV in security office is not working | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-14 13:00:00 | Pass | Checked video from Gatehouse Equipment room, no video from Visits area. Attended Security workstation, found video only available from Visits area, none from the remainder of site. Confirmed Power on network switch , noted no signal activity on Fibre SFP Port 25 on switch. Attended Health CCTV Cabinet traced fibre patch leads and found no led activity on port from Admin Building, transferred fibre SFP to vacant port in Health switch, no change. Returned to Admin Computer Rack and transferred Fibre SFP from port 25 to Port 27, port activity lights flashing on new port. Returned to GH to confirm camera images being received and recording. Confirmed all site cameras viewable from Security.
MSA-DCS | WA3453816 | Female area - Alarm on gate keeps tripping | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 10:00:00 | Pass | Checked reed switch fault and tested connections, reed switch resistor showing slightly low resistance, replaced resistor and sourced new bracket as bracket was warped/damaged. All reading tested and working ok. Job complete
MSA-DCS | WA3453818 | PDA main unit has no volume | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-16 17:00:00 | Pass | Replaced Cat6 cable between gatehouse and arunta room.Gained access below arunta room and comms room.Replaced cable with Cat6 from Seme stock 30m of underground Cat 6
MSA-DCS | WA3453821 | Unit 13, Cell D7- Water entering from roof space | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-17 19:00:00 | Pass | Collected parts and tools from supplier. First attempt to repair failed. Had to return to supplier in Osbourne park for new fittings. Second attempt to weld passed. Tested and ok
MSA-DCS | WA3453823 | Unit 13, Cell B14- sink is very slow to drain. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 16:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3453826 | Yeeda Unit Cupboard near Cell 6 lock is faulty | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-14 10:00:00 | Pass | Gained entry and replaced faulty lock.
MSA-DCS | WA3453827 | Unit 14, Cell B14- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 17:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3453830 | Unit 14, cell D11 - shower pressure low | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 18:00:00 | Pass | Shower ok. Basin blocked. Plunged basin to clear blockage
MSA-DCS | WA3453832 | Unit 14, Cell C1 - Water pressure low, drain blocked in shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-16 18:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3453834 | Unit 14, cell D10 - sink and drain blocked - tap broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-17 10:30:00 | Pass | Shower taps ok. Basin blocked and plunged.
MSA-DCS | WA3453836 | Unit 14, cell A9 - low water pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-17 10:30:00 | Pass | Cleared blockage in shower head and basin. Adjusted pressure
MSA-DCS | WA3453841 | Fault relating to lighting strike | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 12:16:09 | 2020-07-14 11:30:00 | Pass | Tested power at site DBs and reset transformer in admin
MSA-DCS | WA3453842 | Unit 14, Cell B13- main cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 10:00:00 | Pass | Repaired faulty lights in unit 14 b13
MSA-DCS | WA3453846 | Unit 14, cell D15 - bed light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-22 10:00:00 | Fail | Repaired faulty lights in unit 14 d15. Pick up replacement ballasts from wshop site stock
MSA-DCS | WA3453853 | Unit 14, Cell A9 - bedside light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-22 11:30:00 | Fail | Unit 14 Cell A9 Job Not complete - waiting for replacement driver
MSA-DCS | WA3453857 | Unit 1, Westside cages in A/C Yard- Cage 4 is coming away & needs welding | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-08-04 12:00:00 | Fail | 15/07/20Inspected fault04/08/20Welded broken mesh back to panel
MSA-DCS | WA3453860 | Health Admin- Lock on internal door to pharmacy will not unlock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 08:26:29 | 2020-08-10 11:00:00 | Fail | Open jammed lock temp. repair.Replace barrels.
MSA-DCS | WA3453887 | Unit 7 Control Room - ballast required for light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 07:00:00 | Pass | Replaced faulty ballast and tombstones
MSA-DCS | WA3453990 | Kitchen, fridge - fridge running hot | Wandoo Rehabilitation Facility | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 13:28:26 | 2020-07-16 14:41:00 | Fail | Repaired kitchen coolroom. Carried out full operational checks all ok
MSA-DCS | WA3454111 | laundry - speed clean washing machine #1 - stuck on washing cycle | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | VEECO PTY LTD | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 10:10:14 | 2020-07-15 11:15:00 | Fail | Advised machine was full of sheets when run and drum did not turn normally. Suspect machine was overloaded causing the belts to slip and smell. Ran 2 cycles now ok
MSA-DCS | WA3454164 | Unit 1, prisoners toilet - toilet bowl broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-24 11:30:00 | Fail | Supply and install new toilet pan in unit one toilet block.
MSA-DCS | WA3454169 | Unit 1, office toilet - toilet bowl broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-24 12:30:00 | Fail | Refix loose pan to floor in office block.(Silicone and pan screws - truck stock)
MSA-DCS | WA3454187 | Mitchell house - hot water tank corroded leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 11:07:26 | 2020-07-15 14:15:00 | Fail | Complete
MSA-DCS | WA3454200 | Vegetable Preparation - repair potato rumbler in vegie prep | Casuarina Prison | WSM-BR-SITE | Equipment | Electrical Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-08-25 16:30:00 | Fail | Vege prep Potato peeler faulty. Check peeler, remove for repair. Dismantle, remove motor & mounting. Order new belt. Replace bearings & belt. Repair wiring. Assemble & test. Return to store.
MSA-DCS | WA3454244 | UNIT 1, B WING, Grille, - Officer keys gets stuck in the lock.(barrel sticking)? | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 11:35:50 | 2020-07-14 14:45:00 | Pass | Unit 1 / B Wing Key getting stuck in Key switch for Mag Lock Key switch removed from wall and barrel tightend , reassembled with security screws
MSA-DCS | WA3454256 | Unit 10, A8 - Floor waste blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 08:05:00 | Pass | Floor waste blocked I removed grate removing plastic knifes plunger basin and floor waste clearing blockage left running for a while to make sure was clear before reinstalling grate
MSA-DCS | WA3454302 | Unit 7, S wing Corridor - Lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 10:30:00 | Pass | Replaced faulty tombstones
MSA-DCS | WA3454309 | Vegetable Preparation - 2rd cry vac machine not doing the second seal | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 12:13:44 | 2020-08-11 12:00:00 | Fail | Vege Prep, 2nd cryvac machine faulty. Check machine, replace elements. Remove to workshop. Repair element holder & mounting. Return to Vege prep.
MSA-DCS | WA3454342 | Unit 14, B9 - Cell B9 bathroom blocked and water is coming out of cell & spreading in front of B8&B9 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-15 12:00:00 | Pass | Plunged toilet to clear blockage.
MSA-DCS | WA3454413 | Kitchen - Combi oven 4 faulty seals | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 12:39:07 | 2020-07-15 10:00:00 | Pass | Replaced broken doorseal and tested for steam leaks.
MSA-DCS | WA3454453 | Visits hall, All Cameras not working | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 17:09:53 | 2020-10-09 16:02:00 | Fail | Found several ports on network switch not working. Installed 2 x 24 Port network switches in visits comms room and configured all ports and devices. Tested all devices in Visits building OK.Job CompleteParts used:2 x Planet 24 Port PoE Network Switches4 x SFP ModulesFiber patch leads and copper patch leads
MSA-DCS | WA3454584 | PTZ 6 no movement | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-16 12:05:00 | Pass | Tested camera with test monitor,camera working. Reset modem and confirmed with control PTZ functions
MSA-DCS | WA3454585 | MDR 5 offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 18:00:00 | Pass | Raid 1 and 4 have failed, contacted Indigo and checked logs.Disks have become corrupt and unable to recover.replaced disk from site stock (no more AS3000 HD onsite anymore)rebuilt raid and confirmed cameras recording.
MSA-DCS | WA3454586 | Camera footage - Download camera footage from MPC2 | Wooroloo Prison Farm | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 15:05:29 | 2020-07-15 11:30:00 | Pass | Security footage download see security for details
MSA-DCS | WA3454587 | Unit 2 - no control on all doors in unit | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 19:07:21 | 2020-10-07 15:49:00 | Fail | Repaired workstation and tested OK. Reattended and confirmed workstation is still working correctly.Job Complete
MSA-DCS | WA3454588 | Unit 1CCTV offline | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 18:45:00 | Pass | Unit 1 EC14 camera has failed, powersupply located in Unit 1, strong burnt smell coming from PSU, removed and replaced with 48vdc PSU from seme Stock
MSA-DCS | WA3454589 | Microwave H 3 tamper | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 18:42:00 | Pass | replaced resistors as reading 7k when closed.resistors now showing correct value, adjusted microswitch and confirmed alarm has cleared in control
MSA-DCS | WA3454591 | EC8 controller offline | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 18:00:00 | Pass | GBUS offline, recalled to all expanders and checked controller and all cleared. Alarms stored in controller
MSA-DCS | WA3454592 | Gate controller off line | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 18:43:00 | Pass | Gallagher controller failed in gatehouse causing door not to work,attempted to factory reset and bring back online, controller flashing 8 times indicating fault and will not reset.replaced controller from PFM stock and programmed.tested door function and confrimed correct operation
MSA-DCS | WA3454593 | Court services Door no securing | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-16 15:00:00 | Pass | Court services door not securing, reprogrammed door latching times, all programmed and tested ok. Job complete
MSA-DCS | WA3454594 | Cell call has network error | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 15:30:00 | Pass | Travelled to site, attended site and checked system logs. All had checked ok however may have been a possible power surge such cause system to lose its file , reloaded ACM file from system software. All restored and tested working ok. Job complete
MSA-DCS | WA3454596 | Programs P/A fault | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-16 12:00:00 | Pass | Programmed PA fault, found to be faulty microphone, replaced with new redback microphone, 1 x site stock used. All tested and working ok. In complete
MSA-DCS | WA3454598 | Camera 126 rolling black screen | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-16 11:59:00 | Pass | Checked camera image before modem. Image clear.Replaced S700 RST1 from PFM stock.Camera image clear in control
MSA-DCS | WA3454601 | Camera 213 distorted | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-16 11:56:00 | Pass | Removed camera and replaced BNC connection on camera,adjusted camera view and focused
MSA-DCS | WA3454602 | Zone 23 N/W | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 18:46:00 | Pass | Travelled to site, MW in constant alarm, checked microwave and found MW not aligned, readjusted brackets holding microwave and aligned.checekd activation with control, confirmed zone 23 MW alarming and securing.
MSA-DCS | WA3454605 | Under vehicle camera not working | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 18:51:00 | Pass | No image from license plate camera,Re-terminated BNC in control room, camera working,Still not showing, tested Cat5 cable between controller and PC, faulty cores.Re-terminated RJ45 plug on both ends, system operational
MSA-DCS | WA3454611 | Kitchen/office/ back room - ants | Killara - Victoria Pk (Metro Youth Bail) | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 15:00:00 | Pass | Treated ants in Kithea area at Kilara Metro youth bail centre.
MSA-DCS | WA3454624 | Gatehouse - keywatcher the time is out of sync | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-15 11:30:00 | Pass | Fixed issue with keywatcher
MSA-DCS | WA3454625 | Entrance door - please fix the glass front door as it is banging closed and | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 15:44:07 | 2020-07-15 10:00:00 | Pass | Attended site and carried out repairs to the hydraulic door closer on the front entry doors.
MSA-DFES | WA3453762 | Ground floor - Steel undercross gate failed to close overnight | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 14 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-29 16:30:00 | Fail | Technician attended the site of Cockburn Emergency Services Centre ground floor steel gate on 14/07/2020.Following full test and inspection of gate components identified fault was the found PE beam out of alignment, mountings were broken, perished & screws stripped, realigned PE beam & detailed for replacement16/07/2020. Attended site to replace faulty PE beams, however the PE beams supplied were the wrong type, a single reflector PE beam is what is required and got supplied a transmitter receiver set.29/07/2020. Removed existing faulty reflective replaced it with a Grifco safety beam.Full test and inspection of gate components completed prior to leaving site.
MSA-DFES | WA3454067 | Tunic Room- Fan not working, sensor not working | CFRS Armadale | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-28 14:00:00 | Fail | Arrived on site and signed in at 1300 to repair pressure fan motion fan in tunic room. Tested and set for 10min run time. Informed staff and signed out at 1400.
MSA-DFES | WA3454158 | Kitchen Area (15) Kitchen cabinet door hinges are loose | CFRS Perth | GMP-BR | Carpentry | Materials (CA) | AWB Co. | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-21 12:00:00 | Pass | Attended site to tighten cupboard doors - BRAF Submitted, but declined, closing off
MSA-DFES | WA3454485 | Air Con unit - Boiler has failed | DFES Cockburn Emergency Services Complex | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 10:00:00 | Pass | Attend site. Found boiler not working. Reset boiler from BMS but wont reset. Further inspection found the pilot light to have blown out. Carry out manual reset on boiler and found pilot light to start and boiler start. Monitor operation, working ok.
MSA-DFES | WA3454534 | Tracks on Northern sliding door to PPC storage area require repair | CFRS Perth | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-21 13:00:00 | Pass | Sliding door slider rails silicone sprayed and tightened loose bolts.
MSA-DFES | WA3454554 | 3 x Outside Lights not working | Armadale Regional Office | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 16:30:00 | Pass | Locate faulty lights. Turn on the overrides on at the board and all of the outside lights are working. Found a timer at the switchboard not working. Left site to get a new timer. Replaced faulty timer with new. Test and it is now working correctly. Advised staff of work completed.
MSA-DFES | WA3454562 | Lvl 2- Toilet is coming away from the wall, needs to be refastened | Success Career Fire Station (Temp Site) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 13:00:00 | Pass | Screws coming loose screwed back to the wall and working properly
MSA-DFES | WA3454572 | Tunic room - Roof leak above the fan sensor | CFRS Armadale | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 09:00:00 | Pass | Replaced broken tile above roof leak
MSA-DTAG | WA3453752 | Hay St entrance during the after hours timeframe,door is delayed in closing longer than it should be | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 14 Jul 2020 | 2020-07-14 17:00:00 | 2020-07-14 11:00:00 | Pass | Checked Hay Street entrance door after hours. Pacom system working all good and opening door.
MSA-DTAG | WA3454523 | Main Entry- Light not working | Rockingham Justice Complex | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 08:45:00 | Pass | Replaced faulty fitting to main entry and tested working
MSA-DTAG | WA3454531 | Family Violence Service – alarm/sensor #17 regularly goes into alarm state | Rockingham Justice Complex | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-24 13:00:00 | Fail | replaced faulty sensor
MSA-DTWD | WA3453877 | C Block, Room CG40- Leak in roof, see further notes below | Mandurah Campus (formerly Peel) | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-08-20 11:30:00 | Fail | Repaired leak and replaced water stained ceiling panel with new
MSA-DTWD | WA3453930 | G block, G122 - water leaking from ceiling in G122 | Midland Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 09:45:00 | Pass | Found box gutter blocked and full of water, removed debris. Found sheets rusted out around fixing points - Site requested silicone repairs - carried out.
MSA-DTWD | WA3453999 | Q Block, Q001.1 (Main corridor crossroads)- Roof/ceiling leaking | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-21 14:45:00 | Fail | Measured up for skylight replacement attended site with materials, removed 2x weathered skylights, cleaned laps and installed new sheets & screws
MSA-DTWD | WA3454030 | Building 7, ground, kitchen staff toilet - Cistern leaking | Thornlie Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-15 18:09:00 | Pass | Replace toilet cistern
MSA-DTWD | WA3454031 | R Block, R014 (Corridor)- Roof/ceiling leaking | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 14:00:00 | Pass | R014 Corridor - staining to ceiling - checked box gutter and roof sheeting - insulation was dry. Sealed window and flashing above area
MSA-DTWD | WA3454051 | External between C & D blocks- Pole lights not working | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-09-11 12:37:00 | Fail | BRAF declined, invoice costs to date
MSA-DTWD | WA3454055 | external between E & P Block - Security lighting not working | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-29 03:30:00 | Fail | Attended site and signed in. Located stairs at maintenance office. Found light not turning on. Tested pe cell and power is working. Replaced tube and starter and tested all to be working. Other part of job is on BRAF. Job complete
MSA-DTWD | WA3454114 | M Block , M001/Zone4- Fire panel in fault (Zone 4 Smoke Fault) | Balga Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 08:30:00 | Pass | Attended site to investigate fault in building m. Fault had been reset the previous day so unable to electrically test for issue. Had a visual look in area as i know there have been previous water issues. Will inform client.
MSA-DTWD | WA3454140 | Plant Room- Chiller Plant Room- Cooling towers waste water running on | East Perth Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 14:20:00 | Pass | Attended site and found cooling towers overflowing.Found tower 1 float valve filling and tower 2 overflowing but not making up.Suspect tower 2 is slightly lower than tower 1 which is causing the water level on tower 2 to overflow due to the balance line between the towers.Reset the water level valves.Drained towers and filled to confirm water levels.Found water levels ok.Will check on next maintenance,
MSA-DTWD | WA3454160 | Lvl 2, Staff Male Toilet - Loose tap | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-17 08:04:00 | Pass | Replace taps Replace plug and waste Fix leaking trap
MSA-DTWD | WA3454167 | F Block, Main entry auto door malfunctioning | Rockingham Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-14 13:39:00 | Pass | Found safety sensors intermittently staying on causing door to stay open, cleaned activation and safety sensors and checked over door, reset and tested all ok
MSA-DTWD | WA3454181 | E block- Alarm panel indicating that "Rear Landing Door" not secure | Joondalup Kendrew Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-14 13:30:00 | Pass | Login Gallagher workstation. Run check alarm reports E Block. Locate building and area, remove and install new PIR Zone 11 System 3836. All ok
MSA-DTWD | WA3454197 | T & W Blocks disabled male and female toilets lights are not working | Munster Campus (ACEPT) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-08-10 11:00:00 | Fail | Attended site and signed in. Located all toilets needing lights. Removed old lights and replaced with led panel downlights. Tested all okay. Job complete
MSA-DTWD | WA3454204 | Library - Rotate lenses on exit signs to show correct direction | Perth Campus B2 | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 10:30:00 | Pass | Inspected and flipped over exit signs to face the correct way as directed by site.
MSA-DTWD | WA3454298 | T Block - T024 mail room next to customer service -Hinged Glass door dropped and catching on floor | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-08-10 08:28:00 | Fail | Attended site and attempted to carry out repairs to frameless entrance door,while carrying out works we have noticed that new parts are requiredto repair the doors properly (Charging for this part only as quoted as below works were not authorized)Carried out the following repairs :Removed & re-installed frameless entrance doorSupplied and installed new custom countersunk screws to floor closer Door left in best possible working condition
MSA-DTWD | WA3454423 | A Block, Room A316- Tap requires fixing fume hood | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 11:40:00 | Pass | COMPLETED
MSA-DTWD | WA3454481 | C block, ground, Foyer - Fire panel fault | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 14 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-14 14:31:00 | Pass | Call Out, Fault on FIRE PANEL red box that connects to DFES Reset red box to DFES FAULT CLEARED.
MSA-DTWD | WA3454558 | External, closest to Gate, External, car park 12 - Blocked roadway sump drain | Balga Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | High Tech Maintenance | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-24 08:15:00 | Fail | Reported aid blocked road sumps at Balga TAFE - Contractors attempted to unblock, however the drainage pipes are root bound. Contractors cleared as best they could
MSA-DTWD | WA3454583 | R BLOCK, R021/R023 (West side of building) - Timer wiring faulty (A/C) wired to lighting circuit | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 14 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-20 15:45:00 | Fail | Attended site and signed in. Located classrooms and investigated air con issues. Tested and found switches working. Tested out contactors and found to be working. Tested switch cabling to aircon and found no power. Re terminated switch cabling and tested. Air con switches on and off with control inside. Still a condenser issue for precise to repair. Left isolated. Notified staff. Job complete
MSA-MRWA | WA3454639 | Please supply 10 keys of E004 X2 – 97 (Blue Keys) | Materials Engineering Branch | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 14 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-17 13:00:00 | Pass | supply and deliver 10x E004, X2 (Blue) keys
MSA-MRWA | WA3454672 | UPS in software bypass, please attend | Road Network Operation Centre (RNOC)-Server Room | GMP-BR | ICT/Audiovisual | Hardware / Equipment (AV) | Vertiv (Australia) | 0 | CLOSE | 14 Jul 2020 | 2020-07-14 22:37:52 | 2020-07-14 23:00:00 | Fail | ATTENDED SITE TO AN AFTERHOURS CALL OUTDUE TO UPS IN SOFTWARE BYPASS
MSA-DCA | WA3458868 | Multiple BMS alarms after power failure | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 15 Jul 2020 | 2020-07-15 17:00:00 | 2020-07-15 15:00:00 | Pass | Site experienced multiple power outages over the morning. Reset plant in alarm. Pneumatic Air Station, Steam Boilers, Stand alone Air Station, BMS alarms. FCU 8 fan fail alarm. Investigated. VSD tripped on overcurrent fault. Inspected SAF. Metered windings, checked mounting, rotation, bearings. Checked out ok. Reset VSD fault. Monitored system. Alarms cleared. Closed job.
MSA-DCA | WA3460941 | generator is going off line fuse has blown | Art Gallery of WA - James St-Main Building (Block B)-Level 5 - Roof | GMP-BR | Equipment Hire | Compressors, Generators (EH) | Techworks Electrical | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 15:51:00 | Pass | Test generator and rectify as requested
MSA-DCA | WA3461770 | water ingress into bar area from roof above - contractor on site | The Blue Room-Main Building-Level 1-Bar Area | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 17:00:00 | 2020-09-08 10:37:00 | Fail | Have applied silicone sealer to areas suspected to be the source of the leak Further works present access issues that will need to be resolved and works costed
MSA-DCA | WA3471549 | L1 Auto sensing lights intermittently operating | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Terrestrial Invertebrates Laboratory | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 14:00:00 | Pass | The laboratory had 3x sensors faulty, as well as being incorrectly wired, replaced 3x sensors with new and wired correctly.
MSA-DCS | WA3458651 | Front Gate, Pod- Short circut tampered, faults below | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 15 Jul 2020 | 2020-07-15 11:16:08 | 2020-07-15 10:00:00 | Pass | Supplied and replaced 16 in / 16 out Gallagher expander (HBUS). Reconnected and tested, ok.
MSA-DCS | WA3458654 | WWTP- dosing pump fault | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 2 | CLOSE | 15 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 15:20:00 | Pass | Arrived on-site and checked chlorination system for the WWTP. Both gas cylinders were empty from normal use. Empty cylinders were replaced with new full cylinders. Vacuum leak tested satisfactory. System left running in normal operation. Dosing at 540 g/h.
MSA-DCS | WA3458690 | New Cateen, Rear Storage Area- Roof leaking | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jul 2020 | 2020-07-17 17:00:00 | 2020-11-23 09:00:00 | Fail | SOURCE OF LEAKS LOCATED & REPAIRED
MSA-DCS | WA3458697 | Laundry, Number 2 wash machine- Door handle shaft faulty | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 2 | CLOSE | 15 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 11:30:00 | Pass | AMS655698 WA3458697 - Hakea - No 2 WM - Door handle broken. Found hinge pin broken on the door handle and catch latch loose. Tightened latch and repaired hinge at workshop. Refitted hinge. Also re sealed the door seal.
MSA-DCS | WA3458707 | Unit 5, Cell A9- Window is not securing in place when window is raised | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 13:30:00 | Pass | REPAIRED CELL WINDOW
MSA-DCS | WA3458713 | Unit 3, Day Room- Ceiling fan has come loose from ceiling | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 13:00:00 | Pass | Re-sat ceiling fan in unit 3 day room
MSA-DCS | WA3458745 | control camera's 172 and 91 are down-SEME on site | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-27 15:47:00 | Fail | Sourced POE injector.Investigated fault, repaired multiple camera faults and tested OKParts (SEME Service Stock)1 x POE InjectorJob Complete
MSA-DCS | WA3458749 | unit 6 main door entry reed switch perminently on open circuit setiing alarm off | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-15 15:00:00 | Pass | Tested the operation of the Electric strike and confirmed permanent alarm on door. Removed electric strike from door frame and tested operation. Found cable between door strike and Reed switch damaged bymovement of the strike in the door frame when door slammed shut. Cut away damaged cable and installed new end-offline Resistors in new cable. Tested and confirmed correct operation of door monitor.
MSA-DCS | WA3458781 | Camera issues as below | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 15 Jul 2020 | 2020-07-15 12:42:14 | 2020-07-15 13:30:00 | Fail | Attended site checked and found Camera 27 showing blank in control. Checked in EC cabinet found signal from camera is ok. Located the problem to be the Fiber modem in EC cabinet. Reboot Fiber modem and tested it ok. Checked camera 152,153,154&155 video delay in ISU. Reboot CCTV workstation and tested all ok.
MSA-DCS | WA3458801 | L3 bank of 5 lights out, checked power board and can see tripped switch | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 15:45:00 | Pass | Checked lighting on Level 3
MSA-DCS | WA3458807 | L3 lights globes blown across building | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 16:45:00 | Pass | Repaired lighting
MSA-DCS | WA3458817 | House 13, Room 2- Light not working | Boronia Pre-release-AP21 - Prisoner Accommodation House 12 and 13-Ground Floor-House 13 - Bathroom 2 | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 12:00:00 | Pass | Changed lights in house 13
MSA-DCS | WA3458843 | Unit 5, Cell A13 - lighting issues as below | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-16 10:00:00 | Pass | Repaired faulty lights in unit 5 a13
MSA-DCS | WA3458901 | Unit 1, A2 & A10 - cell call light remains on | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 09:32:43 | 2020-07-17 08:00:00 | Fail | Fault not evedint on cell calls tested cell calls to unit control, cell call units operated correctly, Call LED did not stay on for any of the tests conducted.
MSA-DCS | WA3458914 | Unit 2 A7 - blocked no sound can be heard & B8 - can not be heard | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 09:37:47 | 2020-07-17 10:30:00 | Fail | Removed cell call units (2) from bed heads, relocatedto Officer Station. Stripped down cell call units, cleaned out toothpaste, reassembled and returned to cells. Tested cell calls to local control, good audio both ways, reinstalled in bed ends.
MSA-DCS | WA3458928 | unit 2B pod 3 wall heater not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-30 13:00:00 | Fail | Replaced wall heater
MSA-DCS | WA3459155 | Serpentine - powers out in various parts of the unit | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-08-03 15:00:00 | Fail | Instal temporary link to restore power, removed once control issue was fixed
MSA-DCS | WA3459209 | ISU D3 - readling light switch has been pushed in | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 15:30:00 | Pass | Replaced damaged switch
MSA-DCS | WA3459278 | ISU D3 - toilet leaking | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 15:38:00 | Pass | Relaced solenoid valve
MSA-DCS | WA3459789 | Unit 14 - A7 Night light at top bunk bed is not working, | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 11:30:00 | Pass | Repaired faulty lights in unit 14 a7. Used workshop site stock for replacement ballast
MSA-DCS | WA3459795 | Unit 14 - A12 2nd power point cracked needs new corner. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 08:30:00 | Pass | Replaced damaged cell gpo and blank plate in unit 14 a12
MSA-DCS | WA3459964 | Education room 4 & room 4 door and the lock on the gate faulty-see notes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-09-10 13:15:00 | Fail | Service lock, replace bolt throw and lever pack on room 4.Replace lock on gate, cut out gate to suit new lock.
MSA-DCS | WA3460836 | Main control room - fire panel has 7 abnormal points reporting | Casuarina Prison | SPA-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 10:19:17 | 2020-09-07 12:09:00 | Fail | 16/07/20 EI/GAAttended site & inspected POD graphicsGraphics is reporting 129 faults & 5 x isolations.18 x faults relate to node 3-Industries FIP due to building works. Generator room no detection due to Recovery Maintence under building works.59 x faults relate to node 11-Reception FIP due to building works. Visits area is under building works.49 x faults relate to node 12-Infirmary FIP due to building works. Infirmary area is under building works.Unit 13 fault related to the VESDA in unit 13 AC Wing cell 13/14 is reporting low flow in pipe 1.Sample point & pipe is clean & clear suspect faulty flow sensor. Performed a smoke test & verified that the VESDA is working.Recommend replacement of VLS VESDA (7 relay type).Unit 2 FIP on inspection is displaying a normal status. However the POD graphics is reporting a battery low/disconnect fault.Consultation with manufacturer & further investigation required.Unit 4 FIP on inspection is displaying a normal status. However the
MSA-DCS | WA3461285 | Unit 1 hut toilets toilets completely blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 12:00:00 | Pass | Clear blocked drain in unit one using drain machine.
MSA-DCS | WA3461367 | kitchen lunch room urn not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-17 11:00:00 | Pass | Supply and install new rheem mini boil in dining room (kitchen)
MSA-DCS | WA3461385 | Unit 2 top landing showers missing taps and heads | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 13:30:00 | Pass | Supply and install new shower wall taps and new shower roses to middle landing unit 2. (X2)
MSA-DCS | WA3461391 | kitchen lunchroom salad bar exposed wires | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-16 12:00:00 | Pass | Investigate and repair damaged wiring on lunch room salad bar
MSA-DCS | WA3461396 | west side chapel Roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2021-04-08 09:00:00 | Fail | REPAIRS TO BOX GUTTERS CARRIED OUT
MSA-DCS | WA3461403 | Unit 14 B/D wing commons kitchen water damage to floor behind fridge | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-10-23 14:00:00 | Fail | THIS JOB IS A DOUBLE UP - WORK COMPLETED ON WA3123957
MSA-DCS | WA3461409 | Unit 14 - A3 leaky shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 08:30:00 | Pass | Replaced leaking spindle in tap
MSA-DCS | WA3461427 | Unit 3 - A4 Window does not stay open in cell | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 12:15:00 | Pass | REPAIRED CELL WINDOW
MSA-DCS | WA3461439 | Administration - Lobby Area doors require servicing ,doors and locks are not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2021-01-30 16:00:00 | Fail | Service locks, replace bolt throws and lever packs.2 person attend, remove doors and floor closers, install cement new closer box into ground, replace pivot and re install doors.
MSA-DCS | WA3461445 | Unit 1 - A9 needs window vent and wall vent repairing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-09-01 12:30:00 | Fail | VENTS REPAIRED
MSA-DCS | WA3464218 | Kitchen - billi unit is showing error message - filter change x 7 | Maddington (South East Metro) | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 09:30:00 | Pass | CHECKED UNIT FILTER REQUIRED REPLACEMENT SERVICED.RAN CHECKED SETTINGS
MSA-DCS | WA3465272 | main kitchen oven is not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 12:22:15 | 2020-07-16 15:30:00 | Fail | Replaced Fan motor also correct polarity of external water filter one-way valve that was incorrect direction & stopping water flow.
MSA-DCS | WA3465389 | Level 4 - new water system has a fault - keeps running or nothing. | East Perth | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 12:32:08 | 2020-07-15 14:40:00 | Pass | Warranty call lodged with Zip by W2W
MSA-DCS | WA3465403 | Jasper C - exterior light broken | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-23 11:00:00 | Fail | Repaired jasper external light
MSA-DCS | WA3465404 | Turner B02 - inside light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-23 09:30:00 | Fail | Replanted light
MSA-DCS | WA3465406 | Turner B03 - Ariel socket broken | Banksia Hill Detention Centre | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Sapio Pty Ltd | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 10:30:00 | Pass | Attended site. Found socket was damaged. Replaced socket. TV signal tested OK.Job completed.
MSA-DCS | WA3465409 | Murchison - Leaking tap to office | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 15:45:00 | Pass | Reashed kithcen taps
MSA-DCS | WA3465412 | Jasper b & C - holes in ceiling | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-08-07 12:50:00 | Fail | HOLES IN CEILING PATCHED & PAINTED
MSA-DCS | WA3465415 | Lenard, B & C - holes in ceiling | Banksia Hill Detention Centre | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-08-07 12:50:00 | Fail | HOLES PATCHED & PAINTED
MSA-DCS | WA3467696 | U7 G wing shower leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 08:56:00 | Pass | Turned off hwu in control room to replace tap washer in hot tap only in 1st cubicle
MSA-DCS | WA3467856 | Unit S5 tap leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 09:47:00 | Pass | Turned off water to cell removing tap on pillar tap to replace tap washer and valve and reseated then reinstalled and turned water back on
MSA-DCS | WA3468023 | Unit 7 S9 Flush button not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 10:38:00 | Pass | Water continue to run throw toilet, turned off water pulled apart cistern replacing out outlet washer then reinstalled and turned water back on flush button working fine
MSA-DCS | WA3468240 | Unit 8 D wing Shower LHS leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-27 08:19:00 | Fail | Once at unit waited to go down wing to located dripping tap on LHS shower hot tap only went to turn off hwu but could not gain access to service duck as door lock was broken my escort reported to maintance so will wait to be advised to go back and fixlocks fixed able to Turned off water replacing hot tap only turn water back on
MSA-DCS | WA3468526 | Unit 2 cell 70 lock is not working-see notes | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 15:12:00 | Pass | Attended site, rekeyed lock to suit system keys onsite.Date on site: 17/07/2020Time on site: 01:00pm - 03:15pm
MSA-DCS | WA3469284 | U10 staff room Tombstones disintegrated possible new light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-16 14:30:00 | Pass | Replaced damaged tombstones
MSA-DCS | WA3471470 | staff room - exit sign over the main door has been knocked down | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Emergency & Exit Lighting (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-17 14:00:00 | Pass | Re mount exit light
MSA-DFES | WA3458886 | Ground level, eAcademy, change room 2 - full size lockers 69 & 70 broken rods & can not be locked | FESA RHQ - Forrestfield | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 10:25:00 | Pass | Repair to locks for lockers 69 & 70
MSA-DFES | WA3465424 | Lost communication to FIP | CFRS Duncraig | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 14:00:00 | Pass | Spoke with fire fighters regarding codered fault. Telstra outage. Reset FIT & ASE. Communicating.
MSA-DTAG | WA3461373 | ground public toilet Ceiling extractor has failed in male public toilet | Perth Children's Court | GMP-BR-HO | Electrical | General Electrical (EL) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-08-05 16:00:00 | Fail | Completed service works, two (2) new motors fitted to TEF.8 - Public toilet extration system, recommissioned, all working correctly.
MSA-DTAG | WA3464456 | L5 Female disabled public toilet blocked located outside crt 52 | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-16 11:15:00 | Pass | Complete
MSA-DTAG | WA3742619 | RETROSPECTIVE WORK ORDER Courts cameras offline - ATT 15/7/20 | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 15 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-15 10:30:00 | Pass | job completed - Attended site. Mirvac Security have no cameras on Courts. Mirvac Office has no 240V power to PC.Electrician required
MSA-DTWD | WA3458771 | Lvl 1, Foyer - Damaged light fitting | Perth Campus B4 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 13:30:00 | Pass | Job complete
MSA-DTWD | WA3458804 | Lvl 1, A151, bottom of staircase- Damaged light fitting | Perth Campus B4 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 15:30:00 | Pass | Job complete
MSA-DTWD | WA3458845 | Level 1 & 2 - Mutiple lights are faulty (see notes for location) | Perth Campus B5 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 16:15:00 | Pass | Job complete
MSA-DTWD | WA3459153 | C block ground east foyer Glass appears to have dropped or been tampered with in auto door | Mandurah Campus (formerly Peel) | GMP-BR | Building | Automatic Doors (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 15 Jul 2020 | 2020-07-16 17:00:00 | 2020-07-15 15:30:00 | Pass | Door glass wasn’t installed correctly had to deglaze door and set glass in correct position then rubber up again on both sides.
MSA-DTWD | WA3459291 | Outside BLD 851 Backflow device faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-15 16:00:00 | Pass | Supply & install 20mm RPZ device
MSA-DTWD | WA3459718 | G block Exhaust fan not working in Surgery Room-contractor on site | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-15 16:00:00 | Pass | Job completeAwaiting return of signature slips via email due to covid 19
MSA-DTWD | WA3461447 | BLD 822 A, Reception - Front lights faulty | Muresk Institute | GMP-BR | Electrical | Lighting, External (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 15 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-16 09:15:00 | Pass | Replaced ballast and lamps
MSA-DTWD | WA3471530 | L1 mail room Re install fallen mail frame | Perth Campus B1 | GMP-BR | Building | Internal Screens (BU) | AWB Co. | 3 | CLOSE | 15 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 09:30:00 | Pass | Liam Hanlon (22/07/2020) - Work NoteAttend site and get swipe pass Bring materials up from basement Measure up and cut existing bracket shelf from college Set and mark holes, scan walls and drill Fit bracket units to wall Remove rubbish and vacuum floors Sign out
MSA-DCA | WA3473920 | lift dropped below floor level and unresponsive-closes at 5pm | PICA-Main Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 16:15:00 | Pass | Work order to be closed off at $0
MSA-DCS | WA3473198 | Unit 6, Control and officers toilet - Vinyl needs reglueing | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jul 2020 | 2020-07-22 17:00:00 | 2021-01-06 13:30:00 | Fail | REPAIR VINYL SKIRTING
MSA-DCS | WA3473200 | Unit 7, PA System not connecting, see further info below | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 07:03:11 | 2020-07-16 10:30:00 | Pass | Attended site checked and found Unit 7 cell call intercom function is working ok. But PA can’t be heard in Wings. Further check located the problem on PA amplifier. Reboot PA amplifier and adjust the volume. Tested all ok after.
MSA-DCS | WA3473211 | Unit 9, Cells A15- Vinyl needs reglueing | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jul 2020 | 2020-07-22 17:00:00 | 2021-05-28 13:15:00 | Fail | damaged flooring lifted, sub floor prepped - new vinyl laid
MSA-DCS | WA3473261 | Unit 13 - A & C - Blocked shower drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 10:30:00 | Pass | Used acid and plunger and to clear blockage.
MSA-DCS | WA3473264 | MPU (8)- shower is not turning off, Currently shut off from the cupboard in the shower. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 20:00:00 | Pass | Replaced split pins in tap spindles.
MSA-DCS | WA3473266 | Amenities, Female showers- no hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 08:30:00 | Pass | Investigated cause of no hot water. No power to units. Switch board found and power reset. Hot water temp tested and ok.
MSA-DCS | WA3473268 | Unit 1, C Wing, Cell C8- Main window has crack in it | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-17 14:30:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3473384 | Unit 2 cell D81 light switch faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-20 13:30:00 | Pass | Investigate and replace unit 2 cell 81 light switch
MSA-DCS | WA3473396 | Front gate fire board faulting | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 08:54:13 | 2020-07-16 11:45:00 | Pass | faulty plus on brigade board - re-terminated and all ok
MSA-DCS | WA3473492 | Unit 13, Boiler Room- Bad water leak on flange | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 09:30:00 | Pass | Replaced damaged, leaking gasket on hot water pipework
MSA-DCS | WA3473495 | Unit 13, Boiler vibrating badly | Casuarina Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 0 | CLOSE | 16 Jul 2020 | 2020-07-16 13:43:28 | 2020-07-16 15:30:00 | Fail | Job completed - no completion notes
MSA-DCS | WA3473500 | Unit 4, A Wing bathroom sink leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-20 11:30:00 | Pass | Retightened all loose nuts on trap below basin.
MSA-DCS | WA3473555 | Bakery- Sensors not working to taps on th sinks at the rear of workshops | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-12 14:00:00 | Fail | 23/7/20 - Investigate. Test sensor plates. Sensors broken. Braf required to order and replace.12/8/20 - Collected parts offsite. Replaced sensor tap controllers with new ones. Ran new cables in wall cavity and installed new 12v power packs. Tested.
MSA-DCS | WA3473559 | Unit 14, B Wing- Hole in the wall in cleaning cupboard | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-18 15:00:00 | Fail | WALL HOLE PATCHED/REPAIRED
MSA-DCS | WA3473564 | Front Gate, electronic lock on grill into prison & front door into gate are not releasing | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 10:33:04 | 2020-07-16 15:45:00 | Pass | Front door into the gatehouse has mis aligned door from structure frame causing custodial lock sensor to show open to the gallagher system even the door is closed, advice SO with to the problem. Grill door into the prison faulty and doesn’t open custodial lock, dismantle, clean and lubricate. Test ok and back to normal operation.
MSA-DCS | WA3473577 | Offical Visits Doors- One lock is sticky. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-20 11:30:00 | Fail | Service lock Require parts.Replace lock, bolt throw and lever pack keyed to site keys.
MSA-DCS | WA3473626 | Front of vehicle gate - Bollard wont lower | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 0 | CLOSE | 16 Jul 2020 | 2020-07-16 15:11:09 | 2020-08-26 08:00:00 | Fail | 16/07/20Inspected bollard.Removed covers to locate problem.Spray lube locks and switch.Had to break seized chain to lower bollard.Requires further attention to replace chain.26/08/20Replaced rivets to base of bollard.Mode set use manually
MSA-DCS | WA3473629 | gate house OMNI trax coms fault | Greenough Regional Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 11:16:18 | 2020-07-31 13:25:00 | Fail | Investigated omnitrax communication issues. Faults indicated a break in cables around zones 8 and 9 causing power and comms faults. Excavated cables and found contractors had trenched through cables and taped them together with electrical tape.Repaired cabled, reterminated, tested, back filled excavation, calibrated and walk tested ok. Data and power status are now normal.Parts:ConsumablesSenstar connectors x 8SC2 CableJob Complete
MSA-DCS | WA3473642 | Outside industries day room - Grease/Soap Pit to be cleaned out | Casuarina Prison | GMP-BR- HO | Waste Management | Waste Removal (WM) | Western Resource Recovery Pty Ltd | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-04 12:25:00 | Fail | completed 28.07.202
MSA-DCS | WA3473656 | Video link, fire alarm "Z41 CONV" fault | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 11:35:45 | 2020-07-16 13:43:00 | Pass | replaced 3 detectors in fault
MSA-DCS | WA3473704 | unit 4, K5, Cell call Tamper fault | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-21 10:30:00 | Pass | Cell call fault caused by water ingress. Intercom to be replaced once construction has finished. Security Officer LEE COFFEE asked if we could stop tamper alarms and accidental cell calls from coming through to the front gate as there are no prisoners in this area. We explained that U4 can be removed from programming and put back in at a later date. NODE 4 has been removed. All other Units/Nodes tested ok.
MSA-DCS | WA3473723 | Unit 5, A & C- Hot Water Urn not working, runs out of water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-28 12:50:00 | Fail | attended 22.7.2020 - captured asset diagnosed required non common spare a pcb board required - returned and fitted partRheem Boiling Water 25L Unit A40191328H
MSA-DCS | WA3473735 | Reception- Hot water urn not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 12:48:26 | 2020-07-17 09:23:00 | Pass | Replaced solenoid and cleaned level sensor.Recommend filters to be fitted.Wooroloo prison farm ReceptionA4033084E Rheem 5L BWUReplaced Solenoid and Cleaned Level SensorsRecommend Maxiflow scale filter as badly scalednot approved on day.
MSA-DCS | WA3473776 | Education 1, Class 5- Door 5B to class 5 not locking | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 09:15:00 | Pass | Supplied and fitted replacement for faulty mortise lock, and adjusted strike.
MSA-DCS | WA3473778 | Turner, Cell B06- Damaged viewing window | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 15:00:00 | Pass | RE-GLAZE OBS PANEL
MSA-DCS | WA3473781 | visits centre gas heater not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-07 10:00:00 | Fail | Replaced both gas heaters and commissioned
MSA-DCS | WA3473811 | WWTP air hose line faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-07 11:00:00 | Fail | Repaired faulty hose
MSA-DCS | WA3473839 | Unit 3 - Shower Block 1st and 2nd shower taps faulty in D wing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-20 16:00:00 | Pass | Replaced 2 x leaking spindles in shower taps
MSA-DCS | WA3473875 | Mechanical work shop broken switch | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-20 15:00:00 | Pass | Investigate and replace mechanical workshop light switch
MSA-DCS | WA3473901 | main kitchen brat pan hydrolic arm is faulty-contractor on site | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-27 14:35:00 | Fail | Replaced Lift Kit as quoted. Test Operation ok
MSA-DCS | WA3473916 | Cabinet Shop Dayroom Light Fitting Broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-21 13:00:00 | Pass | Repaired lights
MSA-DCS | WA3473944 | safe unable to unlock in medical center | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 16 Jul 2020 | 2020-07-16 21:17:15 | 2020-07-23 11:45:00 | Fail | replaced lock
MSA-DFES | WA3473597 | G.P.O has come away from the wall in firefighters’ study | CFRS Daglish | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-21 11:00:00 | Pass | Arrived at site to fix 2 GPOs in study. Isolated Added supports to both and re energised. Cleaned and tested. Done paperwork.
MSA-DFES | WA3473598 | Substantial water leak Gym ceiling centre join where gym was extended and rear south west corner | CFRS Daglish | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-22 08:45:00 | Fail | Returned back to site and siliconed up gaps if it happens again will return back for fearther investigation.
MSA-DFES | WA3473827 | Kitchen mixer tap loose and leaking | DFES Regional Office - Belmont | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-17 12:43:00 | Pass | Mixer tap in ware house was leaking from the spout and found flexy hoses starting to rust so replace with new mixer tap tested and working
MSA-DFES | WA3473833 | G Floor- BEB side gate is failing to lock & secure | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 15:00:00 | Pass | 16/7/20 - Ryan VestyChecked gate, found reader operating correctly and opening gate.Egress button not operating gate release though.Checked equipment and found a burn mark on the door controller. BRAF approved to replace door controller.Replaced and tested, all working ok.
MSA-DFES | WA3473937 | level 2, male ablutions - Ceiling Light out in rear cubical | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-21 08:35:00 | Pass | Complete
MSA-DFES | WA3473938 | level 2, Male ablutions - Hand basin slow to drain and broken release mechanism and | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-17 15:30:00 | Pass | Plug and waste on right hand side basin brocken replace with a new one tested and working
MSA-DTAG | WA3473515 | 1987 L1 Mclure J Former Office Rubber privacy seal is detached from the bottom of door-see notes | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-17 08:30:00 | Pass | DOOR SEAL RE ATTACHED
MSA-DTAG | WA3473542 | Basement - SMS custody is unable to communicate with server | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 08:35:00 | Pass | Checked Pacom server and found user rights corrupted. Ran server backup and copied GMS directory back C:\. Setup user rights and tested, all is ok.
MSA-DTAG | WA3473551 | Custody monitors have ceased working- see further info below | Joondalup Courthouse | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-16 13:00:00 | Pass | Attended site. Found cable supplying monitor without power. Cable goes into fixed ceiling roof and is inaccessible. Sitehad spare power supply for monitor, used this as replacement PSU.Job completed.
MSA-DTAG | WA3473558 | Magistrate 2 Chambers 2x lights . Lights in garage 1 & 2 also out -see notes | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-17 08:45:00 | Pass | Inspected faulty lighting and replaced faulty tubes + Resecured light hanging by wires. Lighting for garage is working but the issue is the sallyport in custody which needs upgrading - DAS submitted for this -
MSA-DTAG | WA3473891 | ground security office Key safe in Security Office is not locking | Armadale Courthouse | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 16:00:00 | Pass | Attended site, gained entry to locked keysafe. (Damaged electrical keypad) recommend replacement
MSA-DTAG | WA3473893 | Ground level - roof leak - Water drip in MYBS office from air vent, rear corner of office | Perth Children's Court | GMP-BR-HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-09-04 13:55:00 | Fail | MULTIPLE LEAKS IN MULTIPLE AREAS REPAIRED
MSA-DTWD | WA3473314 | T block gym T003 Electrical floor GPO box Broken-see notes | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 10:45:00 | Pass | Attended site and signed in. Located t003 gym room and floor gpo. Removed coverings from floor gpo, opened up bits and pieces inside that appear to be broken. Recovered all parts from bottom of floor box. Assembled latch springs, latch, slide and screws back to floor box. Refitted into ground. Tested all okay. Job complete
MSA-DTWD | WA3473458 | W block work shop 3 faulty emergency stop buttons | Munster Campus (ACEPT) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-09-29 15:30:00 | Fail | Attended site and signed in. Located w block workshop switchboard. Re identified all circuits needing to be on e stop. Isolated switchboard to building. Installed 4 x contactors and relay to internal of switchboard. Rewired circuit cabling from circuit breaker to connect to existing e stop control circuit. Re energise switchboard and test e stop and power. All of workshop tested isolated when e stop pressed. All okay. Job complete
MSA-DTWD | WA3473568 | E block E49 Office – 2 x Damaged Wall GPO’s | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 14:00:00 | Pass | Replaced broken mounting block and gpo in office , resecured pushed in data mechs, replaced faulty isolator switch in LSK. Job complete.
MSA-DTWD | WA3473853 | nth block L2 N229 water damaged tiles | Mount Lawley Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 12:15:00 | Pass | Liam Hanlon (22/07/2020) - Work NoteAttend site Locate room and inspect ceiling tilesLeft site to get materials Got materials from Ceiling supermarket Fine fissure tiles returned to site Set up and brought ladder to level 2 Removed damaged tiles Concrete plaster from soffit had fallen onto tiles Measure up Cut new tiles and bring upstairs and fit Clean up and remove rubbishTake rubbish back to office skip Small amount
MSA-DTWD | WA3473874 | A Block, Room A319- Check tripped power due to water leak | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 15:00:00 | Pass | Inspected power trip in A319, tested outlets close to where water leak is, all tests fine. Job complete.
MSA-DTWD | WA3473880 | A Block, Room A338- Broken barrels on grey storage cupboards | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-21 13:50:00 | Pass | replace 4x hafele cores on cabinet locks
MSA-DTWD | WA3473882 | L1 Museum Card reader not working | Perth Campus B7 | GMP-BR | Security | Access Control (SE) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 16 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-20 12:00:00 | Pass | Attended site and inspected faultFound that the Xenta controller and the LIU controller comms was not working. Restarted both theXenta and LIU controller. Suspect fault due to power interruption due to RCD testing. Replacedbattery as requested by site. Checked and confirmed controller function as well as confirmingbattery backup function.
MSA-DTWD | WA3473886 | G Block, main entry foyer - Roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 16 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 13:30:00 | Pass | Resolved leak - confirmed with Frank
MSA-DTWD | WA3473924 | E block, E23, female staff toilets - Floor drains overflowing with water | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-17 13:45:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3473940 | A BLOCK, cafe sliding door - it will not shut and can not be secured | Leederville Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 16 Jul 2020 | 2020-07-16 20:53:15 | 2020-07-24 13:59:00 | Fail | Arrived on site and found mode board options board and PIB board heavily corroded and also possible main controller faulty. Will also require a new mains lead to power supply as it has been damaged . Cable tied door closed requires quotation. Braf has been approved.Returned to site and replaced mode board, options board and 301 controller. Fitted new power cord. Tested, all ok.
MSA-MRWA | WA3473465 | General Floor - Multiple LED panels/strip lighting not working, please remediate | Don Aitken Centre MRWA Head Office-Main Building-Second Floor | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-21 08:15:00 | Fail | Attended site and replaced 3x faulty led drivers in meeting room 2102. All lights are now working. 3 led drivers left as spare
MSA-MRWA | WA3473475 | floor 7, Kitchenettte - Switch Mech failed please remediate | Don Aitken Centre MRWA Head Office-Main Building-Seventh Floor | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 16 Jul 2020 | 2020-07-17 17:00:00 | 2020-07-16 12:45:00 | Pass | Replaced 2x faulty light switch in kitchen level 7.
MSA-DCA | WA3488454 | White phase 10 to be metre after power spike | Perth Cultural Centre Precinct-Fiji Room-Ground Floor-Server Room | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 11:00:00 | Pass | Circuit tested and has failed IR tests, Out of service tag has been left on and isolated.
MSA-DCA | WA3488751 | ground floor stage - No Water coming from stage sink | His Majesty's Theatre-Theatre Building-Ground Floor-Stage Area | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 12:02:00 | Pass | Located main water supply valve was turned off because water leak off meter underground have let Matt know and will need to raise work order to repair
MSA-DCA | WA3488762 | Level 2, female toilets - toilet not flushing, (first cubical on the right) | His Majesty's Theatre-Theatre Building-Level 2-Female Change and Toilets | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 13:20:00 | Pass | Removed old broken cistern replaced with new
MSA-DCS | WA3488191 | Staff accommodation, Kitchen- Tap hardware is damaged | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-20 10:30:00 | Pass | Supply and install new kitchen sink taps to staff accomodation. ( 1x pair wall top assembly- truck stock)
MSA-DCS | WA3488229 | Video in Interview Room 1 is not working. | Broome Regional Prison-Gatehouse Administration | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-31 03:44:00 | Fail | Removed faulty camera, used cable as draw wire, Getting stuck in roof. Removed roof sheets, located cable .Cable installed and terminated.Camera installed and programmed indigo BX420
MSA-DCS | WA3488230 | PTZ in male exercise yard needs replacing | Broome Regional Prison-Gatehouse Administration | SPA-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-31 10:25:00 | Fail | Programmed camera and confirmed correct operation of PTZ.Have left old camera on system as recordings may be needed. Can delete 1/9/2020
MSA-DCS | WA3488233 | Security yard fan for security cupboard for comms is not working. | Broome Regional Prison-Gatehouse Administration | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Jul 2020 | 2020-07-23 17:00:00 | 2020-09-03 01:55:00 | Fail | Removed faulty 1RU fan.installed new 1RU rack mount fan.
MSA-DCS | WA3488242 | Zone 9- Alarm is constantly activating and wont reset | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 07:34:33 | 2020-07-17 10:30:00 | Pass | Found zone 9 in constant alarm, found 1Mohm at first join , found contaminated section of cable at join, replaced connection and sealed existing splice kit. Tested 1Mohm at controller. Tested fence operating correctly.(If zone 9 fails again the cable between EC cabinet and fence may require replacement).
MSA-DCS | WA3488245 | Kitchen, Freezer temp is high, (currently minus 7) | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Main Kitchen | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 07:38:56 | 2020-07-22 11:09:00 | Fail | BRA declined invoicing costs to date.
MSA-DCS | WA3488255 | Unit 2, Cell D10- Cell window cracked | Hakea Prison-Unit 2 | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 17 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-21 15:00:00 | Pass | CELL WINDOW REGLAZED
MSA-DCS | WA3488261 | Unit 2 - Computor Room There appears to be a leak on a flange in the plantroom next to Calorifier | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-24 08:30:00 | Fail | Investigate leak. Collect rubber offsite. Make and install new rubber gaskets.
MSA-DCS | WA3488262 | Unit 7, Staff toilet in control room- water leaking from ventilation duct | Hakea Prison-Unit 2 | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 17 Jul 2020 | 2020-07-21 17:00:00 | 2021-04-08 09:00:00 | Fail | NEW FLASHING INSTALLED AROUND VENTILATION DUCT & OTHER AREAS OF PENETRATION SEALED
MSA-DCS | WA3488264 | Unit 4 B2 Viewing Window Smashed | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 07:59:41 | 2020-07-17 13:00:00 | Pass | VIEWING WINDOW REPLACED
MSA-DCS | WA3488271 | Front door will not open | Mandurah | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 0 | CLOSE | 17 Jul 2020 | 2020-07-17 12:02:38 | 2020-07-20 13:00:00 | Fail | Attended site and repaired lock, lock in working order but client advised they would like the lock to be changed out. Trade has left site to source new lock to return to site and replace.
MSA-DCS | WA3488273 | Unit 3 control room Roof Leak In Control Room | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-11-18 14:00:00 | Fail | REPAIRS TO ROOF TO STOP LEAKING
MSA-DCS | WA3488274 | Education Centre, photo copier room- Water leak in ceiling | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2021-03-15 09:00:00 | Fail | INVESTIGATED SOURCE OF LEAK, REPAIRED SARKING & SEALED POSSIBLE PENETRATION POINTS
MSA-DCS | WA3488276 | Front Gate, kitchen- Water leak in ceiling | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-11-26 14:53:00 | Fail | REPAIRED ROOFING TO STOP THE LEAK
MSA-DCS | WA3488278 | Unit 7 - C12 Shower head leaking at wall joint | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-20 13:00:00 | Pass | Replaced leaking spindle in shower.
MSA-DCS | WA3488347 | Unit 7, Cell A5- Window wont stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 09:15:00 | Pass | REPLACE SPIRAL BALANCES & WINDOW FEET
MSA-DCS | WA3488402 | Grounds, Visitors Carpark- termites in tree, see further info below | Boronia Pre-release-External Area-Ground Floor-Visitor Car Park | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 13:48:00 | Pass | Drilled tree , injected with 100L Termidor emulsion & corked.
MSA-DCS | WA3488439 | control fire panel sub fit living unit 10 and unit 7 vesda | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 10:00:46 | 2020-07-17 11:39:00 | Pass | 17/7/20 JN CMUnit 10 faultChecked unit 10 zone termination in conventional card at main gatehouse panel, 27vdc from board output and 3.3k EOL to unit 10, all normal.Reterminated and fault cleared, likely loose connection.Unit 7Went to unit 7 to check vesda, E, F, S Wong vesda isolated since 7am this morning causing conventional fault. Deisolated vesda, all faultscleared panel normal.
MSA-DCS | WA3488446 | Unit 4, D9 - door dragging on vinyl, hinges need attention. Creating problems with the locks | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 10:30:00 | Pass | Replace hinges, fixings and adjust strike
MSA-DCS | WA3488506 | Gate house - unable to download video pictures from the computer | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-17 13:00:00 | Pass | Confirmed video still recording from all cameras on site. Refer to log for fault details.
MSA-DCS | WA3488511 | Zone 9 & Zone 6 - omni trax, constantly alarming | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 10:54:33 | 2020-07-23 11:30:00 | Fail | Rectified and fixed Omnitrax z6 and Z9, tested ok and working. Job completed.
MSA-DCS | WA3488512 | Zone 2, IM cable, cable is damaged | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 10:57:58 | 2020-07-20 14:30:00 | Fail | Rectified and fixed microphonics cable internal zone 2, job completed.
MSA-DCS | WA3488514 | Zone 14, Mircowave constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 10:58:47 | 2020-07-20 14:30:00 | Fail | Microwave power and alignment tested ok. Reset receiver and transmitter units. Cable from microwave to Senstar tested ok. Traced fault to issue with input on the Omnitrax module. Fault with Senstar input repaired. Zone tested ok.Invoice raised for costs to date
MSA-DCS | WA3488515 | Zone 3, Zone 7, Zone 11- outer mircophonics constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 10:59:41 | 2020-07-22 12:30:00 | Fail | Rectified and fixed damage cable, replaced damage splice kit, fixed loose MX cable along the fence, tested ok. Job completed
MSA-DCS | WA3488525 | Corner of zone 9 & 10, Zone 3 & 4 top half, fencing is broken and hanging down | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 11:00:43 | 2020-07-21 16:30:00 | Fail | Remove microphonics cables that hanging along the top fence, job completed.
MSA-DCS | WA3488545 | Unit 4, Cell A06 - power fault, power has gone out to cell | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 08:30:00 | Pass | Repaired gpos in unit 4 cell a6
MSA-DCS | WA3488550 | Unit 2, A wing day room - lights are not workinf | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 08:30:00 | Pass | Quote to replace damaged day room lights
MSA-DCS | WA3488551 | arunta room HBUS not responding-SEME on site | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-18 11:29:22 | 2020-07-17 14:40:00 | Pass | HBus expander dropping offline, Hbus has another 3 expander boards and last expander dropping off.Recabled and programmed into Hbus port 2. Recabled power and tested inputs.
MSA-DCS | WA3488583 | Unit 2 C8 broken tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-27 09:40:00 | Fail | Replaced broken pillar tap
MSA-DCS | WA3488590 | Gardens prisoners toilet cracked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-27 11:00:00 | Fail | Replaced cistern fan cone rubber
MSA-DCS | WA3488593 | Gardens, Driscoll Drive, Main retic line broken (cone near location) | DCS - 15 Driscoll Drive Canning Vale | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 17 Jul 2020 | 2020-07-23 17:00:00 | 2020-09-10 14:00:00 | Fail | tree cut out and removed and damaged pipework fixed as per attached supporting documents.
MSA-DCS | WA3488615 | Section 95, work shop - tap set needs replacing | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-21 09:45:00 | Pass | Supply and install new kitchen sink mixer in workshop sink.
MSA-DCS | WA3488742 | Unit 3, A6 - window requires repairs | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-27 09:30:00 | Fail | NEW SPIRAL BALANCE & FEET FITTED
MSA-DCS | WA3488781 | Boardroom, old elec board/panel sparks & whizzing sound ocassionally from switches turning off/on | Nyandi Training Academy | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-11-08 14:30:00 | Fail | Replace faulty switch panel in board room on Sunday
MSA-DCS | WA3488803 | staff room broken window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-20 10:00:00 | Pass | RE-GLAZE & SEC FILM WINDOW
MSA-DCS | WA3488805 | gym roof leaking needs to be check coming from vent when wind blows 12mtr high | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2021-04-08 09:00:00 | Fail | REPAIRS MADE TO RECTIFY ROOF LEAKS
MSA-DCS | WA3488806 | medical centre tap leaking in dentist surgery | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 14:22:00 | Pass | Fixed leaking lhs sink in the dentist room
MSA-DCS | WA3792917 | Relocation of critical spare to Hakea stores | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Jul 2020 | 2020-07-23 17:00:00 | 2020-11-19 13:40:00 | Fail | Works complete as requestedPFM stock Catalogued and delivered to PFM stores - Hakea and Casuarina as requested.Works Complete.
MSA-DFES | WA3488500 | living are callout phone not enough wire cabling for the coms wrack | DFES Rescue Helicopter Base | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 17 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 17:00:00 | Pass | Investigated issue with Telephone failing in Lunch room. I fault found and located that the issue was the RJ45 connection at the back of the patch panel. I replaced the mech and liased with the station officer and proved everything was working correctly.
MSA-DFES | WA3488553 | engine room access door outside to engine room swipe not working-see notes | CFRS Vincent | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 13:30:00 | Pass | 22/7/20 - Dean Simpson, Joshua ParkIssue with locks as previously reported.Engine bay door not powered. Found blown fuse and replaced.BRAF submitted to replace 6 locks.1 lock replaced, will return for the others.24/7/20 - Dean Simpson, Joshua ParkReplaced the other 5 electric strikes.All tested ok.
MSA-DFES | WA3488586 | G Floor, Kitchen- Billi tap button is broken & wires are exposed | DFES - SWORD - State Wide Operational Response Div | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-24 14:33:00 | Fail | Sorry couldn’t access site as no one there to let us in on 21/7/2020. On 22.7.2020 Times were2.55 pm to 4.00 pm on this date could not get on to Promap. Exchanged tap to new one . A404214329 Billi ECO Unit .
MSA-DFES | WA3488719 | G Floor, external fire door not unlocking | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 17 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-23 17:30:00 | Fail | 17/7/20 - Ryan VestyChecked reader and door.Lock intermittently not releasing, requires replacement.BRAF submitted. 23/7/20 - Ryan VestyReplaced lock and tested, not operating.Returned later in the day with another new lock, installed and tested all ok.
MSA-DFES | WA3488725 | TV/training room roof leak and wet patch on ceiling | CFRS Wangara | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 17 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-18 09:30:00 | Pass | Inspected roof void - leak from ventilator flashing system stripped and resealed all jointsreplaced ceiling tilesmall old stain to second leak from pipework of ceiling A/C system - site to monitor.
MSA-DFES | WA3488727 | Engine Room door 4 is not functioning correctly | CFRS Canning Vale | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 17 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-17 16:10:00 | Pass | This is a hardware issue and has been flagged for replacement.Will be replace on the 29-30th install.No current issue running the door as it does not affect operation
MSA-DFES | WA3488734 | Yard - Pillar hydrant has a bad leak from ball valve and Mill cock valve very difficult to operate. | CFRS Maddington | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Critical Fire Protection & Training | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 12:30:00 | Pass | Replaced hydrant landing valve along with 50mm ball valve tested all ok on leaving siteBRAF submitted as costs over $500
MSA-DFES | WA3488858 | ComCen, Level 2, Female bathroom - sink in female toilet is blocked | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Drainage (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 12:25:00 | Pass | Cleaned sink by plunging and tunning hot water down drain and cleared
MSA-DTAG | WA3488393 | Lvl 10 - Toilet in female bathroom constantly running. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-23 16:00:00 | Fail | Complete
MSA-DTWD | WA3488280 | S block student services 2 Faults on Fire panel causing alarm | Mount Lawley Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 17 Jul 2020 | 2020-07-20 17:00:00 | 2020-09-11 11:30:00 | Fail | Faults all rectified
MSA-DTWD | WA3488408 | level 1, Museum main entrance - Door stuck, unable to open | Perth Campus B7 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 11:40:00 | Pass | 17/07 open and make temporary repairs to entry door lock. Replacement required.22/07 Replace faulty lock.
MSA-DTWD | WA3488465 | Lvl 2, Room B223- Leak in classroom next to whiteboard | Perth Campus B4 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 12:00:00 | Pass | leak in d223 not b223 - made ceiling inspection to room leak directly in front of ventilator penetration - stripped flashing to ventillator - sheet not weathered - used silicone to create water barrier - resealed flashings around unit
MSA-DTWD | WA3488517 | room V7 male toilet roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 17 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-27 09:45:00 | Fail | Leak resolved and confirmed with Frank
MSA-DTWD | WA3488538 | U Block workshop roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 16:00:00 | Pass | Leak resolved -confirmed with Frank
MSA-DTWD | WA3488599 | R block ground R010 male toilet Urinal slow to drain / partially blocked | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 09:30:00 | Pass | Cleared blockage
MSA-DTWD | WA3488619 | C block, Male & female toilets - blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 12:20:00 | Pass | Replace inlet valves and clean out drains Make sure no blockage
MSA-DTWD | WA3488641 | Room AT239 roof leak | Kwinana Automotive Centre | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-20 10:30:00 | Pass | Inspected and repaired roof leak
MSA-DTWD | WA3488649 | B block B2417 Roof leak in fashion office | Bentley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-08-10 09:15:00 | Fail | Leak resolved
MSA-DTWD | WA3488730 | A Block, Exterior, Courtyard - broken Padlock TE1 to external water testing unit | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-17 16:00:00 | Pass | replace broken padlock, keyed to master key system
MSA-DTWD | WA3488753 | Room F30 roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 10:00:00 | Pass | Leak resolved - confirmed with Frank
MSA-DTWD | WA3488758 | E Block, Foyer - Main alarm panel – RAS fail area 10 | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 2 | CLOSE | 17 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 12:20:00 | Pass | 20/07/2020No power to ras10.Depolled it to remove fault.Couldn't get into room with dgp and couldn't get in contact with client.2 options rerun cable which isn't viable and moved the keypad next to ras11 which is only 10m away.21/07/2020Showed nick keypad he advised that the cable got cut during construction but not to worry about it as they don’t usekeypad and didn’t even know it was there
MSA-DTWD | WA3488800 | D Block, Lvl 2 & 3- Lights in passages not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 14:45:00 | Pass | Job complete
MSA-DTWD | WA3488807 | D Block, Room D307 - leaking from concrete roof above | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 17 Jul 2020 | 2020-07-24 17:00:00 | 2021-05-18 15:00:00 | Fail | Roof leak repaired
MSA-DCS | WA3488876 | Unit 4 entry grill lock is non functional and the A wing day room door lock is faulty | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 18 Jul 2020 | 2020-07-18 11:20:13 | 2020-07-18 09:00:00 | Pass | Supplied and installed replacement parts as required.
MSA-DCS | WA3488878 | MPU,SHU -Internal Security cameras inside the Unit is not working | Casuarina Prison-External Area | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Jul 2020 | 2020-07-18 11:45:10 | 2020-07-18 12:00:00 | Fail | Operator error, traced issue to software being closed and unit unable to re assign monitors, re assigned and explained process to senior officer. System fully operational.
MSA-DCS | WA3488897 | SITE COST 2 cameras in visits hall have stopped working, and other cameras are dropping in and out | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Jul 2020 | 2020-07-18 14:36:09 | 2020-07-18 13:00:00 | Pass | Reset both cameras and tested all tested ok
MSA-DCS | WA3488909 | detainee reception - cam 73 has no feed | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jul 2020 | 2020-07-19 11:50:52 | 2020-09-10 13:28:00 | Fail | Repaired faults with Admissions/Detainee Reception cameras, confirmed all working correctly.tested OKJob Complete
MSA-DCS | WA3488915 | Zone12 Alarm Cowlin sensor on the outside keep going off | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Jul 2020 | 2020-07-19 12:16:10 | 2020-07-18 17:15:00 | Pass | Contacted Wooroloo to advise of delay, attended to f i nd controller latched in alarm, tested cabling good, reset controller and alarms restored. Tested fence operational.
MSA-DCS | WA3488959 | SITE COST Alarm going off in equipment room | Karnet Prison Farm | WSM-BR-SITE | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Jul 2020 | 2020-07-18 21:56:15 | 2020-07-20 10:00:00 | Fail | Pickup part from workshop and travel to site to replace the water damaged MDAS receiver T9 B6 R0. Tested it ok after replacement. Also reset SN1 enclosure tamper alarm in equipment room.
MSA-DFES | WA3488921 | lift is out osf service.that's one lift . down stairs is closed top is opened | DFES Education and Heritage Centre | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 0 | CLOSE | 18 Jul 2020 | 2020-07-18 17:13:23 | 2020-07-20 09:45:00 | Fail | CAR DOORS JAMMING, FOUND ROCK WEDGED BETWEEN CAR DOOR SHOES AND SILL, REMOVED, CONFIRM OPERATION. AND RETURN TO SERVICEEQUIPMENT RUNNING, BACK TO NORMAL OPERATIONStephanie Edwards from Kone confirmed no charges
MSA-DCS | WA3490263 | Casuarina Prison-Main kitchen roof leak from the aircon | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 19 Jul 2020 | 2020-07-19 11:26:53 | 2020-07-24 15:30:00 | Fail | Attended an after hours call out for the Kitchen evap leaking water. When I attended I found both belts snapped and the water foaming up over the basin for the unit. No spare belts on site and they where a specific size. I isolated the unit. I also investigated the foaming of the water. No chemicals present so I suspect an issue with the water supply as there was a large amount of calsium build up. I isolated the water the unit. Tech will need to attend with new belts and further investigate the water leak.
MSA-DCS | WA3490304 | couple of the camera in gate house area is not working properly | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 13:30:00 | Pass | Attended site.Checked DVM system.Checked all cameras in Gatehouse - live video and recordings.Checked CCTV Workstations and monitors in control room.CCTV system is fully operational in Gatehouse
MSA-DCS | WA3490316 | Unit 1 A wing blocked drain | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 19 Jul 2020 | 2020-07-19 18:08:21 | 2020-07-19 16:30:00 | Pass | nil
MSA-DCS | WA3490323 | SITE COST Unit 1B electric cabinet 2 freezing camera from the alarm | Wooroloo Prison Farm | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Jul 2020 | 2020-07-19 18:35:44 | 2020-07-22 12:00:00 | Fail | Attended site.Checked and resecured connections to reed switch on Unit 1B EC cabinet 2.Adjusted settings on IndigoVision system.Conducted test.All back to normal and operational
MSA-DCS | WA3490420 | perimeter alarm in fault | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 19 Jul 2020 | 2020-07-20 01:20:51 | 2020-07-20 00:01:00 | Pass | Attended site,External perimeter not working and showing blue.Checked senstar servers, Sennet network 3 had software error and has shut down.Restored SN3 and tested various external perimeter zones, working.Stress tested SN 3 by connecting to various controllers and running report. Controllers are all online.
MSA-DCA | WA3491108 | CRC, plantroom - Faults on Heating Water System | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Plant Room - Loading Bay Area | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 16:02:00 | Pass | Complete
MSA-DCS | WA3490828 | Admin, Staff change roooms - light not working | Boronia Pre-release-AH19 - Administration, Education Senior Officers and Programs-Ground Floor-Staff Office | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 13:30:00 | Pass | Changed light fittings in staff toilets
MSA-DCS | WA3490867 | CCU, C6 - sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 10:30:00 | Pass | Plunged basin to clear blockage
MSA-DCS | WA3490878 | Pedestrians gate, inner managemnet fence to the rear - locks not working manually or electric | Greenough Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Jul 2020 | 2020-07-20 15:48:07 | 2020-07-21 18:30:00 | Fail | Pedestrian man gate doesn’t lock and can’t be operated through ebi and manual keys. Trace and check the power from equipment room, ok and normal. Dismantle the lock and clean. Check and test the reed switch funtions, check all the cable connection. Replaced the relay that control the power with un used spare device . Test the man gate multiple times through ebi ok and back to normal operations. Advice SO at the gatehouse with regards to the door closer problem , keeps the door open and not closing properly.
MSA-DCS | WA3490895 | Unit 1, Cell D7- Tap on the sink is loose | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-24 17:00:00 | 2020-08-05 15:00:00 | Fail | Remounted loose basin tap in cell
MSA-DCS | WA3490900 | Unit 5, B & D Wing- Service duct between B7 & B8 has a water leak dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 08:00:23 | 2020-07-21 09:30:00 | Fail | Replaced 2 x leaks on corroded pipe work in plumbing duct.
MSA-DCS | WA3490902 | Unit 4, A10 - Toilet button not working correctly/not flushing properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 09:30:00 | Pass | Replaced spring and remounted cistern. Tested
MSA-DCS | WA3490907 | Unit 6, C Wing, Cell C05- Toilet flush button keeps getting stuck | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-20 15:00:00 | Pass | Replaced inlet valve and outlet rubber in cistern.
MSA-DCS | WA3490911 | Unit 13. A Wing, Cell A11- Sink is blocked, not draining awat | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 10:30:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3490926 | Unit 4, D Wing, Cell D03- Copper water feed pipe under sink dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 11:30:00 | Pass | Resealed and retightened water connection underneath basin.
MSA-DCS | WA3490927 | Unit 3, D wing - cleaning cupboard tap dripping, not turning off properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-21 11:30:00 | Pass | Replaced leaking spindle
MSA-DCS | WA3490934 | Unit 4, D Wing Shower, Basin tap is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-05 11:30:00 | Fail | Collected parts offsite. Removed old tap set. Remounted basin to wall. Installed new tap set and tested.
MSA-DCS | WA3490943 | Unit 2, A Wing- Last shower (closest to the window) is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-21 13:00:00 | Pass | Replaced leaking spindle
MSA-DCS | WA3490945 | Unit 4, C Wing, Cell C5- tap is constantly leaking water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-20 14:00:00 | Pass | Replaced leaking spindle in shower.
MSA-DCS | WA3490951 | Unit 1, A & C, Cell A10- toilet not working due to water tank not filling up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-21 14:00:00 | Pass | Adjusted cistern and flush button to allow cistern to operate correctly.
MSA-DCS | WA3490957 | Gate control - Zone 4 toweling unable to secure | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 08:17:34 | 2020-07-20 11:30:00 | Pass | Checked and found Zone 4 crawling alarm keep going off and can’t be reset. Recalibrate the sensitivity and reboot the controller. Tested it all ok after.
MSA-DCS | WA3490958 | Unit 3, A & C dayroom - Urn is constantly dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 10:36:00 | Pass | Everything okay nothing dripping Rheem A40191316E
MSA-DCS | WA3490963 | Gate control - Zone 6 - Camera 1 no vision | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 08:20:50 | 2020-07-20 12:45:00 | Pass | Zone 6 Camera 1 no vision on monitor wall in control. Checked camera signal in EC cabinet is ok. Located problem to be the Indigovision 8000 encoder. Reboot the encoder and test it ok. Encoder is old. Suggest to replace the encoder if problem happens again.
MSA-DCS | WA3490964 | Unit 3, B & D dayroom - Urn is not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 10:47:00 | Pass | All working okay Checked over nothing wrong A40191317F
MSA-DCS | WA3490969 | Unit 1, C11 - Hole, plaster has been dug out & a cavity into the section behind has been open up | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 08:13:32 | 2020-07-20 14:15:00 | Pass | FILLED IN HOLE
MSA-DCS | WA3490974 | Unit 1, C12 - a Hole on right hand side of toilet bowl where the floor meets the wall | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 08:24:23 | 2020-07-20 15:00:00 | Pass | FILLED IN HOLE
MSA-DCS | WA3490978 | Justice Rec Club, Main Bar- Broken Window By Pool Table | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-10 15:00:00 | Fail | RE GLAZE AND RE TINT
MSA-DCS | WA3490984 | Entrance driveway- Pot holes need repair | Karnet Prison Farm | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-21 14:45:00 | Pass | 21/07/20Picked up asphalt.Repaired 9 potholes.Road needs resurfacing, in very bad condition.
MSA-DCS | WA3490989 | Unit 1, D7 - window cracked | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-21 09:30:00 | Fail | NEW WINDOW SASH & SPIRAL BALANCES FITTED
MSA-DCS | WA3490997 | Unit 3, D8 - Window not staying up | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 10:45:00 | Pass | NEW SPIRAL BALANCES & FEET FITTED
MSA-DCS | WA3491003 | Unit 1, C11 - The light switch cover needs replace can easily be removed by hand | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 08:37:02 | 2020-07-20 14:30:00 | Pass | Repaired faulty lights switch in unit 1 c11
MSA-DCS | WA3491006 | Unit 5, C wing, cleaning room - power point has become loose from the wall and has wires exposed. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 08:39:22 | 2020-07-20 13:00:00 | Pass | Replaced gpos in unit 5 cleaning store
MSA-DCS | WA3491008 | Unit 1, Hut 10 - light switch broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 08:30:00 | Pass | Investigate and replace Unit 1 Hut 10 light switch
MSA-DCS | WA3491015 | Unit 1, Light outside office door hanging from ceiling | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 10:00:00 | Pass | Investigate and repair light Unit 1 office outside
MSA-DCS | WA3491041 | Unit 4, Cell C14- Cell Window Cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 08:47:18 | 2020-07-21 11:00:00 | Fail | CELL WINDOW REPLACED
MSA-DCS | WA3491044 | Unit 14 - B Wing blocked shower drain in B13 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 13:00:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3491049 | Unit 2, A wing - power point at end of A wing, tripped when buffer plugged in | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 15:00:00 | Pass | Repaired damaged circuits for unit 2 a wing. Also replaced faulty plug on floor buffer
MSA-DCS | WA3491050 | MPU (8), Cell M20- Grip/handle on the slider on cell window damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-13 15:00:00 | Fail | CELL WINDOW VIEWING HATCH REPLACED
MSA-DCS | WA3491052 | MPU (8), Cell M12- Grip/handle on the slider on cell window damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-13 14:40:00 | Fail | REPLACED CELL SLIDING VIEWING HATCH
MSA-DCS | WA3491055 | MPU (8), Cell M10- Grip/handle on the slider on cell window damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-13 14:20:00 | Fail | REPLACED CELL WINDOW SLIDING VIEWING HATCH
MSA-DCS | WA3491056 | front gate air lock 2 x Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-21 10:30:00 | Pass | Replaced lights
MSA-DCS | WA3491076 | Front gate, sliding doors, exiting towards visits - very slow to open | Hakea Prison | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 09:06:00 | 2020-07-20 15:15:00 | Pass | Replaced two (2) batteries and test operation, all okay.
MSA-DCS | WA3491129 | unit 1 B wing toilet and shower is blocked | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 09:44:32 | 2020-07-20 12:00:00 | Pass | unblocked toilet
MSA-DCS | WA3491130 | Recovery Restraints Cabinet lock needs attention/ replacing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 09:45:29 | 2020-07-20 11:30:00 | Pass | Realign hinges and lubricate locks
MSA-DCS | WA3491132 | Unit 1 A wing cell A1 broken window | Bandyup Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-17 12:15:00 | Fail | RE GLAZE CELL WINDOW
MSA-DCS | WA3491144 | Unit 1, A & C Wing- Bolts are loose from windows, additional info below | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-09-07 13:00:00 | Fail | ALL BOLTS ASSESSED IN BOTH WINGS - BOLTS EITHER REPLACED OR TIGHTENED
MSA-DCS | WA3491156 | Charger leed for the tug has been broken. (It is the 2100hp charger (left charger) | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 09:56:16 | 2020-07-20 16:30:00 | Pass | Repaired damaged tug charger in kitchen
MSA-DCS | WA3491188 | unit 2A cell 5 - broken window | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 13:30:00 | Pass | RE-GLAZE BROKEN WINDOW
MSA-DCS | WA3491199 | front gate intercome link to the gate not working correctly | Broome Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 10:21:58 | 2020-07-20 15:00:00 | Pass | Contacted site and advised that gate lock was having intermittent issues when gate needs to be unlocked. Had site reset power from connections below desk and leave off for several minutes. After reset had site test multiple times and all had tested and was working correctly. If issue re-occurs then recommend replacing relays for gate release and also intercom at gate.
MSA-DCS | WA3491208 | units 3 & 4 tv reception dropping out on all channels | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Sapio Pty Ltd | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-04 13:00:00 | Fail | Tested all points entering Units and reception is good to very good. Unit 4 each Block A - L has external box with 4 waytap, reception is good at each 85 - 95% In cells it drops to 75 to 80% A lot of modifications found throughout cells with some cells splitting TV points to boost radio antennas Most complaints come at night. Possible amplifier upgrade required and inspection of damage wall plates as well as modified. For now reception is good throughout. Job completed
MSA-DCS | WA3491211 | Gate house, kitchen roof leak through exhaust fan | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 10:00:00 | Pass | MOST LIKELY THE FAN GETTING WIND BLOWN RAIN ENTERING - MODIFY TO SUIT AND SEAL PENETRATION
MSA-DCS | WA3491214 | Unit 2, Cell C12, A15 and D8 - taps are leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-27 12:00:00 | Fail | COMPLETED
MSA-DCS | WA3491241 | L2 electrical room Fire Panel Showing Faults | Melaleuca Prison | SPA-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 20 Jul 2020 | 2020-07-20 14:52:33 | 2020-07-29 13:17:00 | Fail | Arrived on site - refused access, have another callout for Hakea will return once completeReturned to site for fault when arrived vesda in fault unit 11 a/c 15&16. Went and looked and showing valve open and valve closed. Manually tried to open and close the valve which was stuck couldn’t get rid of fault. Went and tested to make sure still goes into alarm all working fine. Recommend swapping vesda unit out with new over 10 years old.Also two times earth faults on panel loop 1 &3 going to log another job through
MSA-DCS | WA3491245 | Unit 2, A 7 - toilet blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 10:55:34 | 2020-07-20 15:01:00 | Pass | Cleared blockage to WC
MSA-DCS | WA3491253 | Control, Vesda fire alarm, sensor fault in cell block 5 | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 20 Jul 2020 | 2020-07-20 15:01:27 | 2020-07-20 15:00:00 | Pass | cleaned all sampling points in a wing A
MSA-DCS | WA3491258 | Unit 2, office, control - PA microphone not working | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-09-04 14:00:00 | Fail | Job complete
MSA-DCS | WA3491271 | Unit 2 A7 Broken Shower Tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 12:00:00 | Pass | Attended site and replaced all damaged and broken floor tiles in shower recess.
MSA-DCS | WA3491277 | Health Admin, Dental - Aircon only blowing cold air | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 10:15:00 | Pass | Test ran unit on arrival and checked condenser. All operating as designed.Left running in 24 set point over night to ensure it maintained without fault.Returned and found unit still running as designed. All ok at time of departure.
MSA-DCS | WA3491280 | Unit 2 A16 Broken Bed Panel | Melaleuca Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Schlager Construction Group | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-31 11:30:00 | Fail | Attended site and carried out repairs to the broken bed panels.
MSA-DCS | WA3491307 | Unit 1, Cell B5- Broken shower hot tap | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 11:14:31 | 2020-07-20 15:30:00 | Pass | Reset tap spindle in duct to fix tap
MSA-DCS | WA3491309 | Unit 1, Cell A2- Sink & Shower Drains blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 11:17:06 | 2020-07-20 16:00:00 | Pass | Clear blockage to sink and shower
MSA-DCS | WA3491313 | Unit 1, Cell B13- Cell Door Jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 11:18:39 | 2020-07-21 13:00:00 | Fail | Job completed - Supplied and fitted replacement lock and adjusted strike. Had to wait for muster to complete.
MSA-DCS | WA3491314 | Unit 14, D11 - upper bunk light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 10:00:00 | Pass | investigate and repair bed light in unit 14 cell D11
MSA-DCS | WA3491318 | Unit 5, C7 - top bunk light flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 09:30:00 | Pass | Repaired faulty lights in unit 5 c7
MSA-DCS | WA3491329 | unit 14, A/C - the cold water tap handle for the shower in cell is loose | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 14:00:00 | Pass | Attended unit. Staff asked and unable to locate the cell with issue. No action taken.
MSA-DCS | WA3491336 | Unit 13, D Wing, Cell D16- Sink is blocked & can not be cleared with a plunger | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 15:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3491337 | unit 13, B wing, Cell B16 - sink is blocked and cant be cleared with a plunger | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 16:00:00 | Pass | Plunged basin to clear blockage
MSA-DCS | WA3491338 | Unit 13, D Wing, Cell D3- Sink is blocked & can not be cleared with a plunger | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 08:30:00 | Pass | Plunged basin to clear blockage
MSA-DCS | WA3491341 | Unit 14 - B & D Blocked shower drain in cell B#3, unable to unblock with plunger.-see notes | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 09:30:00 | Pass | Used acid and plunger to clear blockage in shower drain
MSA-DCS | WA3491342 | Unit 1, C4 - bolt missing and sealant needed around window | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 14:30:00 | Pass | CLOSE OFF COST TO DATE 28/08 - THIS JOB IS A DOUBLE UP OF #WA3491144
MSA-DCS | WA3491355 | unit 1 cells 5,6,10 and 11 cell call buttons not working | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 11:41:21 | 2020-07-28 13:00:00 | Fail | 28/07 Returned to site with another CI-8A card and replaced remaining CI-8 card. This ensured no compatibility issues with other new cards, replaced (now too short) interconnecting cables for audio and power. Reset system. Tested origional faulty cell call ports locally and confirmed they were operating correctly. As we had disturbed the entire cell call system in Unit 1, we tested every cell in the unit between cell and unit control room. All cell calls operating correctly.
MSA-DCS | WA3491360 | External Zones 5, 6 & 19 not activating | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 11:43:47 | 2020-07-24 11:59:00 | Fail | Reported multiple zones not activating. Sourced parts, attended site, repaired multiple perimitrax faults. Recalibrated and tested OK.Job Complete
MSA-DCS | WA3491363 | Unit 10 A5 Water dripping from back of sink | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-27 12:28:00 | Fail | Replaced outlet lock but and replaced o rings in outlet
MSA-DCS | WA3491374 | Unit 6, C9 - top bunk intercom not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-21 11:00:00 | Pass | Attended site.Checked connections and wiring on both intercom units in cell C9.Checked input on CI-8 board.Conducted test.Received loud and clear response from control room.All ok at departure.
MSA-DCS | WA3491379 | Unit 6, A & C- Tap/spout is leaking and spraying | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 10:30:00 | Pass | Replaced leaking spindle and aerator in kitchen sink tap
MSA-DCS | WA3491387 | Unit 13 - Plant-Room Bulb on the UV appears to be broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-13 09:30:00 | Fail | 23/7/20 - Investigate Uv globe in plant room. Globe requires replacement. Needs to be ordered in.13/8/20 - collected globes offsite. Installed new uv globe. Cleaned inside of globe housing. Tested.
MSA-DCS | WA3491393 | Unit 14 - Plant-Room The UV bulb in the Guardian Unit requires attention | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-13 11:30:00 | Fail | 23/7/20 - Investigate I’ve globe in plant room. Globe requires replacement. Needs to be ordered in.13/8/20 - collected materials offsite. Installed new Uv globe. Cleaned inside globe housing. Tested
MSA-DCS | WA3491423 | Gate House- Main zone F3 monitor not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Jul 2020 | 2020-07-20 16:15:04 | 2020-10-02 16:51:00 | Fail | Repaired indigo encoder faults and tested ok.job Complete
MSA-DCS | WA3491431 | Light in the female toilet level 3 (near kitchen), and light on level 2 (near lift entry door). | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-20 17:45:00 | Pass | Replaced failed lamps on level 2 + 3.
MSA-DCS | WA3491541 | Unit 1, DB yard - external lights not working propley | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-12 10:30:00 | Fail | Replaced light fittings and tubes
MSA-DCS | WA3491544 | Unit 2, B wing - lights are out | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-12 12:00:00 | Fail | Replaced various tubes and starters and 2x large led downlights
MSA-DCS | WA3491602 | Abattior - 2 lights not working in freezer 4 | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 13:30:00 | Pass | Repair faulty lights in Abattoir freezer
MSA-DCS | WA3491645 | Bakery tap at rear has two leaks poss resealing with PTFE tape | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 11:30:00 | Pass | Repaired leaking hose tap in bakery.
MSA-DCS | WA3491698 | Medical Centre, Both sinks blocked, line issue | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 14:09:30 | 2020-07-21 10:15:00 | Pass | Drain machine used down x2 basins located should removing gloves plastic cups rocks etc clearing blockage
MSA-DCS | WA3491741 | Main switchboard concrete plinth is broken | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-29 09:00:00 | Fail | Removed old plinth from site main switchboard installed new plinth and refixed switch board
MSA-DCS | WA3491743 | Unit 15, Cell C9- Light cover has had 2 holes burnt for ligature point | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-27 11:00:00 | Fail | Removed damaged cell light diffuser, ordered replacement, picked up and installed
MSA-DCS | WA3491760 | Assessments, Main Corridor - Male Toilet Cistern keeps running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-21 08:50:00 | Pass | Pulled apart cistern replacing outlet washer
MSA-DCS | WA3491763 | Unit 1 C4 basin tap is broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 14:52:08 | 2020-07-21 07:55:00 | Pass | Pillar tap was loose undid panel on side off stainless basin retighting pillar tap
MSA-DCS | WA3491783 | unit 5 house 4 number of down lights out | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-12 13:30:00 | Fail | Replaced 5x led downlights
MSA-DCS | WA3491784 | unit 5 house 4 and 8 exhaust bathrooms not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-12 14:30:00 | Fail | Replaced wall exhaust fans in 2 houses
MSA-DCS | WA3491785 | unti 5 house 8 HW is not getting hot luke work | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-24 10:45:00 | Fail | COMPLETED
MSA-DCS | WA3491790 | Unit 2, office door lock is not locking | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 15:27:49 | 2020-07-21 11:35:00 | Pass | Lock on Unit 2 - office door is faultyNew lock fitted keyed to Prisons system
MSA-DCS | WA3491802 | ECR control room alarm system showing alarm that server requires registration | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 16:47:33 | 2020-07-21 09:15:00 | Pass | Attended site and investigated the fault.Checked settings on server and found alarm that requires registration.Restarted both servers and done synchronisation.Conducted test.All back to normal and operational.
MSA-DCS | WA3491807 | Fire panel to be reset and delay in connecting to fire brigade, needs checked. | Boronia Pre-release-AS20 - Industries Vocational Skills Development-Ground Floor-Fire and Security Panel Room | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 17:34:01 | 2020-07-21 09:12:00 | Pass | After hours call to Baronia after fire alarm due to cooking in house. Unable to reset panel as locked in alarm had to restart all panels to be ableto reset alarm. Then found module for brigade call locked active. Powered down module to clear alarm left panel normal and reinstated codered to normal.BG 21/7Strobe outside house 11 still active after alarm reset. Traced back to module in Gardens office DGP. Rebooted DGP and strobe reset
MSA-DCS | WA3491813 | External perimeter has gone down, not working. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Jul 2020 | 2020-07-21 00:42:15 | 2020-07-20 23:15:00 | Pass | Attended site checked and found external Perimeter already back on line but found multiple zones MW & PX ALARMS are not activating when officer done walk test. Reset Senstar modules and tested all zones MW & PX are activating and resetting correctly.
MSA-DFES | WA3490871 | engine room - engine room doors will not go up or down | CFRS Duncraig | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 20 Jul 2020 | 2020-07-20 17:00:00 | 2020-07-20 13:53:00 | Pass | Technician attended the site of Duncraig Fire Station to the Engine Room Roller Door No. W22174 on 20/07/2020. Following a full test and inspection of door components identified door is working when the tech attended the site. Checked all wiring, loose connection in PLC box and remote box. Also checked all other doors operating correctly. Full test and inspection of door function completed prior to leaving site. Technician returned on site on 07/08/2020 to repair coil cables for bump strips to all engine room doors. He repaired 3 x cables and replaced 1 entirely. Tech has noticed whilst working on the doors that none of the bump strips actually work, door 2 opens when triggered in the closed position. As far as he is aware there is work planned on these doors next week. Only carried out works he was asked to do today.
MSA-DFES | WA3491153 | Driveway - Roller on sliding gate has worn away, perished and cracked. | CFRS Duncraig | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-12 09:30:00 | Fail | Wheels Replaced job closed off
MSA-DFES | WA3491320 | Cleaning Room near gym- light is flashing constantly | CFRS Vincent | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 12:15:00 | Pass | CompleteLocated flickering light in cleaner store room, replaced led panel and all in working order
MSA-DFES | WA3491328 | Roof - Reception of all TV channels is poor, TV antenna needs repair | CFRS Duncraig | GMP-BR | ICT/Audiovisual | General AV works (AV) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-11 17:00:00 | Fail | Located faulty RG6 crimp at the TV in the Theatre room. Re terminating corrected this issue and all is working.
MSA-DFES | WA3491366 | Ground level, staff entry & exit door - Latch to door not engaging, latching correctly | DFES Education and Heritage Centre | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 12:30:00 | Pass | service to lock and adjustment to door closer
MSA-DFES | WA3491388 | SES vol office - Fire detectors are alarming, (detectors are low battery) | DFES Regional Office - Belmont | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-22 08:00:00 | Fail | Call out - investigated fire detectors faulting - removed 4x smoke detectors battery operated from rooms. 2x dead batteries - all rooms covered by hard wired (FIP) smoke detectors.
MSA-DFES | WA3491450 | ground All CL&D offices Aircon too cold needs resetting. | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-21 10:30:00 | Pass | Completed service - call out, reset boiler, all appears ok.
MSA-DFES | WA3491723 | rear of the engine room, strobe llight for doors to open and close not operating | CFRS Midland | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 17:00:00 | 2020-08-06 15:30:00 | Fail | Reattended site and replaced 2 x Green Go lights on doors 3 and 4. Tested for funtion and notified staff.
MSA-DFES | WA3491789 | Zone 15 Kitchen- Hot water system (wall mounted urn) is not working properly. | CFRS Perth | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-21 12:58:00 | Pass | Unit turned off on arrival and continuing to run water out the overflow. Checked solenoid and level sensor. Changed faulty solenoid and JG fitting on unit. Ran system. Waited for unit to heat up and let water in. Cleaned calcium off tap. Normal operation
MSA-DTAG | WA3491059 | Ground, listings office - Lights have failed | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-21 14:30:00 | Pass | Job complete
MSA-DTAG | WA3491294 | courts UPS system cannot be operated by Wilson Sec in their office-see notes | Central Government Buildings - Perth David Malcom Justice Centre | WSM-BR-SITE | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 20 Jul 2020 | 2020-07-20 15:09:39 | 2020-07-20 15:00:00 | Pass | Fitted new mounts on work station and monitors to wall, checked all functions
MSA-DTAG | WA3491799 | Custody The electronic switch that controls the green door, bail door & sally door has failed | Joondalup Courthouse | GMP-BR-HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-01 10:00:00 | Fail | Push button assembly replacement
MSA-DTWD | WA3490860 | C block, Cafeteria Walk-In Coolroom - Not Cooling | Bentley Campus | GMP-BR | Refrigeration | Coolroom (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 20 Jul 2020 | 2020-07-20 17:00:00 | 2020-08-10 16:00:00 | Fail | Traveled to site and signed in. Located Cafeteria Coolrooms and found that two of the walk-in Coolrooms had tripped. Found that main breaker at board was tripped. Condensing unit 1 has a dead short. Tested electrics and found that compressor relay had blown takingout the compressor and timer. New Compressor, start relay and timer required. Braf will be submitted.TRAVELED TO SITE AND SIGNED IN. LOCATED CAFETERIA COOLROOMS AND FOUND THAT TWO OF THE WALK-IN COOLROOMS HAD TRIPPED. FOUND THAT MAIN BREAKER AT BOARD WAS TRIPPED. CONDENSING UNIT 1 HAS A DEAD SHORT. TESTED ELECTRICS AND FOUND THAT COMPRESSOR RELAY HAD BLOWN TAKINGOUT THE COMPRESSOR AND TIMER. NEW COMPRESSOR, START RELAY AND TIMER REQUIRED. BRAF WILL BE SUBMITTED.ATTENDED SITE AN ASSISTED PAUL WITH FIRE WATCH TO REPLACE COMPRESSORPICKED UP PARTS FROM SUPPLIERS. TRAVELLED TO SITE. GAINED ACCESS TO SITE. MET WITH OTHER TECH FOR FIRE WATCH. COMPLETED PAPERWORK. RECLAIMED REFRIGERANT. REPLACED COMPRESSOR AND DRIER. PRESSURE TESTED
MSA-DTWD | WA3491078 | M block ground main system No heating (A/C on, but blowing cold air) | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 16:00:00 | Pass | Signed in and accessed site. M block temps showing some vav heater banks tripped. Attempted to use supplied bms user and passwords to no avail. Site notified of no bms access which controls all m block hvac operation. Inspected vav ac 1,2,3 circuits. Reset 20amp breakers and took amp readings . Amp readings close to trip when running. Inspected vav airflows etc as much as can without bms access. Carried out supply airflow increase to reduce temps. Air flow increased and amp readings reduced.
MSA-DTWD | WA3491088 | B block L1 Door Scanner to allow access to staff room is not working | Mandurah Campus (formerly Peel) | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-22 09:00:00 | Fail | 20/07/2020, 1500-1530No one onsite has acces to comms rooms.Tech support suggests check for LAN issues.LAN isolator may fix issue22/07/2020, 745-900Installed LAN isolator for RAS 7. Tested ok door working correctly. Cleared LAN test fails.
MSA-DTWD | WA3491110 | B Block entrance area - has a faulty light sensor | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 15:00:00 | Pass | Removed sensor from entrance and removed feed from lights that keep turning off when sensor is not activated and get feed from lights that are operated from light switch so they all come on together
MSA-DTWD | WA3491127 | Whole site has lost heating - about 18 degress in building | West One Services | GMP-BR | Equipment | Electrical Equipment (EQ) | Precise Air Group | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-20 15:52:00 | Pass | Attended site . Found boiler on fault. Pushed button to bring up fault code 2 red flashes. Contacted as boilers and spoke to Dean that if reset it should be fine . Reset and tested building and cycled multiple times without a fault . If problem happens again call W.A boilers
MSA-DTWD | WA3491161 | G block G129 male toilets second cubicle blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-23 10:30:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3491292 | Block A, Room A1- The vent to the store room is broken | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-28 08:30:00 | Fail | Liam Hanlon (23/07/2020) - Work NoteAttend site speak with facilities Store room door in drawing room needs air vent replaced Source and order air vent 600x400 to be delivered to office from air additions Will need to attend 1st thing before classes Will have another job to attend same day preferredLiam Hanlon (28/07/2020) - Work NotePick up air grille from office Attend site Get set up close to A1 room Get access and remove door Measure and mark doorCut out for air grille Click and fit new air grille Re hang door Get door locked Clean up
MSA-DTWD | WA3491296 | Block 0, Glasshouse- Boiler is not coming on automatically | Murdoch Campus | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-06 11:30:00 | Fail | Replaced control box and flame rod on gas burner as per approved BRAF
MSA-DTWD | WA3491302 | T block, right hand side lifts not working, doors closed no entry. | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 20 Jul 2020 | 2020-07-20 15:11:46 | 2020-07-20 12:45:00 | Pass | Not chargeable
MSA-DTWD | WA3491311 | B block staff room B15 roof leak water dripping from fan | Murdoch Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 12:45:00 | Pass | Sourced leak, stripped sheets and found previous contractors had double capped sheets nd it had two holes penetrating underneath sheets, allowing rain to seep through laps. Sealed holes not in use and sealed lap at the back of other lap sheet.
MSA-DTWD | WA3491331 | L2 control room batteries faulty may need replacing | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-20 16:00:00 | Pass | Attended site and investigated fault at 19 Aberdeen st. Found That controller 12 was not onlinewith the LIU controller.. uncorrected the controller was operating correctly.Reloaded the LIU software and data base. Checked and confirmed that all devices and doors wereon line and operating correctly. Replaced batteries in the control as requested by site.
MSA-DTWD | WA3491345 | E block ground corridor E26 Free standing freezer is not working-Engie on site | Bentley Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-20 14:00:00 | Pass | While on-site a upright Freezer had stopped working. Located freezer and found that circuit breaker had tripped. Found that condensing fan had seized and burnt the wiring. Traveled off-site to supplier to pick up parts. Removed and installed new condensing fan. Tested operation. All ok.
MSA-DTWD | WA3491669 | Level 2, D225 - No lights and power on lecture theatre | Perth Campus B4 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-20 10:45:00 | Fail | Attended site and signed in. Located B4 lecture theatre. Tested and found floor box gpo cable faulty. Tried to locate where cable is fed from to identify how to rewire. No access and can not rewire. Installed 2 double gpos next to control station of lecture. Isolated old cable in floor box and at switchboard. Tested all okay. Job complete
MSA-DTWD | WA3491686 | A block, level 1, A146 - BMS requires adjusting for Faults on Boiler Temps for AHU's | East Perth Campus | GMP-BR | Building | Materials (BU) | Building Automation & Electrical Services Pty Ltd | 2 | COMPFIN | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-23 00:00:00 | Pass | works completed-Works to closed out at $0 cost
MSA-DTWD | WA3491693 | E Block, G Floor, Room E70- Sink spout is broken | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-21 17:45:00 | Pass | Replace 2 spouts small scale and e74
MSA-DTWD | WA3491694 | M block, Ground & Roof, FP Zone 9 (Supply air unit 2) - False fire alarm | Balga Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-21 09:00:00 | Pass | Fault fixed
MSA-DTWD | WA3491750 | A Block, Room A354- Air Con to HR not heating again | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 1 | CLOSE | 20 Jul 2020 | 2020-07-21 17:00:00 | 2020-07-21 10:30:00 | Pass | Attended site, set up ladder and harness.investigated ac4 system and found hp switch to have an intermittent fault. Picked up new parts from supplier,reattend site and fitted new parts.tested and left system operational
MSA-DTWD | WA3491777 | T Block, level 3 - Boilers are losing water from the relief valves, check for over pressure | Murdoch Campus | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 2 | CLOSE | 20 Jul 2020 | 2020-07-23 17:00:00 | 2020-08-06 09:30:00 | Fail | Replaced 2 x faulty safety relief valves as per approved BRAF
MSA-MRWA | WA3491020 | Please supply 10 of the below keys, PFM to pick up | Materials Engineering Branch | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 20 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 12:17:00 | Pass | 2 x EVVA DPS keys picked up from our workshop
MSA-DCA | WA3492621 | Near G32 Leak from ceiling-possible sprinkler pipework | State Library of WA-Main Building-Ground Floor-G32 - Meeting Room - Divisional Librarian | GMP-BR | Fire Protection Services | Sprinkler Systems (FP) | Critical Fire Protection & Training | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 14:30:00 | Pass | Call out due to leak from ceiling possible sprinkler pipework.Leak was found to be sprinkler pipe needing to be replaced.Drain system, remove sprinkler, rectify leaking pipe.Reinstate and check all before leaving site.
MSA-DCS | WA3491961 | Internal zone 12 & 13 permitrax and 13 IRB - not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Jul 2020 | 2020-07-21 11:16:47 | 2020-07-24 12:03:00 | Fail | Investigated multiple perimeter faults after storm. Repaired multiple zones, some faults still exist but will complete repairs on job WA3451352.This Job is now Complete
MSA-DCS | WA3492013 | Gatehouse, disabled toilet - light fitting faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 15:00:00 | Pass | Repair Gatehouse disabled toilet light
MSA-DCS | WA3492066 | Laundry - light fitting faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 16:30:00 | Pass | Repair Laundry light fitting
MSA-DCS | WA3492068 | Unit 3, Cell C10 - light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 08:30:00 | Pass | Investigate and repair Unit 3 Cell C10 light fitting
MSA-DCS | WA3492188 | Amenities, male Gym - Shower head broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-21 16:00:00 | Pass | Inspected. Collected parts offsite. Installed and tested new shower head
MSA-DCS | WA3492200 | Entry POD - Fire panel, alarm in unit 4 , showing as fault | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Automatic Fire Protection (ARA) | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 08:01:35 | 2020-07-21 12:00:00 | Pass | System status displaying normal on departure
MSA-DCS | WA3492208 | UNIT 4, A & C Urn tap running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 10:20:00 | Pass | Replaced tap on Rheem Unit A40191315D
MSA-DCS | WA3492209 | Unit 3, Cell D5- Door not closing properly | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-22 11:00:00 | Pass | REPAIR CELL DOOR
MSA-DCS | WA3492215 | INF (10) - Fluro light treatment room needs replacing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 13:00:00 | Pass | Repaired faulty lights in infirmary treatment rooms
MSA-DCS | WA3492247 | Gwynlea Building, male toilet - Water leaking badly from cistern | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 16:30:00 | Pass | replaced faulty inlet valve , required trip to supplier
MSA-DCS | WA3492250 | Pilbara Wing, Shower Room Toilet- Water leaking badly from cistern | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 15:30:00 | Pass | installed new cistern supplied by nyandi
MSA-DCS | WA3492253 | Jasper, A Wing, lounge room- Air Con very noisy, not functioning correctly | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-08-04 12:00:00 | Fail | Replaced indoor fan motor and scroll as per quote, unit now runs correctly
MSA-DCS | WA3492268 | Jasper,A wing, Laundry - Aircon not heating | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-08-06 09:00:00 | Fail | Complete
MSA-DCS | WA3492525 | Panel alarm in zone 2 is activating and not clearing | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 21 Jul 2020 | 2020-07-21 13:53:26 | 2020-07-21 13:30:00 | Pass | Attended site unit 6 vesda 2 in low/high airflow fault. Checked vesda found pipes 2&3 in low airflow fault and pipe 4 in high airflow fault. Found pipe 4 c wing sampling tubes and vesda pipe broken at coupling, repaired and left normal. Cleared out all sampling points and tubes in c&d wings to clear low airflow faults on pipes 2&3. Left vesda normal when left site.
MSA-DCS | WA3492549 | Gate house, toilets blocked | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-21 14:00:00 | Pass | Clear blocked sewer using Jetter.
MSA-DCS | WA3492565 | metal house sockets damaged | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 10:27:09 | 2020-07-21 13:00:00 | Pass | Replaced data outlet
MSA-DCS | WA3492603 | Gate House, Door 6 inter sally port, electronic lock is not securing | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 11:00:01 | 2020-07-21 11:50:00 | Pass | Attended site and cleared out dirt from door 6 lock and latch. All cleared out,relubricated and tested ok. Job complete. Travel home
MSA-DCS | WA3492718 | Farm - old power pole has fallen onto new | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-21 15:30:00 | Pass | Removed damaged power pole
MSA-DCS | WA3492735 | control PTZ cameras 7,13,16,17,18,19,21 and 22 no pan or tilt | Hakea Prison | WSM-BR-RC | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-09-10 14:38:00 | Fail | Repaired multiple PTZ cameras after lightning strike.Parts used (SEME Stock)POE Injector PSU12V PSUConsumablesMounting Hardware
MSA-DCS | WA3492778 | Admin, Front entry veranda - roof leak | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-11-23 09:00:00 | Fail | ROOF AND VERANDAH REPAIRED
MSA-DCS | WA3492781 | Shared facilities, S/O training office - light faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-27 08:30:00 | Pass | Repair light in Training office
MSA-DCS | WA3492789 | Access road between control 7 kitchen - PTZ camera 10 inoperative | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 13:21:33 | 2020-07-21 15:00:00 | Pass | Attended site and investigated the fault.Checked DVM system - no video from PTZ 10.Found that fiber modem locatedcin EC cabinet is warm - switched off power and left unit to cool down.Reconnected power and tested.All back to normal and operational
MSA-DCS | WA3492809 | Amenities - East Air con too cold | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-08-05 15:30:00 | Fail | Completed leak check and repair as quote. Unit fully operational.
MSA-DCS | WA3492879 | Unit 2, A Wing, Cell A10- toilet is not flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-24 11:30:00 | Pass | Replaced leaking outlet rubber in cistern.
MSA-DCS | WA3492912 | market garden cool room faulty | Wooroloo Prison Farm | GMP-BR- HO | Refrigeration | Coolroom (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 15:13:05 | 2020-07-23 09:00:00 | Fail | COMPLETED
MSA-DCS | WA3492939 | Unit 3 C14 Cell Window Cracked | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 15:45:16 | 2020-07-22 14:30:00 | Pass | RE-GLAZE CELL WINDOW
MSA-DCS | WA3492943 | Unit 4, Cell C10- Cell Window Cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-08-03 12:30:00 | Fail | RE-GLAZED CELL WINDOW
MSA-DCS | WA3492944 | Unit 4, Cell C14- Cell Window Cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-08-03 13:00:00 | Fail | INSPECT & TEST ONLY - JOB FIXED ON THE 20/07 - JOB #WA3491041
MSA-DCS | WA3492947 | Unit 2, Cell C8- GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 13:30:00 | Pass | Replaced broken gpo
MSA-DCS | WA3492948 | unit 1 B11 GPO Loose and cracked | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 11:30:00 | Pass | Replaced gpo
MSA-DCS | WA3492949 | Unit 1, Cell B8- GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 12:30:00 | Pass | Replaced gpo
MSA-DCS | WA3492950 | Unit 4, Cell A9- Personal light smashed | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 14:30:00 | Pass | Replaced light switch
MSA-DCS | WA3492953 | unit 4 C14 Bed Light Switch melted | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 15:56:24 | 2020-07-22 10:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA3492966 | reception locking mech jammed on door | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 21 Jul 2020 | 2020-07-21 20:37:22 | 2020-08-07 11:30:00 | Fail | Attend site after hours open jammed lock and install temp. lock.Replace 4L42 lock and fixings.
MSA-DCS | WA3492978 | Unit 1 House 3 Elec door fail | West Kimberley Regional Prison | GMP-BR- HO | Building | Doors (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 18:23:00 | 2020-07-28 23:11:00 | Fail | Sourced C300688 from seme stock (HBus 16 in 16 out board)removed faulty Gbus device and installed new Hbus device, programmed to controller and reprogrammed inputs onto new expander.tested inputs and outputs and confrimed ok.
MSA-DTAG | WA3492248 | Custody control - HWS Leak | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 10:45:00 | Pass | COMPLETED
MSA-DTAG | WA3492531 | L5 family violence Zip Tap is not working – no hot water is coming out. Cold water works fine. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-21 13:37:00 | Pass | No hot water out of billi unit. Manually tried to run hot water out of pump but no response. Turned unit on and off, again nothing. Needs Billi warranty call out. Have spoken to Ian - returned and replaced free of charge new hot pump installed under Billi Warranty approved.
MSA-DTAG | WA3492570 | 1903, Basement- Lights not working in Judges chambers & possibly in corridor as well | Supreme Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-23 11:15:00 | Pass | Inspected faulty lighting and replaced light fittings due to age. Tested working
MSA-DTAG | WA3492826 | L11 female toilet is blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-23 11:00:00 | Fail | Complete
MSA-DTWD | WA3492099 | E block, corridor - Replace flashing lights | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 21 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 14:30:00 | Pass | Attended site and signed in. Located e block. Found flickering light in corridor. Replaced tubes and starters. Checked corridors throughout ground level. All okay. Job complete
MSA-DTWD | WA3492295 | Ground, walkway lights - replace all blown undercover walkway lights | Joondalup McLarty Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-22 09:30:00 | Pass | Replaced all passage way lights with new fluorescent globes
MSA-DTWD | WA3492303 | A Block, Door off expo- Door handle to fire exit opposite Security not working properly | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-21 14:20:00 | Pass | replace mortice lock body to stairwell door
MSA-DTWD | WA3492304 | T block cafeteria pie warmer will not heat | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 18:37:00 | Pass | Attended site and signed in. Located cafeteria pie warmer. Investigated to find no heat coming from fan force. Light working all okay. Dismantled control panel on back of unit. Inspected and tested to find broken/burnt cabling to element. Repaired and plugged back onto thermostat. Tested warmer to operate correctly. Job complete
MSA-DTWD | WA3492424 | C block ground floor cafeteria Asbestos sheet is damaged outside rear café door south side see note | Bentley Campus | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-27 09:00:00 | Fail | Removed and disposed of eave sheet and replaced with new, painted to complete
MSA-DTWD | WA3492576 | Lvl 6, West Wing - Investigate VAV Systems | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-30 15:54:00 | Fail | Attended site gained access and completed investigation of equipment. Confirmed Heating water valve operation at AHU. Level 6 located and checked VAVs. Office W606 staff found to have desk heater running. Causing potential fauls reading to occur at BMS. Hot water reheat found inactive for room W601 and W602. With up coming building BMS and controls gear upgrades. Site Facilities have advised not to investigate further. Work area has been left tidy and will be monitored. As a short term solution facilities as been advised to increase pre heat cycle on plant/equipment start up within the service areas.
MSA-DTWD | WA3492602 | E block, E75 Kitchen - no power to extraction unit, | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 1 | CLOSE | 21 Jul 2020 | 2020-07-21 14:14:26 | 2020-10-21 11:30:00 | Fail | Works completed as per BRAF
MSA-DTWD | WA3492626 | Lvl 2, First Aid Room- Water tap is faulty | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 12:50:00 | Pass | Replace specific tap for Steibel
MSA-DTWD | WA3492628 | A block - toilets blocked (male, female & disabled) | Murdoch Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-28 14:47:00 | Fail | Resolved major sewer issues Pump problems and blockages
MSA-DTWD | WA3492678 | B block L3 B2312 air con not working-see note | Bentley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 16:00:00 | Pass | Reset both units and cleared faults
MSA-DTWD | WA3492730 | C-Block walkway to steps, step pavers have come loose | Joondalup Kendrew Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 13:30:00 | Pass | Stair nosing pavers were loose. Removed, prepped and adhered with epoxy adhesive & mortar, and repointed edging.
MSA-DTWD | WA3492733 | B-Block pathway to entrance, replace/repair broken inspection cover lid | Joondalup Kendrew Campus | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-08-07 12:32:00 | Fail | Attended site, signed in, completed a JSA, cut concrete around pit, chiseled and removed concrete from surrounding pit, ripped old pit out and installed new, mixed concrete (rapid set) poured and levelled out. Cleaned surface around pit , Waited to set as it is a main walkway
MSA-DTWD | WA3492872 | block 3 ground Used oil holding tanks (2 off) Tanks number 8 and 12 need emptying | Thornlie Campus | GMP-BR | Waste Management | Waste Removal (WM) | Western Resource Recovery Pty Ltd | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-31 10:00:00 | Fail | SERVICE COMPLETE 24.07.2020
MSA-DTWD | WA3492876 | 6F, painting & decorating - wall and ceiling water damaged | Thornlie Campus | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-12-03 12:30:00 | Fail | Re-attended 21/8/20 Measured up for flashings to carry out further repairsSending roofing supervisor back to site to carry out further investigation Wed 26/8/20 21/9/20 - Waiting on quote from electrician 3/12/20 Re-attend site to complete wall panelling and paint. Existing panels had to have layers of paint removed to achieve consistent ceiling height.
MSA-DTWD | WA3492883 | 6F, painting & decorating - Water stain on ceiling | Thornlie Campus | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 21 Jul 2020 | 2020-07-28 17:00:00 | 2020-09-01 10:00:00 | Fail | Sealed up roof leak. Patched and painted water stain on ceiling.
MSA-DTWD | WA3492964 | Faulty lighting downstairs toilet/shower area - see notes | Armadale Campus? 45 Commerce Ave | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 15:30:00 | Pass | Replaced faulty Fluor tuebss and starters. Female shower. Ground floor.
MSA-DTWD | WA3492965 | C block CG04 classroom 2x water damaged ceiling tiles need replacing.-see notes | Carlisle Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 21 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-22 12:30:00 | Pass | Replaced 2 ceiling tiles
MSA-MRWA | WA3492613 | L2 kitchen Billi tap leaking please attend and remediate. | Road Network Operation Centre (RNOC) | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 21 Jul 2020 | 2020-07-22 17:00:00 | 2020-07-21 13:36:00 | Pass | Replaced inlet and dual solenoids
MSA-DCA | WA3493642 | Hand driers in female bathroom in the lvl 2 upper circle corridor. | His Majesty's Theatre-Theatre Building-Level 2-Upper Circle Female Toilets | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 13:30:00 | Pass | Hand dryer fixed.
MSA-DCA | WA3493648 | Hand driers in Male bathroom in the lvl 2 upper circle corridor. | His Majesty's Theatre-Theatre Building-Level 2-Upper Circle Male Toilets | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 15:00:00 | Pass | Hand dryer fixed
MSA-DCA | WA3493672 | Fire panel beeping unable to silence | His Majesty's Theatre-Theatre Building-Ground Floor-Stage Door Entrance Area | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 22 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 19:00:00 | Pass | Tech attended site as per P1 call out at 10am on Wednesday 22nd July. On attending site as a P1 priority it was advised that he could not carry out any works due to a show taking place in the building.Received a call from site at 1.30pm to advise that the show was over and that we could now attend to investigate the issueAttended site investigated faultsreplaced single batteries in 6 detectors 3.86 / 1.49 / 2.146 / 2.151 / 2.159 / 5.75 and 1 MCP had two batteries replaced 4.002EWIS went into fault - 3/4 of panel - reset Further investigation is required and a quote will be submitted
MSA-DCS | WA3493099 | Unit 2 officers toilet - exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-27 13:30:00 | Pass | Replace Unit 2 Officer's toilet exhaust
MSA-DCS | WA3493103 | Unit 2, Lower outside shower block - exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-27 15:00:00 | Pass | Replace Unit 2 outside shower block exhaust fan
MSA-DCS | WA3493111 | SITE COST control - middle monitor screen flickering off and on | Wooroloo Prison Farm | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Jul 2020 | 2020-07-22 11:38:40 | 2020-07-22 10:30:00 | Pass | Attended site.Checked IndigoVision system.Checked connections and settings on middle CCTV monitor.Power cycle DVM extender and conducted test.All ok at departure
MSA-DCS | WA3493120 | Unit 2, D wing - abloutions hot water not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 22 Jul 2020 | 2020-07-22 11:44:13 | 2020-07-24 10:30:00 | Fail | Replaced split pins in 2 x showers.
MSA-DCS | WA3493152 | Multiple houses on Driscal Drive have been broken into & damaged. Asses & remediate any damage found | Banksia Hill Detention Centre | GMP-BR- HO | Building | Internal Walls (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-23 12:00:00 | Pass | WINDOWS & DOORS SECURED
MSA-DCS | WA3493158 | Cyrenian Demountable - door closer damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-14 14:00:00 | Fail | new door closer fitted
MSA-DCS | WA3493243 | Unit 2, Cell A15- Broken Shower Glass & Mirror | Melaleuca Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Schlager Construction Group | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-07 15:30:00 | Fail | Attended site and assessed damage to shower screen.Replaced shower screen using 10mm safety glass.
MSA-DCS | WA3493244 | Front gate- Fire Alarm panel showing Fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-09-08 14:14:00 | Fail | VESDA fault resolvedLoop faults on gatehouse & reception/medical still unresolved see FSR notes
MSA-DCS | WA3493246 | unit 14, A1 - Bottom of window recess of shower is leaking onto bed | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-31 10:00:00 | Fail | SHOWER RECESS RE SEALED
MSA-DCS | WA3493253 | Social Visits, Entrance Double Doors- Lock jamming when closing | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 14:50:00 | Pass | job complete - Supplied and installed blocker plate to rectify issue.
MSA-DCS | WA3493268 | Front Gate, Entrance Door- Electronic Key lock ( Key Barrel not working ) | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-28 15:45:00 | Fail | Job completed - Gained entry to keyswitch. Temporary repair performed. Parts needed.On site 28/07/2020. Supplied and installed required parts.
MSA-DCS | WA3493271 | Official Visits, Door Beside Control Pod- Door Closer Broken | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-29 15:30:00 | Fail | Job completed - 24/07/20 Performed temporary repair. Replacement required.On site 29/07/2020. Supplied and installed replacement.
MSA-DCS | WA3493295 | Unit 1, C8 - the cell window has been damaged | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 13:45:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3493357 | Unit 3, B & D Wing Shower Block - window faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-27 12:00:00 | Pass | SPIRAL BALANCES & FEET REPLACED
MSA-DCS | WA3493360 | Unit 5, Tea Room- light not working (have already changed tubes & starter) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 11:30:00 | Pass | Checked damaged lights in unit 5. Ordered, picked up replacement fittings and installed
MSA-DCS | WA3493365 | Unit 6 - C Wing 2 Wing lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-23 11:30:00 | Pass | Repaired multiple faulty lights in unit 6 a and c wing landings
MSA-DCS | WA3493371 | Unit 1B, Camera 4 no reader | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Jul 2020 | 2020-07-23 10:36:10 | 2020-08-13 18:44:00 | Fail | Sourced BX420 HD from supplierremoved existing camera, installed new Indigo BX420, programmed and adjusted view as per control officer.confirmed recording on NVR 6.
MSA-DCS | WA3493384 | Kitchen freezer - Refrigerated container temporary | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Main Kitchen | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-18 10:10:00 | Fail | Completed temp freezer has been picked up
MSA-DCS | WA3493403 | control - PTZ2 view obstructed | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-22 15:35:00 | Pass | Black mark covering half the image,used boom lift to access camera and found deceased lizard trapped between camera and wiper.removed lizard and removed wiper as function not used.
MSA-DCS | WA3493417 | staff quarters burst water main outside | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Jul 2020 | 2020-07-23 11:19:17 | 2020-07-23 16:00:00 | Fail | repaired burst water main with repair band, trip to supplier was required
MSA-DCS | WA3493442 | main ground entrance steps Make good defect steps causing trip and slip hazard to main entrance | Nyandi Training Academy | GMP-BR- HO | Carpentry | Staircases, Balustrades and Handrails (CA) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-28 07:30:00 | Fail | DRAINAGE GROOVES CUT IN GROUT LINES ON STEPS
MSA-DCS | WA3493512 | Lenard office Under bench water cooler extreamly noisey and not working correctly | Banksia Hill Detention Centre | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-10 11:00:00 | Fail | System off on arrival. System really old and noisy. Could be the compressor or it could be the fan. Have removed unit to workshop to test. I have connected the filtered water straight to the faucet! 10.8.2020 - Re installed system, install PLV. All okay on departure, returned and reinstalled new Capex Asset IC8 Undersink Chiller - Serial number Manufacturers 19090248 New Programmed number A402011546
MSA-DCS | WA3493519 | Trainng room RHS gas heater not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-30 10:00:00 | Fail | Training Room RHS gas heater not working. Check heater & controls. Dismantle, remove pilot & gas control. Replace thermocouple. Assemble all & test. Report to staff.
MSA-DCS | WA3493523 | Nicol store room Light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 08:30:00 | Pass | Repaired light
MSA-DCS | WA3493534 | unit 1 D10 Light fitting broken/loose | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 12:30:00 | Pass | Remounted light
MSA-DCS | WA3493541 | Connect freezer unit to electrical supply | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Main Kitchen | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-22 15:00:00 | Pass | Supply power to temp freezer
MSA-DCS | WA3493544 | Unit 5, Cell C4- Cell window cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-04 11:30:00 | Fail | RE GLAZED CELL WINDOW
MSA-DCS | WA3493549 | Unit 3, Cell C14- Cell window cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-03 13:30:00 | Fail | INSPECT AND TEST - CRACK WAS ALREADY FIXED ON THE 22/07 - JOB WA3493549
MSA-DCS | WA3493560 | kitchen bun divider control stick attachment fault | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 18:30:00 | Pass | 24/07/2020Found handle was loose, tightened grab screw.Cleaned and lubricated unit.Re-tensioned return spring on oscillating base handle.
MSA-DCS | WA3493570 | Zone 4 omintrax constantly alarming | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-27 18:03:00 | Pass | Attended site, zone 4 alarms every 30 mins roughly.set magnitute plot and performed walk test. adjusted zone 4 and monitored.false alarms have stopped.tested zone and confirmed correct operation
MSA-DCS | WA3493573 | Unit 6, A6 - GPO Cracked | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 11:30:00 | Pass | Replaced blank plate
MSA-DCS | WA3493575 | Zone 11 omnitrax constantly alarming | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-27 18:06:00 | Pass | Checked report and found no false activation. tested zone to find no activations.checked UCM and confirmed alarm on senstar.checked Gallagher and found Alarm zone had been disarmed by Perimeter user 22/7/2020.removed override privileges from user.calibrated zones 9,10 and 11.
MSA-DCS | WA3493577 | Camera 31 Not working | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-10-14 07:21:00 | Fail | work order to be invoiced at cost. new work order will be released to complete job
MSA-DCS | WA3493583 | Unit 5, A12 - GPO Cracked | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 08:00:00 | Pass | Replaced gpo
MSA-DCS | WA3493585 | Camera 16 not working | West Kimberley Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-27 18:08:00 | Pass | Attended site, plugged CCTV tester into Camera from base of the pole, Image is clear. sent test signal back to Maxpro equimpment and found test signal is distorted.traced coax and found corroded BNC connection fibre modem side.re-terminated connection and monitored. confirmed clear stable image.
MSA-DCS | WA3493592 | Reed switch needs repairing Unit 2 house 2 | West Kimberley Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 23:10:00 | Pass | Attended site, checked all reed switches in Unit 2 House 2, replaced 3 reed switches and siliconed into place to prevent future problems.put remaining 3 reed switches into PFM stock
MSA-DCS | WA3493595 | Unit 5, A17 - 2x GPO Cracked | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 09:30:00 | Pass | Replaced gpos
MSA-DCS | WA3493613 | Unit 2, C10 - Lino lifting off floor | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-12-08 14:00:00 | Fail | DAMAGED AREAS OF VINYL UPLIFTED & NEW VINYL LAID
MSA-DCS | WA3493618 | Unit 2, C9 - Lino lifting off floor | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-12-07 14:30:00 | Fail | DAMAGED SECTION OF VINYL LIFTED & REPLACED WITH NEW VINYL
MSA-DCS | WA3493667 | gate control camera 27 PTZ 8 no pan tilt or zoom | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-22 14:00:00 | Pass | Attended camera Equipment Cabinet, found existing modem “hot to touch.” Replaced failed fibre modem with site spare, confirmed Pan, Tilt, Zoom functions with control and tested camera presets.
MSA-DCS | WA3493668 | Grounds, Bore Controller 2- electrical fault | Casuarina Prison | GMP-BR- HO | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-24 11:00:00 | Pass | Electrical burn out of wiring and amp meter. Electrical replacement and tested
MSA-DCS | WA3493694 | Camera 213 Not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2021-05-05 12:00:00 | Fail | Installed new POE injectorin unit1 House2.Programmed camera into system.Brought down ladder and adjusted camera.
MSA-DCS | WA3493696 | Max pro system freezing | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-29 09:17:00 | Pass | Checked system and maxpro keyboards in control, ICF and FV all inputs working
MSA-DCS | WA3493732 | upstairs office a piece if the ceiling tile is coming down-photo's to follow in email | Midland (North East Metro) | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 10:30:00 | Pass | Attended site and carried out repairs to the ceiling tile that was falling down.Touched up damaged ceiling tiles.
MSA-DFES | WA3493689 | north side of FS middle roller door spinning and not engaging | DFES Baldivis | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 22 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 16:30:00 | Pass | Following a full test and inspection of door components found roller door motor not aligned.Tech realigned door - all okay.Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3493700 | engine bay ground Fluro light in Engine Bay - south end making a buzzing noise | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-27 11:30:00 | Fail | Installed 5 x Emergency lights in Truck Bay
MSA-DFES | WA3493724 | Hallway outside main locker room.Floor Skirting Board has broken away from wall-see notes | CFRS Maddington | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 10:00:00 | Pass | Refitted skirting, patched and painted wall
MSA-DTAG | WA3493088 | Key not working on gate lock. Also check magistrates court doors | Midland Courthouse | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 22 Jul 2020 | 2020-07-28 17:00:00 | 2020-08-03 10:30:00 | Fail | supplied and installed restricted cylinders as per quotation sent to and authorised by Mario Kovac
MSA-DTAG | WA3493554 | ground female public toilet Last sink has leak underneath | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 07:48:00 | Pass | Tighten up retaining nut on waste and apply bead of silicone
MSA-DTWD | WA3493104 | Level 1, Beauty clinic - Tap water is leaking | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 22 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-24 12:53:00 | Pass | Fix boiling unit
MSA-DTWD | WA3493201 | D Block, A146- Service date Fault issues with BMS GreenSkills | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Building Automation & Electrical Services Pty Ltd | 3 | COMPFIN | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-29 00:00:00 | Pass | works completed - Work order to closed out at $0 cost
MSA-DTWD | WA3493272 | E block, Deli - the Anode for the Bain Marie does not work | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-22 13:35:00 | Pass | Arrived at site, checked element, drawing 11.5A.Checked the simmerstat, this is one I changed when the plug burnt out last time.Found it was coming on and off correctly as the dial was changed.
MSA-DTWD | WA3493274 | F block F1 sinks are blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-28 14:53:00 | Fail | Resolved isssues with pump and sewer pitSewer lines needed major jet machine work to unblock pits full with mop hairs and paper towels
MSA-DTWD | WA3493281 | N&P Block - Security lights not working between N&P Blocks. Red 2 RCD will not reset | Midland Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 14:15:00 | Pass | Attended site and signed in. Spoke with staff and was advised that the R2 circuit is in P block and won’t reset. Investigated to find 3 x faulty fittings. And 1 fitting isolated but not faulty. Also found pole light incorrectly wired to switchboard. Replaced 3 x faulty lights on exterior. Replaced circuit protection in pole light. Rewired correct lighting arrangements in switchboard to operate all external lights. Tested all lights working okay. Clean and tidy site. Job complete
MSA-DTWD | WA3493283 | Q Block, Room Q11 - Faulty GPO | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 13:00:00 | Pass | Repalced faulty fuse to red phase sub mains. Tested all working properly.job completed
MSA-DTWD | WA3493375 | Cateen Courtyard- Gate lock faulty | West One Services | GMP-BR | Security | Locksmith (SE) | DIAMOND LOCK AND KEY | 1 | FLDCOMP | 22 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-22 12:30:00 | Pass | replaced screws and lubricated locks
MSA-DTWD | WA3493377 | House 805 toilet leaking | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-23 11:30:00 | Pass | Job completed - Repairs to leaking toilet to House 5
MSA-DTWD | WA3493378 | K Block, K004(play room)- Broken fluro fitting | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 10:00:00 | Pass | Repalced faulty fitting in store room .job completed
MSA-DTWD | WA3493390 | K Block, K004.3 & K007.1 (Childrens' Bathrooms)- Seized Taps | Balga Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-11 15:45:00 | Fail | Replaced Tapware
MSA-DTWD | WA3493408 | Level 3, fashion classroom - Replace lights as reuired | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 22 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 14:00:00 | Pass | Signed in, completed jsa, set up work area , isolated lighting , replaced tubes and starters (12x18w tubes , 12x s2 starters, 9x36w tubes 9xs10 starters ) reenergised lighting, all now operational , packed up work area job completed
MSA-DTWD | WA3493634 | B Block, Storm water drain paving collapsed, walkway adjacent room B51 | Rockingham Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 09:38:00 | Pass | Fixed stormwater issues
MSA-DTWD | WA3493693 | End of BLD 835 first aid end Sewer Pit Lids Faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Lane's Plumbing | 2 | CLOSE | 22 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-03 17:00:00 | Fail | job competed - Sewer manhole coverbroken supply and install new sewer manhole cover
MSA-DTWD | WA3493713 | G Floor, West Block, Room W104- Female toilet is blocked | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 22 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-23 09:30:00 | Pass | unblocked toilet
MSA-MRWA | WA3493464 | plant room - loss of water to cooling towers please inspect and remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Air Conditioning | Cooling Tower (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 22 Jul 2020 | 2020-07-22 15:40:26 | 2020-07-22 14:00:00 | Pass | Quoting to replace
MSA-DCA | WA3493966 | Alarm activating in pump room, please check | State Library of WA-Main Building-Ground Floor-Fire Sprinkler Pump Room | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-23 12:40:00 | Pass | Attended site - investigated alarm in pump room - no alarm.Further research found sprinklers were being pumped up at this time 7:30am - 9am.
MSA-DCA | WA3494566 | External area - Isolate lighting circuit for ground light | Shipwreck Galleries | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-27 13:15:00 | Pass | Arrived at site at 8 to disconnect 9 floor lights due to them all full of water and remove 7 of the 9 light pits. Paving team didn’t have enough sand to do the 2 under the anchor so I left the pits in for protection. put wires in jboxes with silicon. Tested existing lights to see operating properly. Filled in paperwork informed management and signed out at 1315.
MSA-DCA | WA3494897 | VESDA unit intermittently beeping on various levels-see notes | Art Gallery of WA - James St-Administration Block (Block A)-Level One-AB1.04A - Plant Room | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 14:30:00 | Pass | Attended site liased with client and they advised that the bank of vesda remote displays had been intermittently beeping, when arrived all Vesda’s showing normal no faults or alarms.Checked history event logs and found there have been a intermittent code 24 fault 00619 on vesda l1 refernace plant room which is due to the vesda remote display not getting correct health signals back from vesda.Checked all connections on back of remote display and found some loose and reterminated. We have advised site to monitor and if fault returns we have recommended that the vlc remote display will need to replaced and the zone list will need to be rebuilt.(photo attached of remote display onsite if need to source parts from xtralis)
MSA-DCS | WA3493846 | unit 3 B wing - urinal leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-30 11:00:00 | Fail | Repair leaking urinal ..
MSA-DCS | WA3493847 | Unit 3, B wing - vanity taps faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-29 10:45:00 | Pass | Supply and install new basin set in unit 3 B wing.
MSA-DCS | WA3493892 | Unit 1, Front entrance - Main entry door is not responding from control room | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 07:39:53 | 2020-07-23 10:30:00 | Pass | Tested door from control, found intermittently the door would unlock correctly. Testedfrom Equipment Cabinet with same result. Removed Custodial strike lock from door frame and identified cable damage., insulation cut and cable exposed. Cut away damaged cable, reterminated lock connection plug, and tested lock operation. Lock released correctly, multiple tests.
MSA-DCS | WA3493951 | Main Kitchen - leaky roof, water coming threw a light fitting. | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 08:39:18 | 2020-09-03 14:12:00 | Fail | Attended site and cut access holes in ceiling so plumber can repair damaged water pipe.Reattended site and removed water damaged section of ceiling. Replaced damaged ceiling flushed and painted.
MSA-DCS | WA3493973 | Main Kitchen - leaky roof, water coming threw a light fitting. | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 08:35:17 | 2020-07-23 14:30:00 | Pass | Isolated water damaged light fitting
MSA-DCS | WA3493993 | Unit 4, 24 - shower taps leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-28 13:45:00 | Pass | Supply and install new taps in shower.
MSA-DCS | WA3494043 | Zone 6 - microwave in cosntant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Jul 2020 | 2020-07-23 13:11:59 | 2020-07-28 10:00:00 | Fail | Pickup part and travel to site to replace the faulty tamper switch and backup battery. Tested all ok after replacement.
MSA-DCS | WA3494064 | Unit 2 - A Wing cleaning room light is not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-23 15:00:00 | Pass | Repaired faulty lights in unit 2 cleaning stores
MSA-DCS | WA3494067 | Unit 6, C5 - Toilet will not flush properly, button has to be pressed right in & it only trickles | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-24 13:00:00 | Pass | Replaced leaking outlet rubber inside cistern.
MSA-DCS | WA3494069 | Unit 5 - B Wing Shower window wont stay up- bracket needs fixing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-27 13:30:00 | Pass | SPIRAL BALANCES & FEET RENEWED
MSA-DCS | WA3494077 | Unit 7 SCU ,D wing pantry doorlock & handle not working . | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 13:00:00 | Pass | Service and replace worn bolt throw in lock
MSA-DCS | WA3494080 | Kitchen - broken probe on first blast chiller not warranty as prisoner snapped it of | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 09:29:23 | 2020-08-07 16:30:00 | Fail | 23/07/20Called as requested to the probe cut through. Reconnected temporarily until a new one can be supplied and fitted. Parts required 1x core probe 04/08/20Called back to site the part required fitted tested all working correctly now.But the panel need to be silicone back in position.Parts required 1 x grey silicone 07/08/20Returned to site with the silicone sealed the conduit And the panel back in position.
MSA-DCS | WA3494082 | kitchen No3 and 4 ovens faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 09:30:52 | 2020-08-10 13:45:00 | Fail | Replaced all approved parts and tested ok
MSA-DCS | WA3494091 | Kitchen - No power going to the kettle not working at all. | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 0 | CLOSE | 23 Jul 2020 | 2020-07-23 13:35:07 | 2020-07-23 17:35:00 | Fail | 23/07/20 - Called as requested to the kettle not working. Found a safety switch stuck so free up tested ok. Also checked the operation due to reported scrapping noise. Found the mixing gearbox and motor loose so secured correctly and tested ok. Also checked the kettle next to as the mixer was not working but just needed to be reset. Left in full working order.
MSA-DCS | WA3494095 | Karakin A wing 3 x smashed windows Approx 1200mm x 450mm, 1 x smashed sash Approx 600mm x 450mm | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-24 10:30:00 | Pass | ALL WINDOWS REGLAZED
MSA-DCS | WA3494306 | Cleaning - Workshop Vaccum power cord has frayed exposed wires | Casuarina Prison | WSM-GR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-28 15:00:00 | Pass | Repaired damaged vacuums in cleaning workshop
MSA-DCS | WA3494316 | Unit 7 - A7 Toilet is running constantly..faulty cistern | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-24 14:00:00 | Pass | Replaced leaking outlet rubber in cistern. Adjusted flush button push rod.
MSA-DCS | WA3494345 | Gascoyne Unit - A6 shower water pressure non existing | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 12:15:00 | Pass | Repair shower head remove debris and restrictior
MSA-DCS | WA3494364 | Multiple systems failure | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 23 Jul 2020 | 2020-07-23 16:06:39 | 2020-07-23 18:00:00 | Fail | Attended site. Resotred Transponder 4 comms with MDAS server. Re-initialized Austco/CellGuard applications. Allsystems up and running.Job completed.
MSA-DCS | WA3494511 | Main Kitchen - leaky roof, hot water cylinder pipe in ceiling. | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 13:23:20 | 2020-07-23 16:00:00 | Pass | COMPLETED
MSA-DCS | WA3494526 | Unit 1 Control room Cell Call PA system working intermittently | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-09-04 14:00:00 | Fail | Job complete
MSA-DCS | WA3494547 | Perimeter between melaleuca and Hakea - damaged lock-see notes | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 13:35:49 | 2020-07-24 11:00:00 | Pass | Job completed - Assessed lock in sterile zone and serviced as required
MSA-DCS | WA3494585 | unit 5 B wing laundry room hot water system is leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 13:57:54 | 2020-07-24 08:30:00 | Pass | Inspected leaking hot water unit leaking from elements will need to be replaced booked in electrician for the morning24/7/20 Installed new hwu
MSA-DCS | WA3494605 | perimiter fencing microphonics fence joint is damaged | Greenough Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 14:08:14 | 2020-07-24 09:04:00 | Pass | Rectified and replaced damaged splice kits, job completed.
MSA-DCS | WA3494609 | Unit 2 computer UBS is faulty | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 14:10:54 | 2020-08-25 16:30:00 | Fail | Removed and replaced UPS in U2 SO office. Load tested ok. PARTS USED:APC smart UPS RT1000
MSA-DCS | WA3494645 | unit 2 plant room Gas Fired Boiler cutting out | Melaleuca Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 14:38:44 | 2020-08-01 13:30:00 | Fail | AMS661726 / WA3494645Melaleuca Prison Attend site to investigate fault on gas fired boiler and install new scanner. Return to site to install pilot gas valve.
MSA-DCS | WA3494650 | Lenard B wing cell #B08 toilet not flushing | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-24 15:40:00 | Pass | Replaved faulty solenoid in lenard b02
MSA-DCS | WA3494655 | Unit2 C and D wing Hot tap won’t turn off | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 14:42:56 | 2020-07-24 13:25:00 | Pass | Renew spindles to kitchen sink Wait 1 hour for escort
MSA-DCS | WA3494667 | unit 2 C and D wing kitchen 25L ZIP hot water urn running out of hot water after 5 cups | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 14:51:21 | 2020-07-24 14:47:00 | Pass | Recalibrate zip unit
MSA-DFES | WA3494259 | undercoft to court yard Door not latching.(door closer) | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-28 13:30:00 | Fail | Replaced door closer with new
MSA-DFES | WA3494369 | Main admin - UPS has failed | DFES Regional Office - Belmont | GMP-BR | Electrical | UPS System Maintenance (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 23 Jul 2020 | 2020-07-23 16:14:52 | 2020-07-24 13:45:00 | Fail | Already onsite. UPS not switching over from bypass mode. Spoke to APC support but unable to repair faulty. DFES need to update their service contract and get an APC tech to service UPS. Informed staff of situation.Site contact not comfortable leaving a rating. Unsure if works have been completed as he is not the one looking after the project and it’s out of his area of expertise.
MSA-DFES | WA3494615 | ground Hydrant Booster Cabinet is broken and needs repair-see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Building | General Building (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 14:45:00 | Pass | Install new hasp and staple to the door
MSA-DFES | WA3494913 | engine room non of the lights are working | DFES Baldivis | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-08-12 11:00:00 | Fail | First visit Attended site and located tripping lights in engine bay, found faulty light in equip emend store room. Isolated and will need to return to replace
MSA-DTAG | WA3493994 | L30 corridor Passage door leading to bathrooms – reader failure | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-11-04 11:00:00 | Fail | Attended site. As requested by Annette Marie on site, removed power to strike and reader for free access.Work completed
MSA-DTAG | WA3494020 | Downstairs Custody control only 1 screen of cameras is working in custody. | Armadale Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-23 15:15:00 | Pass | 23/7/20 - Dean Simpson, Joshua ParkInvestigated fault, screens were not configured for full screen mode. Set in full screen mode, and tested all ok.
MSA-DTAG | WA3494637 | Security check point - Bollard is loose needs re-securing | Rockingham Justice Complex | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-24 13:00:00 | Pass | RE SECURED BOLLARD
MSA-DTAG | WA3494691 | Swipe card entry from Court 3 waiting room not working. | Rockingham Justice Complex | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-24 13:00:00 | Pass | As per signature Slip no fault found
MSA-DTWD | WA3493861 | A block, Levle 1, A101E - repair lock | Leederville Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 23 Jul 2020 | 2020-07-23 17:00:00 | 2020-07-23 22:20:00 | Fail | Replace Broken Mortice lock
MSA-DTWD | WA3494060 | A block lift has working on L3 with students in it | East Perth Campus | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 23 Jul 2020 | 2020-07-23 13:16:06 | 2020-07-24 15:30:00 | Fail | No completion notes
MSA-DTWD | WA3494176 | Faulty roller blind – stuck in up position -see notes | Armadale Campus - 145 Jull Street | GMP-BR | Building | Windows (BU) | NEYLOR | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-08-14 13:27:00 | Fail | Completed & Invoice attached
MSA-DTWD | WA3494234 | 8,1st floor, Disabled cubical in ladies toilet - Water leaking from rear of bowl | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 16:27:00 | Pass | Fixed leaking toilet
MSA-DTWD | WA3494322 | North Block , levle 1, garage - Roller Door will not close | Perth Campus B1 | GMP-BR | Building | Roller Shutters (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-11-23 16:00:00 | Fail | Technician attended the site of North Metro Tafe Perth Campus to the Level 1 Garage Roller Shutter on 23/07/2020. Following a full test and inspection of door components found fault to be grifco sensor was damaged and tech did a temporary repair. Quote was declined. Full test and inspection of door function completed prior to leaving site.
MSA-DTWD | WA3494403 | K block fuel store entry door-Door will no fully close and will not lock , needs easing | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 11:00:00 | Pass | Liam Hanlon (28/07/2020) - Work NoteGet keys Unable to remove door as electrical lock wires running through back of door etc Remove kick plate and cut length down as binding on door frame Drill new holes and refit Grind concrete down Remove original closer Replace and fit new door closer Test and adjust speed Clean up
MSA-DTWD | WA3494529 | B30 water shut off tap Broken needs replacing | Murdoch Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 07:43:00 | Pass | Replaced isolation valve Tried to do so without isolating campus water supply but had to do early before staff got to site
MSA-DTWD | WA3494539 | classrooms J17, J16 - Skirting GPO’S faulty and loose x2 | Jandakot Campus - Annex | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 15:30:00 | Pass | Remounted damaged gpos. J16 and J17
MSA-DTWD | WA3494612 | B Block Ground Floor disabled toilet faulty door lock | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 09:00:00 | Pass | B Block - Ground Floor - Disabled toilet - door lock faulty.Lock repaired.
MSA-DTWD | WA3494642 | E block, ground SK2 - two front ovens tagged out , flame going out when in use | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-08-13 08:15:00 | Fail | COMPLETED 13/8
MSA-DTWD | WA3494656 | E block, Pavilion Restaurant bar area -Restaurant 2 leaking taps one with a hole in it (behind bar) | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 16:00:00 | Pass | COMPLETED
MSA-DTWD | WA3494657 | E block ground SK3 Bun divider, not rolling | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 15:30:00 | Pass | Completed 27/7
MSA-DTWD | WA3494660 | LEVEL 2, B207 - lights faulty require repairs/replacing | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 15:45:00 | Pass | Job complete
MSA-DTWD | WA3494689 | AT220 1st sink is blocked and overflowing in the male student toilets | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 09:40:00 | Pass | Unblocked Sink
MSA-DTWD | WA3494696 | Work shop AT240 & AT215 double glass doors gets pushed off the bottom central railing system | Kwinana Automotive Centre | GMP-BR | Building | Automatic Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 23 Jul 2020 | 2020-07-28 17:00:00 | 2020-08-05 14:00:00 | Fail | Repaired lock to glass sliding door
MSA-DTWD | WA3494904 | L2 art gallery faulty lights | Perth Campus B5 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 23 Jul 2020 | 2020-07-30 17:00:00 | 2020-09-21 13:00:00 | Fail | Arrived on site , signed in , completed jsa , Replaced 9x led downlights 280mm cutout to art gallery , used scissor lift to complete job (scissor lift where driver specified out the front on Aberdeen st key put in yellow bag ready to be picked up )**job completed ***
MSA-MRWA | WA3494546 | Temperatures very hot please investigate/remediate | Don Aitken Centre MRWA Head Office-Main Building-First Floor-Cafe Area | GMP-BR | Air Conditioning | Materials (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 23 Jul 2020 | 2020-07-24 17:00:00 | 2020-07-24 13:30:00 | Pass | Quoting repair works
MSA-DCA | WA3495684 | Ground Floor, FOH, mens stall - Urinal not flushing. | His Majesty's Theatre-Theatre Building-Ground Floor-Male Toilet | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-24 13:20:00 | Fail | Inspected and located why there is no water to urinals need to replace solenoids as the old ones arnt opening
MSA-DCA | WA3496070 | Lighting on the stairs leading down to the Library from the Admin Building Car Park is out. | Collection and Research Centre Welshpool-Administration and Library Building-Basement-Underground Carpark | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | Techworks Electrical | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 08:00:00 | Pass | Lighting circuit tripped in exit stair tunnel. Retested circuit and reset. No issues
MSA-DCS | WA3495312 | Perimetre Fence Alarms are going through the night. | Roebourne Regional Prison-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Jul 2020 | 2020-07-24 13:13:17 | 2020-07-24 12:45:00 | Pass | Call back to site to continue with fault finding. Confirmed with officer in control that all Zones secured after sunrise and warmed up and dried up the condensed water on the PE BEAM cover.
MSA-DCS | WA3495325 | Internal Perimtre fence- XRay alarms going off | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 05:41:39 | 2020-07-24 09:30:00 | Pass | Attended site checked and found Zone B2&B3 PE BEAM keep going off. Further check found a lot condensed water on PE BEAM covers. Cleanup the PE BEAM cover and tested alarm activated and reset correctly.
MSA-DCS | WA3495399 | Unit 10, B09 - roof leak | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 24 Jul 2020 | 2020-07-28 17:00:00 | 2020-11-23 09:00:00 | Fail | DAMAGED FLASHING REMOVED & REPLACED
MSA-DCS | WA3495410 | Unit 7, E18 - Cell toilet not working | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 07:10:22 | 2020-07-24 13:12:00 | Pass | Flush button was broken replaced and installed new outlet washer
MSA-DCS | WA3495413 | Reset Building - Sewer smell coming back through building | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 07:17:11 | 2020-07-24 14:04:00 | Pass | Inspection off all toilets and drainage signs off blockage in main drain all unblocked now
MSA-DCS | WA3495419 | Unit 7, E18 - Cell lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 07:18:55 | 2020-07-24 10:30:00 | Pass | Repaired light
MSA-DCS | WA3495426 | Unit 10, A05 - Hatch lock is loose and can be opened externally | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 07:20:20 | 2020-07-24 12:00:00 | Pass | job completed - Serviced hatch as required
MSA-DCS | WA3495428 | Unit 7, E4 - Aerial outlet smashed requires replacement/repairs | Hakea Prison | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Sapio Pty Ltd | 2 | CLOSE | 24 Jul 2020 | 2020-07-28 17:00:00 | 2020-08-03 08:30:00 | Fail | Attended site, earliest Escort Booking available. Replaced TV point and aerial cable in Cell E4, Unit 7.Job completed.
MSA-DCS | WA3495439 | SITE COST Unit 7, front door - top lock is sticing, can be unlocked from the otherside. | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 24 Jul 2020 | 2020-07-24 11:30:47 | 2020-07-24 10:00:00 | Pass | Replaced faulty cylinder on entry door into Unit 7 ( Old Nursery )New Cylinder built and keyed to Prisons System
MSA-DCS | WA3495490 | Meet PFM onsite on Monday 10am to investigate alarm panel communications error | Riverbank | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-27 10:45:00 | Pass | Job complete, see service report
MSA-DCS | WA3495491 | Meet PFM onsite on Monday 10am to investigate alarm panel communications error | Riverbank | GMP-BR- HO | Security | Monitoring (SE) | Automatic Fire Protection (ARA) | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-29 10:11:00 | Pass | Attended site and found system online and normal.Checked with FAMS and found that system hadn’t been of line but occasional fault with pstn back up line otherwise all normal.Issue was with link to security monitoring not fire - NFA required
MSA-DCS | WA3495547 | Unit 3, Block 2 - 4 xbroken windows | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 18:00:00 | Pass | HIGH LEVEL WINDOWS RE GLAZED
MSA-DCS | WA3495550 | Unit 3, Block 3 - 3 x broken windows requiring repairs/replacement | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-30 15:30:00 | Fail | ALL WINDOW RE GLAZED, RESET & RE SECURED FRAMEWORK
MSA-DCS | WA3495553 | Unit 3, block near office - repair 1x broken window | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-27 11:30:00 | Pass | RE GLAZED HIGH LEVEL WINDOW
MSA-DCS | WA3495562 | 2nd monitor the keyboard & mouse not working | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 08:23:29 | 2020-07-24 12:30:00 | Pass | Attended site and checked KVM power supply and all tested ok. Reset workstation and KVM set. Tested cat5 cabling and all tested ok. Reset monitor and repowered devices. All powered up and tested working ok. Job complete
MSA-DCS | WA3495573 | Zone 14, external perimeter trax not activating | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 08:34:51 | 2020-07-24 16:12:00 | Pass | Attended site, repaired multiple external perimitrax faults. Tested OKJob Complete
MSA-DCS | WA3495581 | Unit 3, Control Room- Carpet squares are loose, unglued & uneven. | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 08:32:31 | 2020-07-24 14:45:00 | Pass | DAMAGED/LOOSE CARPET TILES REPLACED /RESECURED
MSA-DCS | WA3495623 | Reset Building - kidsToilet is now overflowing and flooding | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 24 Jul 2020 | 2020-07-24 13:22:47 | 2020-07-24 12:20:00 | Pass | Kids toilet on rhs needed a new flush pipe fan cone to stop leak Toilet on lhs was leaking from mini stop and inlet valve was continue to run so replaced inlet valve mini stop and mini stop
MSA-DCS | WA3495624 | kitchen chip fry gas regulator faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 09:25:30 | 2020-08-24 11:30:00 | Fail | 24/07/20Attended kitchen Found two jets and burners blocked with oil.Cleaned jets and burners.Checked gas pressure, okTank has a small leak.Parts required 1 x Tank 24/08/20Installed fryer, altered hose connections and performed gas tightness test and checked burner pressure. Unit is operating to manufacturers specifications.
MSA-DCS | WA3495633 | Farm - electrical fault, trips out DAS Hot water for Pasteurizer | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 09:33:13 | 2020-07-24 17:00:00 | Pass | Investigate and repair tripping circuit at Dairy
MSA-DCS | WA3495670 | Unit 4 - B Wing Toilet not functioning in cell B10. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-27 13:00:00 | Pass | Replaced blocked inlet valve in cistern.
MSA-DCS | WA3495690 | Unit 10, Control Room- Smell emanating from ceiling | Hakea Prison | GMP-BR- HO | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 10:18:39 | 2020-07-24 13:45:00 | Pass | Carried out a service for rodents at Hakea Prison unit 10. There were reports of an odour coming from the roof void. Upon further inspection the dead rodent could not be located as there is minimal access into the roof void. Installed an odour bag as close as possible to the odour.
MSA-DCS | WA3495694 | Crypt, Front Entrance - please download footage from Crypt for Security | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-27 12:30:00 | Pass | Downloaded CCTV video as requested by Security Manager related to Ambulance vehicle in Prison, and searched multiple cameras for video of person of interest.
MSA-DCS | WA3495708 | Unit 2, B5 - pin has fall out of door | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 10:26:40 | 2020-07-25 10:00:00 | Pass | Replaced 2 x broken hinges on Cell B5 Unit 2
MSA-DCS | WA3495709 | Unit 1, B5 - lock is sticking | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 10:29:41 | 2020-07-25 09:00:00 | Pass | Adjusted lock strike and serviced cell lock to enable positve lockingUnit 1 Cell B5
MSA-DCS | WA3495716 | Perimeter zones B1 & C1 are constantly alarm even after been reset | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 10:33:28 | 2020-12-02 12:00:00 | Fail | Previous parameter change appears to have solved issue. Prison staff confirmed these zones no longer are alarming without cause and reporting confirms.
MSA-DCS | WA3495718 | PRU zones are not activating | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 10:36:06 | 2020-08-21 18:00:00 | Fail | This job completed on Work Order No. WA3658224
MSA-DCS | WA3495766 | Unit 13, Day Room- Boiling water unit not functioning correctly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 13:42:00 | Pass | Unit not filling correctly. Removed and cleaned level probes. Now filling correctly and fully to capacity.
MSA-DCS | WA3495773 | Unit 2, B & D Wing, Cell D2- toilet blocked (maybe an apple) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-27 11:30:00 | Pass | Plunged toilet to clear blockage
MSA-DCS | WA3495830 | Serpentine Kitchen- Faulty fan switch in Kitchen (attached to double power point) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 16:00:00 | Pass | Replaced faulty PowerPoint in serpentine kitchen
MSA-DCS | WA3495923 | Entry Foyer - Touch screen monitor on computer is not working | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 13:02:29 | 2020-07-24 14:00:00 | Pass | Reinstalled workstation monitor with new drivers for touch screen function as has lost its current driver file or became corrupt. All installed and tested ok with latest driver software. Job complete
MSA-DCS | WA3495973 | unit 1 hut showers hot water tap leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-29 11:45:00 | Pass | Supply and install new shower wall top assembly in unit one hut showers.
MSA-DCS | WA3495978 | Front door of entry building- Automatic security lock has failed | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 24 Jul 2020 | 2020-07-24 17:49:26 | 2020-07-24 16:00:00 | Pass | Attended site. Tested lock, tested ok. Tested override switch, tested okay. Traced issue to a Gallagher "Front DoorLock" Logic Block that wasn't active. Reset Logic Block. Tested all good.Job completed.
MSA-DCS | WA3496005 | Unit 2 - A Wing Leak on Drain pipe in Fire cabinet behind Awing. (Access from rear of Unit) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-18 15:00:00 | Fail | 27/7/20 - investigate job. Burst water pipe under concrete. Braf required to order parts and repair.11/8/20 - Escorted to job. Cut concrete. Exposed pipe. Located leak inside sealed sleeve within a 2m section . Unable to gain access via non- concreted end of pipe due to the position of soakwells and footings. Will need to rebook an escort to cut more concrete up to access pipe.18/8/20 - Escorted to job. Cut more concrete. Exposed damaged section of pipe. Repaired. Wrapped in denzo. Backfilled and reinstalled concrete.
MSA-DCS | WA3496013 | perimeter the cowling is not resetting | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 14:12:08 | 2020-07-24 17:15:00 | Pass | Attended site checked and found Zone 9 crawling alarm keeps going off. Recalibrate the crawling sensitivity and reboot control module. Tested it alarm activated and reset correctly.
MSA-DCS | WA3496014 | Front entry PA & call station- button doesnt open the gate | Broome Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-29 19:18:00 | Fail | Sourced 8in 4 out expander from WKRP (PFM stock)Replaced cable from lock to Gallagher controller in gatehouse. Used 7 core underground rated cable from seme stock.Installed expander and programmed door lock into gallagher
MSA-DCS | WA3496017 | Gate house, control room - shows gates open but is not open | Broome Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-31 16:09:00 | Fail | Door recently replaced. Reed swith not screwed in. And corroded.Removed old reed switch and resistors.Re-terminated 10k resistors and mounted new reed switch
MSA-DCS | WA3496019 | Garments Could you please repair damaged cord on cutting machine. | Casuarina Prison | WSM-GR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 15:00:00 | Pass | Repaired damaged cutting machines in garments
MSA-DCS | WA3496075 | Unit 2 D2 blocked drain | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 16:00:23 | 2020-07-24 20:20:00 | Pass | Unblocked drain
MSA-DCS | WA3496077 | Reception Medical building fire panel Loop 3 ground fault-Circuit in fault | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 24 Jul 2020 | 2020-07-25 16:08:49 | 2020-09-08 14:16:00 | Fail | Attended site for fault in fip. Upon arrival found 2x earth loop faults present on loop 1 and 3. After investigation, informed staff that works willare required to be carried out by 2 techs to rectify.29/7/20 KS JNWorked on loop 3 earth fault traced to module in security panel output on loop 3 module 74.Possibly faulty module FDMR-1 will require a revisit with module to see if module is causing fault or input from security.8/9 KS GAReturned to site and fitted new module to device 3074 as previously found faulty and found earth fault to now be clear.
MSA-DFES | WA3495831 | Station Deliveries Door (In) Push button combination lock faulty-see notes | CFRS Wangara | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-27 13:45:00 | Pass | Code lock working correctly =, adjusted door hinges & strike - would recommend the door needs replacing
MSA-DFES | WA3495842 | L2 Room 6 LIGHT SWITCH TO BALCONY LIGHTS NEEDS REPLACING, MECHANISM broken on switch | CFRS Fremantle | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 13:45:00 | Pass | COMPLETED
MSA-DFES | WA3495964 | Gym extension ground Electric hot water system in laundry not working | CFRS Canning Vale | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 15:15:00 | Pass | Investigate no hot water located laundry Remove cover of steible eltron HWU and test for power supply and reset buttonIsolate water mains to property and remove HWU off wall to remove hot and cold inlets to check and clean filtersOnce filters cleaned re-install and turn mains back on, check for leaks and test operation HWU will need replacing and job raised Take all relevant information and photos Pack up and clean up work site
MSA-DTAG | WA3495662 | L10 Store room door – reader failure | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-18 14:30:00 | Fail | Investigated and reset lock & re-programmed.
MSA-DTAG | WA3495672 | Level 5, Family Violence Office - Storeroom door lock is faulty | Central Law Courts | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-27 09:45:00 | Pass | Attended site, presented with a locked door on Abloy.Latch was jammed and unable to unlock door.Gained entry, and replaced mortice lock and cylinder.2x keys given to admin staff.
MSA-DTAG | WA3495710 | Custody Hallway- Door release not functioning, see further notes below | Perth Children's Court | GMP-BR-HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-24 14:30:00 | Pass | Custody Door not working. Checked & found no voltage at locks. Found PSU faulty no voltage coming out. Rerouted cabling to another PSU. Tested operation and all is ok.
MSA-DTAG | WA3495824 | 1903 room 220 ladies toilet leak coming from underneath tiles | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 24 Jul 2020 | 2020-07-24 16:00:31 | 2020-08-03 08:10:00 | Fail | Fix leaking WC.
MSA-DTAG | WA3495845 | L10 card readers continuously beeping | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 13:00:00 | Pass | Reprogrammed Readers on Level 10 and checked. All ok.
MSA-DTAG | WA3496049 | Registry of Births, Deaths and Marriages- Lighting issues listed below | Westralia Square | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 24 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-27 16:30:00 | Pass | Job complete
MSA-DTWD | WA3495394 | E block, Level 2, E200 - Replace/repaire light | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 24 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-27 08:00:00 | Pass | Attended site and signed in. Located e200. Found light out in office. Replaced tube and starter. Found light flickering in hallway. Replaced tube and starter. Tested all okay. Job complete
MSA-DTWD | WA3495548 | G Block, Room G129- Male toilets, last cubicle blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-29 16:00:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3495608 | ICT servers are losing power | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 24 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 15:00:00 | Pass | Checked and tested the power. Found no fault. Site overloading the UPS. Identified ways to balance the load. Site happy.
MSA-DTWD | WA3495626 | Extraction in A316 not working effectively | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | Precise Air Group | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-09-02 15:03:00 | Fail | Attended site and inspected exhaust fan serving room a316.Found exhaust fan 14 not operating.Carried out tests and found motor is tripped on overload.Reset and tested.Found amp draw within spec and motor running ok.Found motor bearings noisy and beginning to fail which may have caused trip.Also found the fan is out of balance and causing vibrations.Recommend replacing fan deck.Picked up parts from office.Attended site and accessed roof.Isolated power to exhaust fan system.Replaced exhaust fan system and contactor overload.Confirmed correct operation.Cleared debris from site and removed old fan system.
MSA-DTWD | WA3495656 | Level 1, Facilities Entrance - Roller Door not closing | Perth Campus B1 | GMP-BR | Building | Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-27 10:45:00 | Pass | Attended site, found door not closing correctly, reset door & realigned curtain, tested operationseveral times, tested all ok. If problem is ongoing the 35 year old door operating system mayneed upgrading
MSA-DTWD | WA3495728 | C Block, West entry auto door beeping, showing wire fault | Joondalup Kendrew Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-24 16:05:00 | Pass | Arrived onsite and signed in, located door and found controller in sensor wiring fault checked sensors and found the external sensor dirty with cob webs and dust over the circuit board and cleaned, reset controller and tested operation all correct.
MSA-DTWD | WA3495772 | D block ground lift starts moving up then stops and jolts, lift now not level with floor | Joondalup Kendrew Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 24 Jul 2020 | 2020-07-27 17:00:00 | 2020-07-24 16:00:00 | Pass | job completed - covered under contract. No charge to be applied
MSA-DTWD | WA3495817 | Q Block, lift the emergency phone is not working | Joondalup McLarty Campus | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 24 Jul 2020 | 2020-07-27 17:00:00 | 2020-08-14 16:00:00 | Fail | Job completed - RETURNED FOR FOLLOW UP INSPECTION FOUND LIFT BACK IN SERVICE WITH STILL NO LINE CONNECTION FURTHER TECHNICAL INVESTIGATION FOUND GSM NOT PLUGGED IN PICS SENT TO BUILDING MAINTENANCE AND SUPIVISOR PLACED BACK TO NORMAL SERVICE AS REQUESTED BY CUSTOMER.Stephanie Edwards from Kone confirmed no charges
MSA-DTWD | WA3495836 | Main Entrance- Lights not working | Perth Campus B5 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-10-07 15:45:00 | Fail | Attended site, signed in, located lighting to be replaced, completed jsa, isolated lighting circuit,removed old lights, replaced with 2x led fittings, tested , working correctly,cleaned up work area,completed paperwork,signed out , braf list now completed ***job completed ***
MSA-DTWD | WA3495893 | E block E30 Small Scale Kitchen – Faulty tap at station 12 | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-24 14:39:00 | Pass | Fix taps
MSA-DTWD | WA3495902 | A block A038 & A208 window blinds have broken from their fittings | Joondalup Kendrew Campus | GMP-BR | Building | Windows (BU) | NEYLOR | 2 | CLOSE | 24 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-14 13:18:00 | Fail | Work Completed and invoice attached
MSA-DTWD | WA3496045 | F Block, Male Toilets – Auto Flush on urinals not working | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 24 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-04 11:00:00 | Fail | Replaced solenoid after needing to order part inThought I had started job on promap when I put wait for paints
MSA-DCS | WA3496129 | SITE COST Unit 3 evolution, sewer is flooding, drainage blocked | Wooroloo Prison Farm | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 25 Jul 2020 | 2020-07-25 15:30:56 | 2020-07-25 14:00:00 | Pass | job done
MSA-DCA | WA3499752 | fire panal fault alarm | State Library of WA | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 26 Jul 2020 | 2020-07-27 15:50:25 | 2020-07-27 07:45:00 | Pass | Investigated FIP fault - intermittent fault due to the age of the system. Reset.
MSA-DCS | WA3499681 | SITE COST Bandyup Prison- U 3 -C 3, Infrared camera is not working | Bandyup Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jul 2020 | 2020-07-26 11:08:53 | 2020-07-26 10:15:00 | Pass | Attended site checked and found customer complaints Unit 3 Cell 3 Camera night view not clear. Simulated night time conditions by blocking all the light sources and turn off TV. Confirmed with officer in control night view is clear. Go through footage found a short time ( two three minutes) cell is dark. Except that whole night footage is clear. Can’t see too much problem. Advised customer call again if problem still happens.
MSA-DCS | WA3499689 | Entry control intercom - the talk button is not working. | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Jul 2020 | 2020-07-27 08:32:59 | 2020-07-26 12:45:00 | Pass | Restart and Refresh the 3210 ,tested ok. Job completed.
MSA-DCS | WA3499691 | No hot water working in the ZIP tap in Visit's kitchen | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 26 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-12 10:36:00 | Fail | replaced parts and filter as per quoteREPLACEDFILTER - INLET SOLENOID KIT, LEVEL SENSOR AND WIRING LOOM ASSY, DISPENSER XL TAP, PLV 500KPA BILLI PARTS
MSA-DCS | WA3499701 | Hakea Prison - In control room main alarm screen is down | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jul 2020 | 2020-07-26 13:30:14 | 2020-07-26 11:15:00 | Pass | Power cycle ws pc. Job completed.
MSA-DCS | WA3499703 | Gatehouse- CCTV monitors are not working around the gatehouse doors | Wooroloo Prison Farm-Gatehouse | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jul 2020 | 2020-07-26 13:29:24 | 2020-08-07 12:30:00 | Fail | Attended site and replaced monitor with new VGA extender set. All installed and working ok, reconfigured camera layouts and also adjusted for correct resolution settings. All tested and working ok. Job complete
MSA-DCS | WA3499732 | Unit 2- bad water leak from the service duct between B7 and B8 | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 26 Jul 2020 | 2020-07-26 16:08:33 | 2020-07-26 14:45:00 | Pass | job done
MSA-DCS | WA3499751 | MAINGATEHOUSE- Pump house is in alarm. Cannot be isolated. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Fire Protection Services | Fire Protection - Fire Brigade (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 26 Jul 2020 | 2020-07-26 19:29:53 | 2020-07-27 14:02:00 | Fail | Hakea prison.Pump fault.Pump 1 is failing to start on drop of pressure and manually. System is loosing pressure quickly and jacking pump continually running which keeps pressure at 800kpa. I have isolated the crank on pump 1 and will need pump tech to attend. Batteries also require replacement as they have failed2x 12V/90AH.27/7/20Attend site to investigate diesel pump not starting- found number one cylinder valve damaged, further inspection after removing cylinder head catastrophic has sustained internally requires a new Diesel engine.Found check valve in jacking pump discharge pipe bypassing causing the pressure loss, fitter to attend to replace valveMH ASArrived on site and pulled apart copper pipe work on jacking pump suction sideRemoved 25mm check valve and installed new check valve with galv pipe. No y strainer before the jacking pump previously reported and defected, one should be installed to prevent debris getting blocked in jacking pump causing failure to operate
MSA-DCS | WA3499760 | Greenough Regional Prison - Unit 2 - Cell 17 - PRA goes into constant alarm. | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Jul 2020 | 2020-07-27 17:46:04 | 2020-08-07 09:32:00 | Fail | Investigated and repaired all PIR faults.Job Complete
MSA-DCS | WA3499761 | Greenough Regional Prison - Zone 2 and 11 - Microphonics constantly going into alarm without cause. | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jul 2020 | 2020-07-27 01:49:00 | 2020-07-28 16:00:00 | Fail | Attended site.Checked microphonics cable for any damage and replaced missing cable ties in zones 2 and 11 outer.Replaced two damaged splice kits ( supplied by SEME).Checked EOL.Checked Senstar modules.Conducted test.All back to normal and operational.
MSA-DCS | WA3499762 | Greenough Regional Prison - Zones 6,8,9 and 13 - OmniTRAX going into constant alarm. | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Jul 2020 | 2020-07-27 01:50:42 | 2020-07-30 17:30:00 | Fail | attend site & recalibrate multiple zones as required. tested all zones ok. job complete.
MSA-DCS | WA3499772 | Cameras in gate control room, 3 monitors shutting off | Greenough Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Jul 2020 | 2020-07-27 23:01:36 | 2020-07-31 13:27:00 | Fail | Sourced parts, attended site, Investigated multiple display faults in control room. Repaired faults and monitored for correct operation.Tested OKJob Complete
MSA-DCA | WA3500213 | Level 1, Male Change Room- Urinal blocked, Water not running away | Art Gallery of WA - James St-Administration Block (Block A)-Level One-AB1.30 - Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 13:10:00 | Pass | Tryed to get drain machine down urinal didn’t fit bent up some copper to get down couldn’t reach anything causing blockage tryed to find downstream off urinal no luck so sucked out water and paper and what looked like paper towel and put down 1lt off acid and left for 30mins seems to be clear atm
MSA-DCA | WA3500388 | Entrance at PCC entrance Automatic entrance doors not closing -see notes | State Library of WA-Main Building-Ground Floor | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 27 Jul 2020 | 2020-07-27 14:18:44 | 2020-07-27 12:10:00 | Pass | Found floor guide broken causing door to jam, replaced floor guide and checked over door all ok
MSA-DCA | WA3500609 | Lift 2 Exhaust fan not working in lift 2 (public access lift)-see notes | State Library of WA-Main Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-28 13:00:00 | Pass | Not chargeable
MSA-DCA | WA3500634 | Graffiti on Centenary Gallery window, facing staff carpark | Art Gallery of WA - James St-Centenary Gallery-Ground Floor | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 15:00:00 | Pass | Job completed - removed graffiti from various location using paint and other chemicals
MSA-DCA | WA3500677 | External theatre terrazzo wall, by Francis St.- Graffiti on wall | State Library of WA-Main Building-Ground Floor-GF06 - Theatre | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 11:30:00 | Pass | removal of Graffiti
MSA-DCA | WA3500830 | Fire Panel – Western Entrance Intermittent fault on Fire panel-see notes | DO NOT USE TO BE DECOMMISSIONED A Shed, Victoria Quay, Fremantle-A Shed-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-27 15:15:00 | Pass | Investigate fault. Earth fault. Further investigation required.
MSA-DCS | WA3499838 | Unit 2 C-D Wing Internal Air Lock Door Aluminium Door Jamming in Frame-see notes | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 27 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 15:45:00 | Pass | job completed - service lock, adjust as required to allow correct locking operation.
MSA-DCS | WA3499887 | Jeelia B wing kitchen oven is smoking and making strange sound | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 27 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-13 08:35:00 | Fail | Cut back cable, reconnect ok
MSA-DCS | WA3499890 | Fire pumps running over the weekend. Please attend site and check tags on all fire hose reels. | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-05 11:30:00 | Fail | nil
MSA-DCS | WA3499977 | zones 3,4 and 13 lights have been reported as not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 15:00:00 | Pass | Fixed perimeter light
MSA-DCS | WA3499993 | Unit 15 - C Wing Please check the wiring to cell C 11.-see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 27 Jul 2020 | 2020-07-27 12:03:56 | 2020-07-27 12:00:00 | Pass | Tested cell c11 for shock received in weekend. All ok. Report to western power.
MSA-DCS | WA3500002 | Unit 1 - C3-Metal spiral runners in the cell window have been pulled out and need repair. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-10 15:00:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3500009 | Unit 1 - A4 Window need to resealed | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-13 11:45:00 | Fail | CELL WINDOW SURROUND RE SEALED
MSA-DCS | WA3500038 | kitchen leaking tap | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 12:00:00 | Pass | COMPLETED
MSA-DCS | WA3500040 | Unit 14, A & C- Cell A13, Sink & toilet is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 11:30:00 | Pass | 29/7/20 - Basin plunged to clear blockage. Cistern requires new part which needs to be ordered in.31/7/20 - Collected parts offsite. Installed new part inside cistern. Tested.
MSA-DCS | WA3500044 | Unit 6, Cell A7- Flush system will not stop running water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-27 15:00:00 | Pass | Replaced leaking outlet rubber and tested
MSA-DCS | WA3500047 | Unit 5, A Wing, Cell A8 - Floor drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 08:30:00 | Pass | Removed paint and plunged floor drain to clear blockage
MSA-DCS | WA3500049 | Unit 5, A Wing, Cell A3 - Tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 09:30:00 | Pass | Replaced leaking spindle in basin tap
MSA-DCS | WA3500055 | Unit 1, A Wing, Cell A9- Tap leaking in basin | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 09:30:00 | Pass | Tested tap and toilet multiple times. No issues found
MSA-DCS | WA3500056 | Unit 1 - B2 Runners come out of the sides of the window and wires are showing. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-04 12:45:00 | Fail | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3500064 | unit 2 C and D wing kitchen 25L ZIP hot water urn running out of hot water after 5 cups | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 08:37:20 | 2020-07-27 14:55:00 | Pass | Unit completely blocked and requires filter and unit check waited for it to refill and get to temp. All okA403540491 Zip Autoboil 25L BWU
MSA-DCS | WA3500066 | kitchen various lights out | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-21 10:00:00 | Fail | Replaced 7x faulty lights with LEDs
MSA-DCS | WA3500072 | Unit 14, A Wing, Cell A1 - Base of toilet is leaking into shower recess | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-04 11:30:00 | Fail | 28/7/20 - Investigated job. Braf required to order parts and repair leaking toilet.29/7/20- Braf approved. Parts ordered and job booked in for 4/8/20 @ 8:304/8/20- Collected parts offsite. Removed leaking pan. Installed new pan and tested. Cleaned up and disposed of rubbish.
MSA-DCS | WA3500076 | Unit 2, B Wing, Cell B2- water leaking from pipe under sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 08:30:00 | Pass | Replaced leaking spindle in basin tap
MSA-DCS | WA3500082 | Unit 6, Cell D10- Sink had previous crack and now has broken in half | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 08:43:46 | 2020-08-12 10:30:00 | Fail | 27/7/20 - investigate job. Basin requires replacement. Braf required to order parts and repair.12/8/20 - parts collected offsite. Old basin removed. New basin installed and tested. Rubbish removed.
MSA-DCS | WA3500083 | Unit 1 C5 Small holes have been dug into the cell wall above the bottom bunk and requires filling | Casuarina Prison | GMP-BR- HO | Building | Foundations (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-10 14:15:00 | Fail | ALL HOLES FILLED/PATCHED
MSA-DCS | WA3500087 | Unit 12, A & C, Cell HA14- toilet cistern is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 10:30:00 | Pass | Replaced inlet valve and outlet rubber in cistern. Tested
MSA-DCS | WA3500089 | Unit 4, Numerous lights are out | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-21 11:00:00 | Fail | Replaced pe cell
MSA-DCS | WA3500090 | Unit 1 - B8 window appears to be twisted and does not operate properly. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-13 10:00:00 | Fail | SPIRAL BALANCES TO CELL WINDOW REPLACED
MSA-DCS | WA3500095 | Unit 4, Cell I36 - hand basin broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-18 13:04:00 | Fail | Replace with new vanity and basin, due to plastic basin having burnt marks from cigarettes.
MSA-DCS | WA3500096 | it 3 - C6 window does not open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-06 11:15:00 | Fail | RE-NEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3500099 | Unit 4, cell A3 - exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 10:00:00 | Pass | Investigate unit 4 cell A3 exhaust fan.Requires replacement.Source parts.Replace unit 4 cell A3 exhaust fan.
MSA-DCS | WA3500101 | Unit 2, Cell 80- exhaust fan not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 08:30:00 | Pass | Investigate unit 2 cell 80 exhaust fan.Fan requires replacement.Source parts.Replace unit 2 cell 80 exhaust fan.
MSA-DCS | WA3500106 | Unit 3 - C8 window does not open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-06 12:15:00 | Fail | RE-NEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3500107 | Unit 6, B & D Day Room- Window winding mechanism broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 11:30:00 | Pass | NEW WINDER MECHANISMS FITTED
MSA-DCS | WA3500109 | Unit 3, Cell A1 - light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 08:30:00 | Pass | Investigate and repair unit 3 cell A1 light
MSA-DCS | WA3500110 | Unit 3, Cell A10- light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 10:00:00 | Pass | Investigate and repair unit 3 cell A10 light
MSA-DCS | WA3500112 | Unit 3, Cell A12- light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 11:30:00 | Pass | Investigate and repair unit 3 cell A12 light
MSA-DCS | WA3500114 | Unit 4 - B & D door handle\knob faulty | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-24 13:00:00 | Fail | RE SECURED LOOSE DOOR HANDLE/KNOB
MSA-DCS | WA3500117 | Unit 3, Cell D12- light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 13:00:00 | Pass | Investigate and repair unit 3 cell D12
MSA-DCS | WA3500121 | Abattoir- No 2 Fridge door rusted & seperating | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-09-09 16:00:00 | Fail | Essential Ref. attended , found rusted and faulty door on fridge, order new door and replace
MSA-DCS | WA3500123 | Unit 1, Cell A2- Fire damage to cell floor | Casuarina Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-21 10:00:00 | Fail | 06/09/21 - closing job cost to date as site not given us response on access - cost is labor only for inspection
MSA-DCS | WA3500130 | Unit 2 - B & D Window in B/D dayroom missing winder. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-10 13:30:00 | Fail | INSTALL NEW WINDOW WINDER
MSA-DCS | WA3500141 | Unit 2, A & C- Shower area window needs repair | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-10 12:30:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3500142 | Unit 2, B & D- Shower area window needs repair | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-10 11:30:00 | Fail | RE-NEW SPIRAL BALANCES
MSA-DCS | WA3500145 | Unit 14 - A Wing Cell A11 outside light switch needs replacing, wires exposed. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 09:08:04 | 2020-07-28 08:30:00 | Pass | Replaced damaged switch in a11 unit 14
MSA-DCS | WA3500146 | Unit 2, Cell A11 - Broken window fittings | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-05 10:45:00 | Fail | RE-NEW SPIRAL BALANCES
MSA-DCS | WA3500149 | Unit 2, Cell A4 - Broken window fittings | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-05 10:00:00 | Fail | RE-NEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3500151 | Unit 2, Cell D9 - Broken window fittings | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-07 08:45:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3500153 | Unit 2, Cell D10 - Broken window fittings | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-07 11:15:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3500155 | Unit 2, Cell A2 - Broken window fittings | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-05 09:00:00 | Fail | RE-NEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3500156 | Unit 2, Cell D12 - Broken window fittings | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-07 10:15:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3500158 | Unit 1 - A Wing Globe in bunk light cell A4 top bunk not working. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 10:00:00 | Pass | Repaired faulty lights in unit 1 a4
MSA-DCS | WA3500161 | Kitchen, Sink near C2- Hot water tap not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 10:15:00 | Pass | Renew detention spindle to kitchen hot
MSA-DCS | WA3500162 | Unit 2, Cell B13 - Broken window fittings | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-05 11:30:00 | Fail | RE-NEW SPIRAL BALANCES TO WINDOW
MSA-DCS | WA3500165 | Unit 13 - B Wing personal cell light switch in B8 not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 08:30:00 | Pass | Repaired faulty lights in b8 unit 13
MSA-DCS | WA3500166 | Unit 1, Cell B7, cell call very hard to hear, blockage can be seen in speaker holes | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 12:30:00 | Pass | On arrival found cell call speaker grill completely obstructed (by toothpaste). Drilled out retaining Rivets, removed cell call from cell, stripped down, cleaned reassembled and returned to cell. Tested cell call to Gate Control, good audio both ways. Riveted Cell call unit in place
MSA-DCS | WA3500184 | CCU (11), Observation cell 4 monitor is grainy | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-10-23 08:15:00 | Fail | Monitor to be replaced under - WA3701508 - No further works required under this WO
MSA-DCS | WA3500187 | Amenities - Male Gym Powerpoints in mens changing rooms require attention and testing | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 08:30:00 | Pass | Checked and tested circuits in amenities. No issues found, working as intended. Possibly overloaded by the bathroom iron and steam cleaner
MSA-DCS | WA3500188 | Unit 2, Cell D1- Cell call very faint & not clear | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 11:00:00 | Pass | On arrival, cell call unit speaker grill compleatly obstructed. Drilled out retaining Rivets, removed cell call from cell, stripped down, cleaned, reassembled and returned to cell. Tested with Gate Control, good audio, both ways.
MSA-DCS | WA3500190 | Unit 2, Cell D2- Cell call very faint & not clear | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 13:30:00 | Pass | On arrival, cell call unit speaker grill compleatly obstructed. Drilled out retaining Rivets, removed cell call from cell, stripped down, cleaned, reassembled and returned to cell. Tested with Gate Control, good audio, both ways.
MSA-DCS | WA3500191 | Unit 2, Cell D4- Cell call very faint & not clear | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 10:00:00 | Pass | On arrival, cell call unit speaker grill compleatly obstructed. Drilled out retaining Rivets, removed cell call from cell, stripped down, cleaned, reassembled and returned to cell. Tested with Gate Control, good audio, both ways.
MSA-DCS | WA3500192 | Unit 2, Cell D11- Cell call very faint & not clear | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 15:30:00 | Pass | On arrival, cell call unit speaker grill compleatly obstructed. Drilled out retaining Rivets, removed cell call from cell, stripped down, cleaned, reassembled and returned to cell. Tested with Gate Control, good audio, both ways.
MSA-DCS | WA3500195 | Metal Shop- electric cord on the hand grinder is exposed | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 15:00:00 | Pass | Repaired damaged grinder in metal shop
MSA-DCS | WA3500198 | Unit 1, A & C- Hot water dispenser is leaking water from underneath main body of unit & down the wal | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-28 11:50:00 | Pass | Checked unit and no sign of leak. No one on site aware of issue. Also checked unit in B/D dayroom in case was reported incorrectly. But no issue with this unit either. A40189253L and A40336910 both checked
MSA-DCS | WA3500232 | Swipe door entry way - Light not automatically turning on | Walcott Centre (Central West Metro ) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 10:45:00 | Pass | Repaired lighting in entry and office.
MSA-DCS | WA3500248 | Unit 1, B Wing day room- Zip hot water unit not working | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-09-07 09:30:00 | Fail | Repairs completed & all okay on departure.INSTALLED NEW PARTS ALL RHEEM - SOLENOID, LEVEL SENSOR, ELEMENT AND CONTROLLER
MSA-DCS | WA3500255 | Staff over night house- hot water system is not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 09:48:28 | 2020-07-28 12:23:00 | Fail | Attended site,Investigate issues with no hot water,Identify faulty regulator to gas bottles,Sourced new from supplier and installed to rectify issues with gas supply.Tested hot water and works on completion
MSA-DCS | WA3500367 | Unit 4, PRU, Control Room- Pedestrain gate is not opening & closing from control panel | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 10:12:45 | 2020-07-27 10:15:00 | Pass | Contacted Bunbury PRU Control room - pedestrian gate failing to operate.Site informed of power outage, found software failing to communicate with server. Talked site site through software procedures, workstation failed to boot software, talked site staff through rebooting workstation. Workstation booted and command centre restored. Restored site maps and tested doors operational.
MSA-DCS | WA3500370 | Unit 4, PRU, Control Room- Front sliding doors are not functioning from control room | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 10:15:30 | 2020-07-27 11:15:00 | Pass | Contacted Bunbury regional prison, confirmed front sliding doors non operational, command centre so f aware causing issue after power outage, re established connection and tested fully operational
MSA-DCS | WA3500373 | Unit 4, PRU, Control Room- Jaques server reporting error "out" | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 10:16:29 | 2020-07-27 12:36:00 | Pass | Jacques server indicating error "out" system is now online and operational no further action is required.
MSA-DCS | WA3500383 | Unit 14, B & D Laundry Room- Roof Leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 13:00:00 | Pass | Sealed penotration in dwing floor
MSA-DCS | WA3500387 | Unit 14, B & D Day Room- Kitchen Draw wont close properly | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-09-17 15:00:00 | Fail | new drawer runners installed x 6.
MSA-DCS | WA3500391 | Unit 14, B & D Day Room- Kitchen window needs sealing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-18 14:00:00 | Fail | WINDOW HAS BEEN RESEALED
MSA-DCS | WA3500470 | Unit 2, Cell E7- Bed light is faulty | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-12 15:00:00 | Fail | Replaced bed light with led
MSA-DCS | WA3500476 | Visits Waiting- Billi Eco- XL requires filter changing | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Visits Waiting Area | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 14:00:00 | Pass | A40052628G Serviced Billi Quadra changed filter reset checked
MSA-DCS | WA3500547 | 2nd security bollard not opening | Greenough Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-07 08:30:00 | Fail | 07/08/20Adjusted height and packed up bollard
MSA-DCS | WA3500563 | Unit 1, Cell C2- Main light tube keeps falling out | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 10:00:00 | Pass | Repaired faulty lights in unit 1 c2
MSA-DCS | WA3500565 | Admin, Male urinal is very slow to drain & fills urinal to the top before it drains | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 11:30:00 | Pass | Used acid and plunger to clear blockage in urinal
MSA-DCS | WA3500567 | Unit 1 - B7 Viewing hatch requires attention faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-13 11:00:00 | Fail | VIEWING HATCH IN WORKING ORDER - CELL WINDOW SPIRAL BALANCES MISSING, BOTH REPLACED
MSA-DCS | WA3500588 | Fronte Gate, Disability Parking- Pot Hole in Parking Bay | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Asphalt (PR) | AFD Contracting | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-09-09 14:45:00 | Fail | 30/07/20Pot hole is 1,000 x 1,100sunken existing repairEntry road full of pot holesLarge job, have to return to site.09/09/20Cut out sink hole, recompact and patch with hot mix.Hire plate compactor.Fill potholes on road.Workshop - load up, clean trailer, pick up/drop off compactor, pick up asphalt.
MSA-DCS | WA3500594 | Unit 3, Cell D15- Sink smashed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 11:45:12 | 2020-07-27 16:00:00 | Pass | Removed broken basin broken toilet and replaced basin and tap with new replaced toilet and toilet seat and re concreted in new toilet
MSA-DCS | WA3500600 | Unit 3, Cell D15- Viewing window smashed | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 11:47:41 | 2020-07-28 12:30:00 | Fail | OBS PANEL RE GLAZED
MSA-DCS | WA3500604 | Unit 3, Control- Fire Alarm keeps activating | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 11:50:28 | 2020-07-27 14:00:00 | Pass | Unit 3 vesda intermittently in fault due to low airflow fault on pipe 1 (44%). Cleared out blockages in all cells in A wing and also D wing (66%).Levels returned to over 100% vesda back to normal condition.
MSA-DCS | WA3500610 | Unit 1, Cell B8- GPO smashed | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-28 09:00:00 | Pass | Replaced gpo
MSA-DCS | WA3500613 | Laundry, Sheet Press- Extractor fan not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-28 14:00:00 | Pass | Repaired ex fan
MSA-DCS | WA3500628 | Kitchen, Dishwasher Area Floor & Wall Panels- Repair Damaged & Mouldy Silicon | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Schlager Construction Group | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 14:00:00 | Pass | Attended site and removed all mouldy silicone around preparation and floor areas.Re sealed all stainless steel bench tops and tiled areas.
MSA-DCS | WA3500655 | Unit 4, B Wing, Cell B10- door scaping on floor, hinges may require replacing | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-10 10:30:00 | Fail | REPLACE HINGES
MSA-DCS | WA3500659 | Unit 4, D Wing, Cell D12- door scaping on floor (glass blocks), hinges may require replacing | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-10 09:15:00 | Fail | REPLACE HINGES
MSA-DCS | WA3500713 | Unit 3, Cell 9- Fan not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 11:00:00 | Pass | Replaced ceiling fan
MSA-DCS | WA3500734 | Unit 3 - Court Yard An electrical conduit has been exposed outside unit 3 | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-28 13:30:00 | Pass | Rectified exposed conduits in unit 5 courtyard
MSA-DCS | WA3500805 | Unit 2, A Wing- shower door is missing | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-31 14:00:00 | Fail | NEW SHOWER DOOR FITTED
MSA-DCS | WA3500852 | Unit 3, B Wing, Shower window doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 13:45:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3500854 | Unit 3, D Wing, Cell D12- Window not working runners need fixing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 15:00:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3500856 | Unit 3, D Wing, Cell D10- Window not staying up, runners need fixing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-14 12:30:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3500884 | Unit 6, D Wing, Cell D02- Toilet flush is not operating correctly, further info below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 10:30:00 | Pass | Installed new spring and adjusted flush button mechanism
MSA-DCS | WA3500978 | PTZ 24 is not responding to alarms-see notes | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-18 08:30:00 | Fail | Unable to use any PTZ functions from gatehouse. Unable to control camera with CCTV tester at EC. Reset power to camera and transmitter fiber modem. Image and PTZ functions tested ok from EC and from the gatehouse.
MSA-DCS | WA3500980 | PE Beam in Zone 15 - When zone is activated there is no PTZ activation. | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-18 10:30:00 | Fail | Leading, Lagging and Alarm zone cameras ok. Traced fault to lost settings for PTZ 25 which affected alarm presets for zones 15, 16 19, 20 and 22. Reprogrammed settings on Indigo for all mentioned zones. All zones tested ok.
MSA-DCS | WA3500981 | PE Beam in Zone 20 - When zone is activated there is no PTZ activation. | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-18 12:30:00 | Fail | Leading, Lagging and Alarm zone cameras ok. Traced fault to lost settings for PTZ 25 which affected alarm presets for zones 15, 16 19, 20 and 22. Reprogrammed settings on Indigo for all mentioned zones. All zones tested ok.
MSA-DCS | WA3500982 | PE Beam in Zone 19 - When zone is activated there is no PTZ activation. | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-18 15:00:00 | Fail | Leading, Lagging and Alarm zone cameras ok. Traced fault to lost settings for PTZ 25 which affected alarm presets for zones 15, 16 19, 20 and 22. Reprogrammed settings on Indigo for all mentioned zones. All zones tested ok.
MSA-DCS | WA3500985 | Control Room - Cell call network error | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jul 2020 | 2020-07-27 19:56:07 | 2020-07-27 18:30:00 | Pass | Found network error on console, reset nodes and check status of nodes, all online. Test units and cells, look ok, advised client another tech would return in the morning to check again.
MSA-DCS | WA3501031 | Wooroloo -Zone 13 - Fence alarm not activated tried twice | Wooroloo Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jul 2020 | 2020-07-27 21:22:53 | 2020-07-27 21:00:00 | Pass | Attended site, client advised they had re tested zone 13 and came up ok. Re test zone again whilst onsite, no fault found at time of testing.
MSA-DCS | WA3501051 | Banksia Hill Detention-No alarm in activated in serpentine-self key unit | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Jul 2020 | 2020-07-27 22:04:51 | 2020-07-30 11:00:00 | Fail | Attended site and replaced Serpentine building - Tecom panel with new LAN Isolation module.All replaced and tested building alarms and Arming and Disarming and all had tested ok. Job complete
MSA-DFES | WA3500868 | Rear yard gate- Upright post (RHS) which gate locks into is loose, unsecure & coming away from wall | CFRS Kiara | GMP-BR | Building | Steel Fencing & Gates (BU) | AWB Co. | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-28 14:00:00 | Pass | Refix rear yard gate post to wall
MSA-DFES | WA3500878 | Appliance room Replace appliance room globes & refix light fitting, clean dis fusser-see notes | CFRS Claremont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-25 14:30:00 | Fail | Installed 5 x new LEDs in truck room
MSA-DFES | WA3500977 | Lvl 1, Bedroom 1- Hinge on awning window is broken, this is above main entry to premises | CFRS Fremantle | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-19 12:15:00 | Fail | Hoping to access site this Wednesday 19/8/20. Will need to coordinate with site and glazier Replaced - window winding mechanism
MSA-DFES | WA3500979 | Dorm Room 7 - Lower sliding door guide broken. | CFRS Perth | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 10:15:00 | Pass | Attend siteSign and speak to SOLocate dorm 7 remove old broken guideRemove pelmet and get door to slide backInstall new guideAdjust and test door closerReplace pelmetClean up sign out
MSA-DFES | WA3500983 | Kitchen- Extraction fan not operating effectively | CFRS Wangara | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 13:45:00 | Pass | COMPLETED
MSA-DFES | WA3500984 | Rear appliance door – Door Number 4 does not close automatically, further info below | CFRS Kiara | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-10 13:30:00 | Fail | Technician attended the site of 165 Morley Drive, Kiara, WA to the Entry door 4 bi-fold door W23731 on 05/08/2020. Following a full test and inspection of door components found fault to be external photo beams faulty and as a temporary measure technician has put in reflective photo until new safety beams are ordered. 10/08/2020 Technician reattendedReturned to replaced grifco PB060 SEND RECEIVE safety beams test all ok.Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3500990 | Breaker for carport lights tripping out | CFRS Malaga | GMP-BR | Electrical | Lighting, External (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-14 11:30:00 | Fail | COMPLETED
MSA-DFES | WA3500997 | Main Building - Fluro in centre of Engine room broken | Kensington (old) | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 09:15:00 | Pass | Locate faulty lights. Replaced faulty tubes and starters with new.
MSA-DTAG | WA3500822 | Ground & Level 1 - fluro lights not working as below | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-03 08:00:00 | Fail | Replaced light globes and starters
MSA-DTAG | WA3500828 | Level 1, Public area - fluro lights not working as below | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-03 09:00:00 | Pass | Replaced tubes and starters
MSA-DTAG | WA3500832 | Level 1, Magistrates Chamber 2, Fluro light not working | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 27 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-03 09:30:00 | Pass | Replaced tubes and starters
MSA-DTWD | WA3500206 | E block, E617, Male toilets - Last cubicle blocked. | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 16:20:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3500483 | L Block, 1st Floor, LF12- Hot water urn not dispensing hot water | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 16:50:00 | Pass | Pump faulty. Replaced. Level probes not working correctly. Replaced probes. Issues still present. Repaired cleaned and re fitted earth tags. This fixed most issues. Had to re fit level probes as wasn’t reading correctly. This fixed issue and now all working ok. A402021883
MSA-DTWD | WA3500705 | E Block, Stall area - Blocked drains | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 27 Jul 2020 | 2020-07-27 16:44:42 | 2020-07-27 13:54:00 | Pass | Blocked in kitchen all cleared now
MSA-DTWD | WA3500745 | E block ground E009 kitchen Blocked drain (suspect tree roots) | Balga Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 14:30:00 | Pass | Cleared blockage using small drain machine
MSA-DTWD | WA3500911 | D Block, D19- Large Sottoriva Mixer spinning in reverse | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 16:00:00 | Pass | completed.
MSA-DTWD | WA3500963 | G Floor, Room 8G36- RCD tripped and 1 row of lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-03 15:00:00 | Fail | Inspected lighting circuit, rcd now not tripping, no faul found. Site happy.
MSA-DTWD | WA3500966 | A Block, Carpark- Remove graffiti from OXford St entrance | Leederville Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 27 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 14:30:00 | Pass | REMOVAL OF GRAFFITI FROM BLOCK CARPARK
MSA-MRWA | WA3500116 | Lvl 4, Female toilet- Flush button not working please remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 14:39:00 | Pass | Re attach air pipe to bellows
MSA-DCS | WA3501114 | Several cameras in the primitive fence are not working and not even scanning to the alarm | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Jul 2020 | 2020-07-28 10:53:31 | 2020-07-28 10:45:00 | Pass | Travel to site,located several camera that had been reported offline. Reset relevant encoders and retested functions, all tested and back online. Reset Indigo workstation and re-armed alarm zones and added correct privelages to user group for control operators. Walk tested several zones and tested for correct alarm activation in the gatehouse and all had tested ok. job complete
MSA-DCS | WA3501134 | ISU D01 x2 smashed cell window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-31 12:00:00 | Fail | windows reglazed
MSA-DCS | WA3501139 | ISU D03 x1 cell window , Obs window & mirror smashed | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-31 15:00:00 | Fail | WINDOWS & MIRROR REPLACED
MSA-DCS | WA3501143 | ISU C04 x2 smashed double power points | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-03 14:00:00 | Fail | Replaced damaged gpo x2
MSA-DCS | WA3501148 | Jeelia C1 personal lock faulty | Wandoo Rehabilitation Facility | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 28 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-04 08:30:00 | Fail | tightened up hinge and adjuted
MSA-DCS | WA3501171 | Unit 2 A/C hot water urn leaking behind the wall area and onto floor. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 28 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 09:55:00 | Pass | attended diagnosed Rheem BWU needs to be replaced. Quoted to replace client does not want to go ahead with replacement
MSA-DCS | WA3501175 | Unit 4 - D9 URGENT Door is unable to be locked to or closed. Door hinge is broken. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 07:45:54 | 2020-07-28 13:30:00 | Pass | NEW HINGES FITTED
MSA-DCS | WA3501297 | control room Carpet tiles lifting | Hakea Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-25 15:45:00 | Fail | DAMAGED CARPET TILES UPLIFTED & REPLACED
MSA-DCS | WA3501332 | Unit 2 Regi Area Fluorescent light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-29 12:00:00 | Pass | Repaired light
MSA-DCS | WA3501343 | Unit 8, Cell C1- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 15:00:00 | Pass | Replaced broken light switch Unit 8, C1
MSA-DCS | WA3501350 | Unit 4, Cell B11- Fluro Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 11:30:00 | Pass | Re-mounted light switch which was hanging down
MSA-DCS | WA3501360 | Unit 4, Cell D16- Cell call faulty | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 09:18:39 | 2020-07-28 15:00:00 | Pass | Cell call was vandalised and pulled out from the wall, rectified and fixed. Job completed.
MSA-DCS | WA3501402 | Old Videolink - 2x power points are broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 09:40:31 | 2020-07-29 13:00:00 | Fail | Replaced broken gpos
MSA-DCS | WA3501866 | SITE COST Unit 5, control door - locks playing up, unable to enter | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 28 Jul 2020 | 2020-07-28 14:09:11 | 2020-07-28 11:45:00 | Pass | Replaced officers cylinder on Entry Door into Unit 5new cylinder supplied and fitted keyed to Prisons Systemnew door frame strike also fitted
MSA-DCS | WA3501908 | SITE COST Laundry, no power to dryers or washing machines | Bandyup Prison | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 28 Jul 2020 | 2020-07-28 14:23:01 | 2020-07-28 12:00:00 | Pass | Replaced fuse and tested
MSA-DCS | WA3501935 | WARRANTY - Zone 16 omnitrax is constantly alarming | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Dataline Visual Link Pty Ltd | 0 | CLOSE | 28 Jul 2020 | 2020-07-28 14:34:56 | 2020-07-29 12:00:00 | Fail | Reset clutter, adjusted margin and threshold. Conducted walk tests to ensure proper zone detections. Ran and recorded response plot and monitored zone. Found system stable and operating normally. This work order can be closed out. There will be no invoice
MSA-DCS | WA3502005 | control internal zone 9 MF in tamper | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-29 09:00:00 | Pass | Attended site checked and found Internal Zone 9 Microphonics tamper alarm not alarming anymore. Checked on filed in EC cabinet Microphonics sensor cable End Of Line resistance measurement is correct. Checked cable connections are ok. Reboot controller and tested alarm activated and reset correctly.
MSA-DCS | WA3502006 | Admin, Male toilet- seat broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 16:00:00 | Pass | Investigated job. Parts collected offsite. New toilet seat installed.
MSA-DCS | WA3502008 | Admin, Male toilet- Urinal blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-29 11:30:00 | Pass | Inspected urinal . Tested multiple times. No blockage present.
MSA-DCS | WA3502026 | Hotham, kitchen - power point in Kitchen faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-31 09:30:00 | Pass | Reset rcd and tested.
MSA-DCS | WA3502089 | Control - PDA 166 incorrectly activating the whole time | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Jul 2020 | 2020-07-28 16:06:33 | 2020-07-28 14:15:00 | Pass | Travelled to site and reprogrammed faulty PDA 166 with site spare 185. All reprogrammed and tested ok. Job complete
MSA-DCS | WA3502090 | SITE COST Unit 6, Cell 5- Personal lock is broken | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 28 Jul 2020 | 2020-07-28 16:08:37 | 2020-07-28 15:00:00 | Pass | Unit 6 Cell 5 - prisoners Privacy lock difficult to open removed cylinder from door and lubricated refitted and tested
MSA-DCS | WA3502121 | Reception Automatic Entrance Door - Issues with Opening and Closing Door, see further info below | Rockingham Justice Complex | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-29 11:45:00 | Pass | Technician attended the site of 15 Whitfield Street, ROCKINGHAM, WA to the Main entry, Sliding Auto Door, Door no.W28535 on the 29/07/2020. Following a full test and inspection of door components found door was not opening when in lock mode.Door would unlock but stay close.Tech suspected issue is with the access system.Tech conferred with security company on site and worked out problem.Tech reconfigured security swipe connections to wire directly into key impulse into main board instead of mode board.Tech carried out full test of operation - okay.
MSA-DCS | WA3502143 | Kitchen - Left hand prover not steaming | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 12:39:05 | 2020-09-04 11:00:00 | Fail | 28/07/20Arrived at site liaise with reception, identify faulty prover, remove panels, test/fault find diagnose and found the wet element and element tank to be faulty and requires replacement.1x Element1x wet element tank 07/08/20Sign in Escorted to site Install element and tank Found float has hole in and continuously filling Requires replacing Isolate machine and advise staff24/08/20Fitted valve valve and connected element.04/09/20Arrived at site liaise with reception, identify proover, remove panels, test/fault find diagnose and found the main control breaker had tripped, reset breaker, tested all components for correct function and was all okay, checked and tested elements and all control wiring for correct functionality and all okay. Moisture or a cockroach may have tripped the breaker tested for 30 minutes and checked all over again all okay.If this issue continues, recommend replacing the circuit breaker,
MSA-DCS | WA3502157 | Medical Centre, Main Desk- Flooring Lifting behind desk | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-09-08 13:39:00 | Fail | REPLACE DAMAGED FLOORING X3 AREAS
MSA-DCS | WA3502160 | Both fire pumps offline. Please investigate. | Hakea Prison | SPA-BR | Mechanical Services | Pumps (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-09-22 08:19:00 | Fail | Job complete
MSA-DCS | WA3502168 | unit 9, A5 - lino floor lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2021-02-18 11:00:00 | Fail | damaged sections of vinyl uplifted & replaced with new
MSA-DCS | WA3502170 | CCU, H7 - window seal damaged | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-04 15:00:00 | Fail | FRAMEWORK REPAIRED
MSA-DCS | WA3502172 | D Wing Ablutions Grille Lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 13:03:23 | 2020-07-29 12:30:00 | Pass | job completed - Serviced lock and fitted required new parts.
MSA-DCS | WA3502181 | Unit 1 D7 Lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 13:11:28 | 2020-07-29 14:30:00 | Fail | Job completed - serviced U1 - D7 main lock.
MSA-DCS | WA3502190 | Make good chainmesh fence to rear of DDU at Hakea | Hakea Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-11 15:00:00 | Fail | FENCING MADE GOOD
MSA-DCS | WA3502191 | Dairy packing pipe needs to be located as needed for drainage | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-06 11:00:00 | Fail | Investigate to location off sewage drains drairy pasturiser
MSA-DCS | WA3502198 | gatehouse external retic cupboard main retic pressure pump constantly trips | Banksia Hill Detention Centre | WSM-BR-SITE | Landscaping & Gardening | Grounds Maintenance (LG) | Pumps n Pipes | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-05 12:45:00 | Fail | replaced 3 pressure fuses burnt out
MSA-DCS | WA3502208 | Admin building, entrance double doors - doors locks jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 15:15:00 | Pass | Job completed - supplied and installed blocker plate to rectify issue.
MSA-DCS | WA3502211 | Front gate, key control - key watcher door not closing | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 13:36:02 | 2020-07-28 16:15:00 | Pass | Rectified and adjust the electronic latch, tested ok. Job completed.
MSA-DCS | WA3502215 | front gate, master control - camera 053 not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 13:38:18 | 2020-07-28 16:45:00 | Pass | Refresh from DVM, camera back to normal view. Job completed.
MSA-DCS | WA3502216 | Please provide standby assistance with generator test | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-29 08:00:00 | Pass | Standby for generator test on site. Job completed.
MSA-DCS | WA3502240 | entrance of front offce door sensor issue | Karnet Prison Farm | GMP-BR- HO | Building | Automatic Doors (BU) | MARSHALL BEATTIE AUTOMATION | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 13:57:35 | 2020-07-29 11:00:00 | Pass | Travel to and from NON METRO site. Inspect front door. Reported intermittent alarm noise, not showing while on site.Suspect batteries. Test battery, operation failed. Replace batteries and test,all okay. Chain tension loose and very dry.Lubricate chain and tensioned, now okay. Four (4) BWN track wheels are in poor condition causing noisy operation, butstill working (Will need 2 techs to remove doors to replace if becomes a problem). Test operation several times, all okay.
MSA-DCS | WA3502262 | Unit 2, Rear of Unit- Guttering is damaged, water leaking insite unit | Karnet Prison Farm | GMP-BR- HO | Roofing | Guttering (RF) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-11-27 10:07:00 | Fail | sealed roof as required, removed and installed new gutter and np to unit demountable
MSA-DCS | WA3502278 | Industries - MDAS tamper | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-29 11:37:00 | Pass | Rectified and fixed loosed tamper switch, job completed.
MSA-DCS | WA3502301 | Barrier ram - Ram has sheared bolts | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | AFD Contracting | 0 | CLOSE | 28 Jul 2020 | 2020-07-28 18:41:04 | 2020-07-28 16:15:00 | Pass | 28/07/20replaced sheared bolts.Tightened all loose bolts on all 3 locking plates.
MSA-DCS | WA3509701 | Input showing open on alarm and wont allow system arming | Maddington (South East Metro) | GMP-BR- HO | Security | Monitoring (SE) | Sapio Pty Ltd | 3 | CLOSE | 28 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-03 11:30:00 | Pass | Shunted zone in mean time to allow client to arm without alarm going off.
MSA-DFES | WA3501381 | Change Room 2, Rear Transportable- Linoleum floor has lifted/bubbled in 2 centre areas of the floor | FESA RHQ - Forrestfield | GMP-BR | Flooring | Vinyl (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-21 12:45:00 | Fail | Change Room 2 Rear Transportable lino floor has lifted/bubbled in 2 centre areas of the floor.Installation of expansion strip to area where vinyl bubbling
MSA-DFES | WA3501387 | Knowledge & Training Support Office- Water stain on the ceiling tile | FESA RHQ - Forrestfield | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 08:45:00 | Pass | Rat nest in ceiling space - Cleared debris and painted ceiling panel with stain block
MSA-DFES | WA3501910 | Sprinkler system in the gated car park, north east corner, is spraying water. | DFES Cockburn Emergency Services Complex | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-06 08:30:00 | Fail | Dom call out to investigate on 4/08/20Dom went back on 6/08/20 to repair & parts
MSA-DFES | WA3502221 | Issue with Courier Door and Frame. Bent Hinges and door sticking | CFRS Wangara | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-31 11:45:00 | Pass | Complete
MSA-DFES | WA3502226 | Level 1 (Northern end of building), Downstairs CESM office- fluro lights not working | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 12:45:00 | Pass | COMPLETED
MSA-DFES | WA3502304 | ground yard Garden tap at rear of engine room leaking | CFRS Duncraig | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 13:15:00 | Pass | Investigate leaking garden tap outside engine room, locate garden tap and isolate water to fire stationRemove old garden tap and supply and install new garden tap with vacuum breakerTurn water back on and check for leaks , test operation, pack up and clean up worksite
MSA-DFES | WA3502401 | one of the light dripped the circuit .no electricity | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 17:00:00 | 2020-08-11 10:45:00 | Fail | CompleteAttended site and signed in, replaced faulty lights in kitchen all in working order. Notified staff and signed out
MSA-DFES | WA3502978 | RETROSPECTIVE WORKORDER-NO SIGN OF FORCED ENTRY OR DAMAGE . CLEARED OFFSITE BY OPS -Do not attend | VFRS Mandurah | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 15:41:00 | Pass | Despatch Comments:BY PASS ZN 22 REED S/WA APP BAY 1 REAR DOORPatrol Resolution:REACHED ONSITE DID AN EXTERNAL CHECK , NO SIGN OF FORCED ENTRY OR DAMAGE . CLEARED OFFSITE BY OPS .
MSA-DTAG | WA3501100 | control room level 10 cctv screen Has power issues not turning on | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 28 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 08:30:00 | Pass | Finished setup of Level 10 CCTV PC. Domain online and 2 x Milestone clients running on auto start and auto login forCCTV wall.Job completed.
MSA-DTAG | WA3501281 | Remove graffiti from column & wall – main entrance/foot of ramp (Hay Street) | Central Law Courts | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-30 11:00:00 | Pass | Removed graffiti
MSA-DTAG | WA3502280 | Cell 3 - Bio Clean for golden staph | Rockingham Justice Complex | WSM-BR-SITE | Cleaning | Hazardous Materials (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 18:00:00 | Pass | Job done as per Work Order
MSA-DTWD | WA3501179 | C block ground foyer High Ceiling light blinking | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 28 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-28 14:45:00 | Pass | Attended site and signed in. Located faulty light in foyer. Removed lamp and found blown. Replaced with new. Tested all okay. Job complete
MSA-DTWD | WA3501185 | A block ground Front of room near door flouro tube is flashing and needs to be replaced | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 28 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-28 15:15:00 | Pass | Attended site and signed in. Located room AG10. Found faulty light. Replaced tubes and starters. Tested all okay. Job complete
MSA-DTWD | WA3501189 | G block ground Roof leaks in two spots | Mandurah Campus (formerly Peel) | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 28 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-25 12:00:00 | Fail | 3/8/20 Have attended site to assess leak. Unable to do so on this occasion as safety access equipment was required. Will need to return with vertical cable grab21/8/20 Have ordered materials and will schedule as soon as materials arrive in stock 7/9/20 - Site requested works be scheduled during the coming TAFE term date - Currently scheduled for Sept 29
MSA-DTWD | WA3501204 | admin G block Main Auto Door, controller is off line unable to lock | Clarkson Campus | GMP-BR | Building | Automatic Doors (BU) | BJ SYSTEMS | 1 | CLOSE | 28 Jul 2020 | 2020-07-28 17:00:00 | 2020-07-30 11:00:00 | Fail | Replaced faulty power supply due to suspected power spike and replaced 4x batteries as below 5V. Confirmed panel online and tested ok
MSA-DTWD | WA3501214 | G block ground metal workshop 4 High ceiling lights not working. | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 15:45:00 | Pass | Attended site and signed in. Located g block workshop in metal fab. Found 4 x lights out in workshop. No power to lights. Inspected and yested circuit at switchboard. No faults present. Reset and tested lights to all be working. Job complete
MSA-DTWD | WA3501365 | Block 6, Painting and Decorating - Blocked water separation pit in floor | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-29 13:27:00 | Pass | Remove baffle for cleaning purposes
MSA-DTWD | WA3501411 | Block 8, Room 8F60- Water leak into classroom | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-10-13 15:15:00 | Fail | Sealed up around roof penetrations in the area above the leak
MSA-DTWD | WA3501836 | E Block, Room E204- Air con is not heating | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-29 11:00:00 | Pass | Attended site and located room e204,tested system and checked operation,found system to be all ok.with supply temps of 50 degrees,gas charges all within spec and system is meeting room temp set point of 30 degrees.left system all operational
MSA-DTWD | WA3501855 | A, block south, external auto sliding door - chain drive very noise | Leederville Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 28 Jul 2020 | 2020-07-28 13:59:53 | 2020-07-28 11:14:00 | Pass | Adjusted door height, adjusted chain tension and moved endstop as necessary. Checked over and tested door and left in good working order.
MSA-DTWD | WA3501869 | P Block, Alarm system not arming, fault showing comms failure | Midland Campus | GMP-BR | Security | Monitoring (SE) | CONNECT SECURITY SYSTEMS | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-29 11:54:00 | Pass | GSM Dialler in P Block found to not be registering with Vodafone SIM after network maintenance by Vodafone. Campus advised to obtain a new Telstra SIM, and shown how to replace SIM once it arrives.
MSA-DTWD | WA3501873 | Level 3, Classroom B314- Roof leak | Perth Campus B6 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 14:15:00 | Pass | Leak appears to be ingressing from exposed pipework from box gutter, re-sealed sump and outlet, if problem persists it may be an issue with the PVC joints.
MSA-DTWD | WA3501875 | Level 2, Room S226- Blind is broken | Perth Campus B1 | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-19 10:03:00 | Fail | All Complete & invoice attached
MSA-DTWD | WA3502022 | B Block, East auto door- making a humming noise | Munster Campus (ACEPT) | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 13:52:00 | Pass | 631029. Found battery voltage low, replaced battery and tested door all ok
MSA-DTWD | WA3502025 | A Block, Room A306- Circuit breaker was on but lights where off, possible faulty switches. | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-31 14:00:00 | Pass | Job complete
MSA-DTWD | WA3502027 | Dental Division 17 Monash Ave Repair Lock to Chemical Cabinet Dental Division-SEE NOTES | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 10:50:00 | Pass | Attend site to survey flammable liquid cabinet for repairs. Repairs are not possible, end users are contemplating having the cabinet replaced.
MSA-DTWD | WA3502029 | A13 Female toilet entry door- Door closer faulty | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-28 12:15:00 | Pass | Liam Hanlon (28/07/2020) - Work Notep2 A13 female entry toilet door closer has failed leaking oil and slamming door Got new closer Closed off toilets and replaced closer Cleaned up
MSA-DTWD | WA3502044 | Male Toilet- Flush system not working | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-30 12:30:00 | Pass | Install dual flush cistern
MSA-DTWD | WA3502051 | Level 2, disbale toilet - Basin fallen off the wall | Perth Campus B6 | GMP-BR | Building | Materials (BU) | Falcetta Plumbing and Gas | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 14:37:00 | Pass | Fix basin
MSA-DTWD | WA3502078 | Block 12, 1st Floor, RM 12G1- Water leak into classroom | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-09-29 10:30:00 | Fail | Currently scheduled for Aug 20 weather permitting7/9/20 - Site have requested that works be carried out during the coming TAFE break - Currently scheduled for 29th September 2/10/20 - Works now complete and leak resolution confirmed with site
MSA-DTWD | WA3502123 | ground level, Workshop Carpentry and Joinery - Power problem with router. | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 17:00:00 | 2020-09-07 11:30:00 | Fail | Repalced faulty start/stop kits to machines as shown by site. Job completed
MSA-DTWD | WA3502161 | J block J111 male toilet blocked-see notes | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-03 15:40:00 | Fail | Cleared blockage using plunger
MSA-DTWD | WA3502178 | D block - Several lights not working, covered walkway adjacent to D block heading towards G block | Midland Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-31 10:15:00 | Pass | Attended site and signed in. Located lights not working in walkway. Spoke with staff and was advised to replaced the whole section with LED tubes. Site supplied all the parts. Disconnected and removed all fluro and control gear. Rewired with new led gear and installed led tubes. Tested all okay. Job complete
MSA-DTWD | WA3502188 | A block, A113 - Taps in female toilet Student Services hard to turn on and off | East Perth Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 13:00:00 | Pass | Complete
MSA-DTWD | WA3502224 | U Block, UO24.7 - 2 x roof leaks in the same room | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 28 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-30 12:45:00 | Pass | Made inspection to void, located leaks to vent pipe and extraction/vent ductwork - re-sealed all joints to unit and flashings - sealed underneath front flashing where sheet ends had not been turned up
MSA-DTWD | WA3502363 | level 1, replace faulty shower heads where required | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 28 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-31 14:34:00 | Pass | Shower head replacements
MSA-DTWD | WA3502395 | E Block, Bentley Pines Restaurant ,Male Toilet – Cubicle toilet is leaking water | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-29 08:45:00 | Pass | Replaced pan cone on toilet
MSA-MRWA | WA3501380 | Rear exit gate - not operational please remediate | Traffic Operations Centre | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 28 Jul 2020 | 2020-07-29 17:00:00 | 2020-07-28 12:19:00 | Pass | Gate was open. Diagnosed the fault to be safety beam receiver not working correctly. Replaced the beams and tested all good. Ps gate operates correctly for a few operations then opens slowly. Before operating correctly. Suspect the encoder or controller is on its last legs. Brendan Mitchell has requested the official quote, not a Braf
MSA-DCA | WA3502589 | Ground floor, Plant room, Boiler room - boiler 2 fault | Maritime Museum Victoria Quay-Robert Steele Marine Engineers Display-Ground Floor-Boiler Room | GMP-BR | Mechanical Services | Boilers (MS) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-11 16:30:00 | Fail | Re-attended site with Boilertronics. Original PO cancelled due to Boilertronics attending for site RM. Applied tests and checks to boiler. Simulated low fire and hi fire simulation testing. Calibrated and reconfigured combustion gas module and tested operation. Monitored system during on and off cycle ok. System operating correctly.
MSA-DCA | WA3502600 | Harry Butler building management system remote connection not working | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-09-14 16:30:00 | Fail | Please refer to work logs and attached Alerton service report for in depth analysis.
MSA-DCA | WA3503160 | fire panel - 3 x fault on fire panel – please investigate and rectify | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 4 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 14:15:00 | Pass | Attended site - investigated 3 x faults on FIP - M2130 and M130 have been ongoing faults and are disabledThe earth fault had been recorded 21st July with no work going on They had an alarm on the 20th which required a detector changing over the base on this has dried corrosion on the side recommend changing the base to new for a possible solutionsAttended site 31st July to change over base due to corrosion
MSA-DCA | WA3503276 | Plant Room- Water inside honeywell MSSB-G-3 please investigate | State Library of WA-Main Building-Ground Floor-GF06 - Theatre | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-30 14:52:00 | Pass | Water has pooled inside the MSB for AC 13 in the gnd floor Theatrette. There is no longer any leak present. Honeywell on site for PM, service tech inspected controller and BMS for alarms. Appears that no damage has occurred as a result of the water leak. Drilled holes in the base of the MSB in case water leaks again. Cleaned and dried MSB. Inspectedduct section above AC 13. No water leak present or signs of previous leaks.
MSA-DCS | WA3502496 | PE beam F - 2 is going off again - Not the urgent one | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-07 08:30:00 | Fail | On arrival at perimeter, checked Tx and found infested by ants. Cleaned out and sprayed with bug spray. Checked allignment and confirmed correct. Attended Rx and when visually checking allignment noted weed growth starting to obstruct lower PE Beam, cleared grass from beam path. Adjusted allignment and confirmed with test meter. Confirmed with gate control all alarms clear. 07/08/2020 On arrival was advised by control that Tamper Alarm had activated on Rx module over night. Returned to Rx and cleared alarm
MSA-DCS | WA3502532 | pod control room camera PTZ 5 has a blury picture | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 07:15:07 | 2020-07-29 12:00:00 | Pass | Attended site. Checked PTZ5 view. Camera in focus. Checked footage. Camera was rebooted and focused by SEMEtech. Rectified time fault with 72 cameras and alarm screens.Job completed
MSA-DCS | WA3502540 | Staff change room - Male Urinal slow to drain after flushing & occasionally overflows | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 11:00:00 | Pass | Complete
MSA-DCS | WA3502554 | Security Area - Office Indigo unit not operating in the security office, | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-29 09:00:00 | Pass | Attended security office and investigated loss of “live view” on CCTV monitors. Reset Indigo workstation and attempted to login as “ Security”, found problem still exists. Reset Security login, then logged into system to confirm video available as “Live view” and “Replay” on screen.
MSA-DCS | WA3502558 | unit 7 C wing cleaning store tap constantly drips. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 11:00:00 | Pass | Removed outlet. Cleaned flow restrictor blockage. Reinstalled tap and tested
MSA-DCS | WA3502561 | Unit 1 - A2 Management cell window cracked and requires replacement glass. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jul 2020 | 2020-07-31 17:00:00 | 2020-08-04 12:00:00 | Fail | CELL WINDOW GLASS REPLACED
MSA-DCS | WA3502569 | Cell wash bashin blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-31 08:30:00 | Pass | Plunged basin to clear blockage
MSA-DCS | WA3502572 | Toilet is not flushing. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-03 11:00:00 | Pass | Investigated blockage location. Plunged toilet to clear blockage
MSA-DCS | WA3502590 | SITE COST control pod - fobs is not securering door when accessing | Wandoo Rehabilitation Facility | WSM-BR-SITE | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 29 Jul 2020 | 2020-07-29 12:14:58 | 2020-07-29 10:30:00 | Pass | Attended site. Checked reported fault. Reset associated Logic Blocks. Tested operation, all OK.Job completed.
MSA-DCS | WA3502686 | Unit 2, showers - ventilation grilles have been ripped off the walls | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 08:45:29 | 2020-07-30 10:30:00 | Fail | Attended site to carry out works, prison staff not abled to find missing metal grille so was requested to wait in unit 2 pod until it was determined that it was taken of site by another contractor.
MSA-DCS | WA3502729 | Unit 6 - B Wing oven drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-31 09:30:00 | Pass | Removed oven. Used acid to clear blockage. Flushed with water. Replaced oven.
MSA-DCS | WA3502734 | Investigate PTZ1 intermittently turns screen purple | Wandoo Rehabilitation Facility | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2021-01-29 12:08:00 | Fail | Ptz set up recording and integration tested ok network security adjusted for camera
MSA-DCS | WA3502738 | PTZ 5 intermittently crashing requiring power cycle | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-11-30 13:32:00 | Fail | work order to be invoiced at cost to date
MSA-DCS | WA3502740 | Cleaning- Dripping tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-03 12:00:00 | Pass | Replaced leaking spindle in kitchen tap
MSA-DCS | WA3502743 | O D P - West Womens toilet lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 09:14:38 | 2020-07-31 12:45:00 | Fail | remove jammed toilet indicator bolt.replace toilet indicator bolt, hinges and adjust strike.
MSA-DCS | WA3502745 | Cleaning, workshop - lights not working, keeps tripping | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-09-01 13:30:00 | Fail | Replaced faulty hi bay lights in cleaning workshop
MSA-DCS | WA3502760 | unit 3 cell 5 faulty heater power point | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 14:30:00 | Pass | Replaced cracked power point
MSA-DCS | WA3502791 | kitchen leak from the kitchen tap causing wet | Midland (North East Metro) | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 14:45:00 | Pass | Complete
MSA-DCS | WA3502794 | Unit 1, PSA system hand receiver not working properly | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 09:31:22 | 2020-08-07 07:30:00 | Fail | Replaced faulty unit with new (CellGuard mod.CG-OH - supplied by SEME).Tested.All ok at departure
MSA-DCS | WA3502800 | Unit 1, PIR for port area is constantly flashing green | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 09:34:25 | 2020-08-06 15:08:00 | Fail | Repaired PIR faults and tested OKJob Complete
MSA-DCS | WA3502801 | Unit 3, PIR for port entrance and Cell 2 are constantly flashing | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 09:36:04 | 2020-08-06 13:30:00 | Fail | Attended site.Found that PIR for port entrance is faulty - replaced with new (Interlogix mod.EV1116 supplied by SEME)Used sundries.Conducted test on all PIR’s in unit 3.All back to normal and operational
MSA-DCS | WA3502803 | Unit 2, PIR cell 8 & 9 constantly flashing and cell 17 not working | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 09:37:16 | 2020-08-06 15:33:00 | Fail | Repaired multiple PIR faults and tested OK
MSA-DCS | WA3502805 | Unit 4 office - external light fitting broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-31 12:00:00 | Pass | Investigate unit 4 office external light.Requires replacement
MSA-DCS | WA3502851 | Unit 2 Shower, Repair vent grill | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 09:51:27 | 2020-09-15 12:00:00 | Fail | VENTS REMOVED/ REPAIRED/ REPLACED
MSA-DCS | WA3502912 | Unit 14, Cell A14- Lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-30 10:00:00 | Pass | Repaired faulty lights in unit 14 a14
MSA-DCS | WA3502917 | Unit 6, Cel B9 -Obs light not wworking | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-30 11:30:00 | Pass | Repaired faulty lights in unit 6 b9
MSA-DCS | WA3502927 | Jasper, C wing, common room - sash window frame damaged | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-13 15:00:00 | Fail | SASH WINDOW RE GLAZED
MSA-DCS | WA3502955 | Unit 1,Cell D4- Bed End Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 09:30:00 | Pass | Attended site and carried out repairs to the damaged bed panels.
MSA-DCS | WA3502959 | support building 1 external door between vocational room 3 and yard tounge not catching | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 11:45:00 | Pass | Adjust strike plate to allow lock to engage.
MSA-DCS | WA3503014 | SITE COST SOG Base- training room, key touch keypad for door is not working | Hakea Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 29 Jul 2020 | 2020-07-29 15:02:49 | 2020-07-29 13:00:00 | Pass | Job completed - Inspected and tested lock. Could not fault. Job closed, but will test again next time on site.
MSA-DCS | WA3503017 | Kitchen - dishwasher leaking chemicals | Melaleuca Prison | GMP-BR- HO | Cleaning | Materials (CL) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-31 12:30:00 | Fail | 13/08/20Called as requested to the dishwasher leaking chemical. Found the unit leaking rinse aid and requires a new T and hose pipe. Parts required 1x rinse injector kit 31/08/20Fitted parts tested all ok
MSA-DCS | WA3503057 | Unit 10, Control Room- Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 14:00:00 | Pass | Repaired light
MSA-DCS | WA3503064 | Unit 6, Cell A9- Metal Base from bunk pulled away | Hakea Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-24 09:45:00 | Fail | RE WELDED METAL MESH TO BED FRAMEWORK
MSA-DCS | WA3503067 | Unit 6, Cell D8- Light not working , broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 11:00:00 | Pass | Repaired light
MSA-DCS | WA3503079 | unit 3, A9 - Water dripping through smoke alarm | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 15:00:00 | Pass | Inspected water leak there was no mains water leaking possibly rain water leaking throw roof did get up and look and located a possible leaking spot in valley
MSA-DCS | WA3503098 | Unit 10 cell B9 Water leak from ceiling | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 11:49:59 | 2020-07-29 13:05:00 | Pass | Inspected and located leak shut off all mains
MSA-DCS | WA3503117 | unit 6 nth wing showers sink tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 11:56:38 | 2020-07-29 13:57:00 | Pass | Tightend up loose basin outlet
MSA-DCS | WA3503119 | Unit 13, Cell A6- Seal in shower needs sealing as leaks onto lower bunk bed | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-17 12:45:00 | Fail | RE SEAL LEAKING SHOWER SCREEN
MSA-DCS | WA3503129 | Unit 13 - B5 tv power point is faulty | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-30 08:30:00 | Pass | Repaired faulty gpo in unit 13 b5
MSA-DCS | WA3503138 | unit 1, Outside Gate at End of Unit- Lock jammed won't open | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 12:01:24 | 2020-07-29 15:30:00 | Pass | job completed - serviced grille and rectified issue.
MSA-DCS | WA3503255 | out side Unit 2 gate - drain grill is bent | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-09-02 14:00:00 | Fail | Attended site and assessed what repairs where required.Removed damaged grills and took them of site to be rewarded.
MSA-DCS | WA3503437 | Kitchen - hobart slicer jamming on slide | Melaleuca Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-13 10:30:00 | Fail | 13/08/20Called as requested to the meat slicer jammed. Found the unit in working but oiled anyway. Staff reported the push handle missing so will order a new one and return. Parts required:1 x push handle complete2 x s/s bolts to suit 05/10/20Staff had already screwed handle back on so supplied new handle as spare part
MSA-DCS | WA3503440 | Kitchen - Gas Fired Brat Pans x 2, Thermostats Faulty | Melaleuca Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-31 11:00:00 | Fail | 13/08/20Called as requested to the faulty thermostats. Found the the unit gas pressure incorrect and an incorrect data badge fitted both units appear to have been NG when LPG is required and the LPG data has not been fitted.Both unit showing an over gases flame and found the the gas pressure to low but unable to check due to no data badge. Adjusted the gas reg but was unable to get the correct flame will obtain the correct information and parts and return. Parts required2x tilt switch 31/08/20Called to site as required checked the burner and the injector found the burner to be correct but rusting out in comparison to the new burner I checked with and the injectors over sized. Adjusted the operating pressure to 2.5kpa as required. Parts required (On job #17925)20x LPG burners 20x injectors
MSA-DCS | WA3503446 | House 10, Unit 5- Hot water system is not producing hot water | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 11:00:00 | Pass | COMPLETED
MSA-DCS | WA3503493 | Unit 15, outside of prisoners yard, blocked sewer- see further info | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Sewage Treatment Plant (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 29 Jul 2020 | 2020-07-29 20:55:47 | 2020-08-06 09:30:00 | Fail | Inspected sewage station outside. No alarms and both pumps and macerator are working correctly.
MSA-DFES | WA3502780 | Rear Appliance bay door will not close- see further info below | VFRS Bassendean | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-09-04 17:00:00 | Fail | Technician attended the site of Bassendean Fire Station, Rear LHS Panel Door W21251 on 10/08/2020. Following full test and inspection of door components identified fault was overload tripped. Technician has investigated and found that inertia switch faulty and CB6 Logic fault require to replace both.Technician returned on 04/09/2020 to carry out quoted work to rear engine room door. Technician has changed the CB6 control board for door and replaced the safety inertia switch on motor. Door is now working as should. Full test and inspection of door components completed prior to leaving site.
MSA-DFES | WA3502811 | ground Kitchen sink spout leaking water. Is also loose | CFRS Midland | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 09:55:00 | Pass | Replaced leaking spout.
MSA-DFES | WA3502995 | Ground floor, ladies bathroom - The taps are the sink in the ladies bathroom require replacement. To | SESU Northshore | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-06 12:16:00 | Fail | Replacing the tap set.
MSA-DFES | WA3503151 | Find and repair leak on toilet roof and make good ceiling and paint once done | VFRS Secret Harbour | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-09-30 14:00:00 | Fail | 3/8/20 Attended site and assessed roof leak. Water has been flowing back up under the sheets as there is insufficient overlap into the gutter. Sheets are corroded and need replacing. Water damage to ceiling will need to be replaced Approx 3.8 x 2.4 works will need BRAF prepared Repair works commenced Friday 4/9/20 7/9/20 - Sheeting replacement and ceiling repairs have been completed - electrical re-connection and re-installation of access ladder to be completed 30/9/20 - Roof access ladder reinstalled. Works are now complete
MSA-DFES | WA3503385 | Level 2, mens toilet - 2 x cistern’s running not stop | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 11:06:00 | Pass | Servicing two toilet cisterns.
MSA-DTAG | WA3502828 | Basement & Ground- Detention Kitchen & Magistrate Horrigan’s Chambers- GPO's damaged, see info below | Perth Children's Court | WSM-BR-SITE | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 08:15:00 | Pass | Replaced Socket and carried out test on socket in basement kitchen, new data point and test in Magistrates office, replaced 3 no. 2ft tubes and 3 no. Starters in Links office.
MSA-DTAG | WA3502889 | Level 5, Family Violence Staff Kitchen - A small area of plaster has detached from the kitchen wall | Central Law Courts | GMP-BR-HO | Building | Internal Walls (BU) | PPM Project Painting & Maintenance | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 12:00:00 | Pass | Repair and Re-paint wall
MSA-DTAG | WA3502969 | level 1 - room 1.02 Judicial door alarm doesn't not work -see notes | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 29 Jul 2020 | 2020-07-29 14:43:09 | 2020-08-11 11:00:00 | Fail | Turned face plate around tested OK
MSA-DTAG | WA3503303 | Lvl 5, Court 58- Door closer screws are loose – public entrance door | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 09:30:00 | Pass | RE SECURED DOOR CLOSER
MSA-DTAG | WA3503310 | L5 Several seats are loose outside Court 56 – public area | Central Law Courts | GMP-BR-HO | Furniture | Office Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-04 09:00:00 | Fail | ALL SEATING RESECURED
MSA-DTAG | WA3503362 | Staff Car Park- Outside tap is dripping | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 09:30:00 | Pass | hose tap was in faulty condition so replaced with brand new hose cock
MSA-DTAG | WA3503389 | Duress Alarm in Magistrates Chambers 1 not working | Rockingham Justice Complex | GMP-BR-HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-08-04 09:30:00 | Fail | Replaced battery and put site on test and tested operation. Button is now operating.
MSA-DTAG | WA3503468 | Entry to registry office (in front of Caffissimo)- Floor strip is lifting- see further info below | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 08:30:00 | Pass | RE FIXED STAIR TREAD
MSA-DTWD | WA3502584 | A block cafe area ground Door closers broken | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-29 11:19:00 | Pass | Replaced broken hold open device in 1x canteen door and re-secured slide arm channel on other canteen.
MSA-DTWD | WA3502696 | L2 cleaners rom leak in ceiling | Perth Campus B4 | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-30 15:30:00 | Pass | Made ceiling inspection - sealed around vent pipe, discovered small leak from water fountain feed pipe.
MSA-DTWD | WA3502802 | Block 10 disable toilet Broken light. | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 12:00:00 | Pass | Repaired failing light. Disabled toilets 1st floor block 10
MSA-DTWD | WA3502809 | 3 welding tech- 1st welding bay on right- Broken 3 phase socket cover | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-03 14:00:00 | Pass | Arrived at site signed in , completed a jsa , met with site contact , located 3phase 32a PowerPoint , isolated circuit , changed PowerPoint , tested PowerPoint , re-energised circuit , re tested PowerPoint ***Job completed ***
MSA-DTWD | WA3502812 | Block 3, 3B66c RPL Room- Water leak through light | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-29 15:30:00 | Pass | Carried out leak repairs. Site reported leak has been resolved
MSA-DTWD | WA3502929 | T block classrooms T041 and T042 Both entry doors dropped and will not lock | Murdoch Campus | GMP-BR | Building | Automatic Doors (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-29 14:30:00 | Pass | ATTENDED SITE, ADJUSTED INTERNAL HINGE AND PACKED UP BOTTOM RAIL AND RE SECURED DOOR IN T042ADJUSTED INTERNAL HINGE, PACKED UP BOTTOM RAIL, ADJUSTED LOCKS AND RE-SECURED DOOR IN T041KEVIN ON SITE HAPPY WITH WORKS DONE
MSA-DTWD | WA3503015 | R block ground comms room FTC 14 both sides of building showing low battery | Joondalup McLarty Campus | GMP-BR | Electrical | General Electrical (EL) | BJ SYSTEMS | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 11:45:00 | Pass | Sign out keys FM Joondalup, login Gallagher workstation, check controller status and location. Inspect PSU, test voltage 13.7v ok. Remove and install new backup batteries to controller. Battery load test ok, clear alarm. All ok
MSA-DTWD | WA3503020 | Room 1MA Key- Problem with keys in lock | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-30 11:30:00 | Pass | Reset cylinder
MSA-DTWD | WA3503029 | A block ground server room FTC 08 showing low battery | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | BJ SYSTEMS | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 12:30:00 | Pass | Locate FTC#08. Inspect and test Gallagher PSU voltage 13.53v ok. Inspect batteries backup leads. Install 4x new backup batteries. Test battery power, all ok. Alarms restored
MSA-DTWD | WA3503045 | A block, A001 - CCTV camera not working | Balga Campus | GMP-BR | Security | CCTV Surveillance (SE) | Casa Security Pty Ltd | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-04 13:30:00 | Fail | repairs to CCTV
MSA-DTWD | WA3503120 | A block, level 2, 237 & 236 - Problem with indoor air quality in classrooms A237 & A236 | Leederville Campus | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-05 13:00:00 | Fail | Attended service call regarding smell in room A236. Carried out deep clean of Indoor coil and flushed condensate lines. Reassembled unit then test ran , all ok
MSA-DTWD | WA3503187 | G Block, G23 workshop- Large Metal sliding doors getting stuck at top railing | Fremantle Campus (formerly WA Maritime) | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-18 12:45:00 | Fail | Installed new structural steel bracing to metal doors. Tested ok
MSA-DTWD | WA3503235 | A block Campus grounds Lights not working on south side of A block grounds | Bentley Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 29 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 10:08:00 | Pass | Attended site and signed in. Located walkway to A block from C block. 2 x pole lights out. Located feed in c block. Circuit is tripping. Isolated feeds and poles and identified faulty cable. Rewired cables in switchboard and used new feed to pole lights from security light contactor. Reconnected poles and tested all okay. Looked into carpark and all external lights reported to be out. Replaced fuse in 1 pole. Reconnected up some isolated poles and tested to be all okay. Back of B block had tripped breaker, insulation tested cables to look for fault. But all is okay. Reinstated power and tested all security light poles. Reconnected led pole. Intermittent fault on old light pole swing pole. All lights have power and have noted to dead globes on sites map. NOT COMPLETE! Submitting BRAF !Replaced all faulty Car park lighting- all now working.
MSA-DTWD | WA3503351 | North, Level 2, Room N213- Air Con not working | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 29 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-18 10:00:00 | Fail | Returned to site after initial service call with new filters for PAC#2. Accessed unit then replaced as required, removed all rubbish from site then completed paperwork.
MSA-DTWD | WA3503355 | South Block, level 2, S216 kitchen - Replace/repair cracked gpo | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-05 11:15:00 | Pass | Attended site and signed in. Located S216 kitchen. Found left hand side gpo on bench to have faulty switch. Supply and replace with new double gpo. Tested all okay. Job complete
MSA-DTWD | WA3503408 | Lvl 2, Records- broken frame in carpet floor | Perth Campus B1 | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 29 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-18 14:15:00 | Fail | Carried out repairs as directed by site staff
MSA-DTWD | WA3503489 | Hot water system has burst/leaking | Balga Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ECO PLUMBING AND GAS PTY LTD | 0 | CLOSE | 29 Jul 2020 | 2020-07-29 20:42:23 | 2020-08-10 12:35:00 | Fail | Replaced bust hot water uni
MSA-DCS | WA3503693 | gate control PTZ 2 camera 30 no picture-SEME on site | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 08:02:17 | 2020-11-25 11:03:00 | Fail | work order to be invoiced at cost to date
MSA-DCS | WA3503778 | unit 4B shower block spotlight not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 12:30:00 | Pass | Replaced roof top spot light
MSA-DCS | WA3503798 | Kitchen - #3 oven back firing gas | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 08:52:06 | 2020-08-10 15:40:00 | Fail | Replaced Ignition electrode & boiler tank.
MSA-DCS | WA3503861 | Grounds, Pump house- Pressure switch appears to be sticking & pump will not turn off | Casuarina Prison | GMP-BR- HO | Mechanical Services | Pumps (MS) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-04 16:00:00 | Pass | Investigated cause off jacking pump 2 continually running. No leaks detected on fire system. Pressure switch set to high and needed to readjusted. Pumps now switch on @ 850kpa and turn of @ 1050 kpa
MSA-DCS | WA3503872 | unit 2 4 locks on all 4 fire doors not working | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 30 Jul 2020 | 2020-07-30 13:41:43 | 2020-07-30 12:45:00 | Pass | Unit 2 - Fire Doors in A&B + CD Wings Checked all locks removed from doors and serviced ( 6 doors )
MSA-DCS | WA3503877 | Administration, lunch room - Bain Marie (Power cord)in admin lunchroom appears damaged and unusable | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 09:44:49 | 2020-07-30 15:00:00 | Pass | Repaired faulty Bain Marie in admin lunchroom
MSA-DCS | WA3503886 | Gate House, Front Entrance - Security camera 6 spinning constantly | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 09:51:19 | 2020-07-30 12:00:00 | Pass | Checked Camera from Gatehouse, confirmed camera still rotating. Attended Equipment Cabinet at base of camera pole, power reset the camera. Confirmed correct camera restart and control had PTZ functions available. Returned to Gatehouse, reset camera presets.
MSA-DCS | WA3503896 | Control Room- PDA system not working | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 09:56:51 | 2020-08-07 10:30:00 | Fail | Attended unit 4, confirmed fault with Cell call / Intercom handset. Replaced handset and tested operation. Confirmed handset and unit PA operating correctly.
MSA-DCS | WA3503898 | A & B door controls are not working for unit 4 | Albany Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-06 13:00:00 | Pass | Replaced all momentary round vandal resistant door bottoms on panel and push on/off button (with LED) for Turnstile. Panel was installed over five years ago.
MSA-DCS | WA3503899 | unit 2, A&C - Boiling water unit installed yesterday is leaking badly. Call Back | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-04 11:35:00 | Pass | Diagnosed issue unit completely corroded inside tank and leaking have advised before about this cannot repair
MSA-DCS | WA3503908 | Grounds - Pump House Alarms for the fire pumps are reading incorrectly in the POD. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 10:02:07 | 2020-08-21 11:06:00 | Fail | reprogrammed graphics as quoted
MSA-DCS | WA3503916 | Unit 3, Back of pool- Hot water system is leaking | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-05 13:45:00 | Fail | Rear of pool room unit 3, locate Bosch 16H with split to heat exchanger. Unit will require urgent replacement.
MSA-DCS | WA3503927 | entry building reception and male amenities toilet light globes need to be changed | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-21 12:30:00 | Fail | Replaced tubes and LED batten lights
MSA-DCS | WA3503934 | unit 7, B wing - Cell hatch will not close | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 09:25:27 | 2020-07-30 12:30:00 | Pass | DOOR HATCH REPAIRED
MSA-DCS | WA3503942 | Unit 3 - D Wing window will not stay up when opened and the spiral wire strip is sticking out | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-07 12:00:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3503962 | External stores - holes in ceiling cell | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo **PLEASE USE VENDOR S12018** | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 08:30:00 | Pass | HOLES IN CEILING PATCHED
MSA-DCS | WA3504002 | Visits/Kitchen - Door frame requires stabilising | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Corridor - Between Main Kitchen and Supermarket | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-19 11:00:00 | Fail | NEW DOOR FRAME FABRICATED & FITTED
MSA-DCS | WA3504003 | House 16, Bathroom- Rectify termite damage to vanity unit & skirting | Boronia Pre-release-AK23 - Prisoner Accommodation House 6 and 7 | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-09-23 13:31:00 | Fail | REMOVAL DAMAGED AREAS - REPLACE NEW SKIRTING AND VANITY - PAINT
MSA-DCS | WA3504009 | Unit 14, A9 - Shower blocked flooding cell floor when showering. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 10:51:37 | 2020-07-30 11:52:00 | Pass | Used acid and plunger to clear blockage in shower drain
MSA-DCS | WA3504021 | Front gate, sally port - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 15:30:00 | Pass | Replaced 2 lights
MSA-DCS | WA3504067 | Reception, Sally Port- Door bell broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 13:00:00 | Pass | Repaired buzzer
MSA-DCS | WA3504131 | Unit 14, Control PA System intermittently working. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-05 14:00:00 | Pass | Replaced cell call handset with new CG-OH, test PA and cell call. Job completed.
MSA-DCS | WA3504248 | SHU, Office - security monitor (SH Control) not workig, it shows blank screen | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-26 15:04:00 | Fail | Sourced HDMI extender from seme stock.Installed new extender and 2x HDMI cables from seme stock and restored image on CCTV screen
MSA-DCS | WA3504264 | ground/hallways 3x Break Glass not working and Reed Switch in boardroom not working-see notes | Rockingham Justice Complex | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-05 09:00:00 | Fail | Traced cabling and sitting in breakglass and terminated. Terminated cable in and traced in cabinet. Programmed. All OK.
MSA-DCS | WA3504267 | G Floor - Strobe and Siren not working | Rockingham Justice Complex | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-31 11:45:00 | Fail | Ran cable to new location for strobe and siren. Terminated all connections and tested operation.
MSA-DCS | WA3504411 | Gate house, arunta room - PE beam in Alarm | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-07-31 16:10:00 | Pass | Fence recently removed. Fence been in alarm since 17/7/2020Fuse has blown, replaced fuse, PE beams alarming non stop.Realigned all PE beams and re attached cover as cover partially off
MSA-DCS | WA3504413 | Gate house, MDAS server failed | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-10-27 13:22:00 | Fail | work order to be invoiced at cost to date, new work order to be released.
MSA-DCS | WA3504414 | Security section - PE7-M-R-B-1 in alarm | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-07-31 16:11:00 | Pass | Re aligned PE beam on rooftop
MSA-DCS | WA3504415 | Gate - MSB 1 &2 showing as open | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-05 16:28:00 | Pass | Doors have been replaced. Drilled reed switch holes and mounted magnets
MSA-DCS | WA3504417 | TR5 in tamper | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-07-31 16:12:00 | Pass | Tamper switch has fallen down.Resecured tamper switch in cabinet and adjusted
MSA-DCS | WA3504419 | MSM workstation sound is not working | Broome Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-07-30 19:43:00 | Pass | Speakers failed on Gallagher WS.Advised gallagher workstation requires second monitor as officer unable to view alarms and control access through one screen efficienctly.Approval to add second monitor with inbuilt speakers
MSA-DCS | WA3504436 | Unit 2- Door controls are down | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Jul 2020 | 2020-07-30 20:52:28 | 2020-07-30 18:15:00 | Pass | Unit 2 Door Control not working. Screen is black so rebooted PC into safe mode. Checked system and service, all is ok. Rebooted PC back into Windows and system is now up. Controls are back and all working.
MSA-DCS | WA3533705 | Admin computers not working, no power | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 30 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-14 08:38:00 | Fail | Repaired computers
MSA-DFES | WA3503630 | toilet near gym fluro not working cover has fallen off | CFRS Claremont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 30 Jul 2020 | 2020-07-30 17:00:00 | 2020-07-30 10:45:00 | Pass | Replaced faulty light with new
MSA-DFES | WA3504148 | Front gate is not activating the “Gate Reed Switch” when closed,- further info below | FESA RHQ - Forrestfield | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-04 14:00:00 | Pass | 31/7/20 - Dean Simpson, Joshua ParkAsked to also look at boom gate. Security system working ok, Boom tripping 16A MCB, advised that gate contractor required.Checked MRS on vehicle gate, working ok locally, signal not receiving on main system. Need to return and test more.4/8/20 - Dean Simpson, Joshua ParkReset controller and replaced connectors.Tested all working ok
MSA-DFES | WA3504150 | Gym - Large wall mirror is cracked and broken (one section of broken glass has come away completely) | CFRS Canning Vale | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-09-08 13:30:00 | Fail | Waiting on reply to BRAF RequestNew mirror installed
MSA-DFES | WA3504153 | Level 2, north end- Zip tap boiling water function not working | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-31 11:38:00 | Pass | Replaced faulty hot pump. All now working ok.
MSA-DFES | WA3504186 | USAR Shed- Rat / mice infestation in shed, further info below | CFRS Canning Vale | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 11:30:00 | Pass | Carried out a service for rodents at Canning Vale Fire Station. Installed eight fully baited rodent stations, four in the back shed, one on the outside of the back shed, one in the laundry, one on the outside of the station and one in the kitchen. Inspected and replenished all existing rodent stations. It's highly recommended that all rodent stations are inspected and replenished at least every three months.
MSA-DTAG | WA3503855 | Registry Office - Monitor for Security screen not showing any cameras as operational | Mandurah Courthouse | GMP-BR-HO | Security | Monitoring (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-31 10:15:00 | Pass | 31/7/20 - Dean Simpson, Joshua ParkNo cameras showing on security screen.NVR and cameras do not match Pc time.Re-synced NVR and cameras.Tested, all working ok.
MSA-DTAG | WA3504014 | Court 2 entry door lights isn’t displaying when door is locked/unlocked | Armadale Courthouse | WSM-BR-SITE | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 14:45:00 | Pass | 30/7/20 - Dean SimpsonResoldered connections on unlock LED, all working correctly.Replaced lock LED, all working correctly.
MSA-DTAG | WA3504151 | Drain outside court 2 has become blocked with leaves that is preventing water to drain and backlog | Joondalup Courthouse | GMP-BR-HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-07-31 13:00:00 | Pass | Complete
MSA-DTAG | WA3504185 | Custody Staff, Accused In Custody person has urinated-see notes | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-30 21:30:00 | Pass | Job carried out as per work order.
MSA-DTAG | WA3504216 | ground level - Door between Waiting Area & Secure Registry Area gives electric shock to some people | Mandurah Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-31 11:00:00 | Pass | 31/7/20 - Dean Simpson, Joshua ParkStripped break glass unit and re-terminated the connections.Sleeved the cable on the request to exit button.No electric shock from any device.Tested and all working ok.No call out fee as already onsite.
MSA-DTAG | WA3504434 | Irwin st end carpark - Lights inside the carpark are not working | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, External (EL) | AWB Co. | 0 | CLOSE | 30 Jul 2020 | 2020-07-30 20:43:40 | 2020-07-30 19:45:00 | Pass | Job complete. Suspect paper tube which labelled circuits behind switch caught fire
MSA-DTAG | WA3504444 | Irwin st end carpark - Reed switch has blown - Fire panel requires reset | Central Law Courts | GMP-BR-HO | Electrical | Materials (EL) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 30 Jul 2020 | 2020-07-30 21:40:19 | 2020-07-30 18:15:00 | Pass | Attended site for FIP Alarm after hours call out, no alarm on arrival or in logs.System normal on departure
MSA-DTWD | WA3503580 | K block K12 male toilets blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 30 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-03 16:00:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3503700 | T block cafeteria freezer large build up of ice on the coils. | Murdoch Campus | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-10-01 12:32:00 | Fail | Traveled to site and signed in. Located Cafeteria freezer room and found that coil had partially iced up. Found that defrost element does not seem to working correctly. Braf will be submitted to pump down unit, move evaporator to access the heaters, install new heaters and reinstate system.
MSA-DTWD | WA3503848 | A block, Room A236 - Carpet tiles damaged, see below for further info | Leederville Campus | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-07-31 15:00:00 | Pass | Carpet removed and tiles installed as requested by site
MSA-DTWD | WA3503852 | E block E58 LSK target top gas cooker gas will not stay on | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-31 14:56:00 | Pass | COMPLETED 31/7
MSA-DTWD | WA3503860 | level 2, disabled toilet - cistern not filling | Perth Campus B5 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-30 15:30:00 | Pass | Fixed leaking toilet
MSA-DTWD | WA3503866 | Room A311 - completely lost power to 1 side of lab | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-30 16:30:00 | Pass | Job completed
MSA-DTWD | WA3504145 | K Block - Repair sticky lock in C & J Classroom (locked to fit AB key). | Mandurah Campus (formerly Peel) | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-31 10:45:00 | Pass | Job completed - replaced CYL/570 Cylinder 570 Restricted
MSA-DTWD | WA3504172 | T Block, Cafeteria- Tap is dripping badly | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 14:52:00 | Pass | Replaced timeflow tap
MSA-DTWD | WA3504173 | H Block, washdown pits are overflowing & maybe blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 16:00:00 | Pass | Unblocked drains
MSA-DTWD | WA3504262 | level 1, A101 - leaking tap | Perth Campus B5 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-07-31 11:15:00 | Pass | Fix leaking taps
MSA-DTWD | WA3504292 | A block A214 external door/entry to staff corridor repair to door handle-see notes | Leederville Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-03 09:25:00 | Pass | replace broken handles to A214 external door
MSA-DTWD | WA3504293 | Lvl 1, Room A101- Power point is faulty | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-05 12:15:00 | Pass | Attended site and signed in. Found supposed faulty gpo. Tested and retested gpo, no fault present. Job complete.
MSA-DTWD | WA3504319 | E block E500 Check 15amp GPO in the sheet metal workshop | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-04 10:28:00 | Pass | Attended site and signed in. Investigated machine out of service. Isolated and Made safe. Job complete.
MSA-DTWD | WA3504352 | E Block, Bistro- Male toilet leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-31 08:00:00 | Pass | Sealed leak on toilet
MSA-DTWD | WA3504364 | Lvl 2, Creche- Broken door handle | Perth Campus B1 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-06 11:15:00 | Pass | replace Lockwood 931 passage set on creche internal door
MSA-DTWD | WA3504421 | North Block, N222 Kitchen- Boiling Water Unit dispenser tap broken | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 30 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-31 12:15:00 | Pass | replace broken tap
MSA-DTWD | WA3504423 | Block 4, Room 4G7- White ant activity/damage to jarrah skirting boards – front of classroom | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 30 Jul 2020 | 2020-07-31 17:00:00 | 2020-07-31 08:15:00 | Pass | Carried out a service for termites at Thornlie Tafe. There were reports of termite activity located in room 4G7, upon further inspection determined to be old damage. Old damage was also located in a tree outside the classroom. A termite barrier and tree treatment is highly recommended.
MSA-DTWD | WA3504437 | Classrooms – 2, 3 & 4- 8x damaged light covers | Armadale Campus - 40 Commerce Ave | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-17 14:45:00 | Fail | Attended site and replaced faulty fluros. Replaced broken diffusers and replaced missing Tbar. All now working and safe.
MSA-MRWA | WA3504134 | Administration, front office - Please supply 2x Cabinet keys cut to code (2x Pair) (see notes) | Materials Engineering Branch | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 30 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-10 10:38:00 | Fail | Keys pick up from Advanced Lock & Key by Craig Jacka
MSA-DCA | WA3504977 | Lift 4 unresponsive | Art Gallery of WA - James St | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 14:30:00 | Pass | Lift 4 Art-Hydraulic :lift out of order with doors open, found no power to safety circuit and control circuits due to circuit breaker tripped in controller. Reset and tested circuits unable toreproduce fault, tested operation and could not reproduce fault left in service
MSA-DCS | WA3504542 | B2 perimeter sensor staying on and no one there | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 31 Jul 2020 | 2020-08-04 17:00:00 | 2020-07-31 10:52:00 | Pass | Zone B2 beamset false activating, removed some debree (gardens) from between beams and found some moisture, for bags now in bottom and beamset no longer in alarm, site to rectify gardens.
MSA-DCS | WA3504547 | Unit 1 - B7 Tap on the prisoner's sink is loose and needs securing as soon as practcle. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 07:54:25 | 2020-07-31 12:29:00 | Pass | Inspected cell. Adjusted and retightened loose basin tap.
MSA-DCS | WA3504559 | Unit 14 A3 Shower screen requires sealing. | Casuarina Prison | GMP-BR- HO | Building | Internal Screens (BU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 31 Jul 2020 | 2020-08-06 17:00:00 | 2020-09-03 09:30:00 | Fail | SHOWER SCREEN RE SEALED
MSA-DCS | WA3504562 | chapel near unit 2 smashed window | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 08:09:08 | 2020-08-07 13:45:00 | Fail | RE GLAZE WINDOWS
MSA-DCS | WA3504677 | programs rooms 2 zip auto boilers not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-08-06 11:51:00 | Pass | Asset capture complete of area. Blocked filters changed. Scaled taps cleaned and split tubing replaced. All ok
MSA-DCS | WA3504699 | Kitchen - gas deep fryer will not ignite | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 09:25:20 | 2020-07-31 15:30:00 | Pass | 31/07/20Attended Fryer Found corroded pilot assembly, low output from thermopile and corroded baffles, the right hand is the worst.Cleaned burners, checked burner pressure and operation of thermostat. Thermocouple output is low, but unit is staying on, but requires replacement.
MSA-DCS | WA3504721 | gate house door 1 - door 1 is logging fource door alarms on entry | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 13:48:46 | 2020-08-04 10:30:00 | Fail | Job completed under job WA3508412. Retested lock and Reed switch when problem resolved, both devices operating correctly, no further action required.
MSA-DCS | WA3504727 | zone 1A no activation-Seme on site | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 17:55:41 | 2020-11-20 08:30:00 | Fail | Confirmed that zone 1A Inner microphonics will be made redundant with the installation of the electric fence. Removed damaged cabling.
MSA-DCS | WA3504732 | zone 1B no activation - Seme on site | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 17:57:41 | 2020-08-24 13:00:00 | Fail | Replaced 2 Splice kits and a number of cable ties. Tested ok to the gatehouse. Parts used:2 x Splice kits Consumables
MSA-DCS | WA3504734 | zone 7 not activation middle set of MW - Seme on site | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 17:58:50 | 2020-08-06 16:37:00 | Fail | Repaired microwave set, calibrated and tested okJob Complete
MSA-DCS | WA3504736 | zone 9 MW B no activation - Seme on site | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 18:00:03 | 2020-08-05 15:54:00 | Fail | Repaired faulty PCB, recalibrated and tested OKJob Complete
MSA-DCS | WA3504740 | Zone 14A MW not activation - Seme on site | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 18:00:59 | 2020-11-18 09:30:00 | Fail | Installed reflective metal plate on the side of the sallyport wall for the transceiver to bounce the me beam off of. Repaired and tested ok. Parts used:600mm x 600mm metal plateConsumables
MSA-DCS | WA3504742 | Zone 4 outer MF no activation - Seme on site | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 18:01:54 | 2021-08-05 16:00:00 | Fail | Attended site and repaired fault.Tested OKJob Complete
MSA-DCS | WA3504746 | Gate House, Front Entrance - Fire alarms require resetting in the Pod | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-05 07:30:00 | Pass | 7/8/20 JNReset ODP flowswitch alarm all okay.
MSA-DCS | WA3504770 | Cell Calls not working after power failure | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 18:06:27 | 2020-07-31 11:19:00 | Pass | Call call not working after power failure, checked with site issue is contained to unit 6 which is under warranty, confirmed numerous cell call points in other areas / units fully operational. Confirmed with site they will contact the builds contractor.
MSA-DCS | WA3504773 | CCTV not working after power failure | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 18:09:28 | 2020-09-29 11:00:00 | Fail | Rack layout rearranged, installed new UPS on bottom of rack, acquire and install UPS IEC leads to all devices in rack. Test and commission UPS function.
MSA-DCS | WA3504785 | Unit 4, Control Room- Camera / Monitor is frozen that looks out to Unit 4 gate. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 10:18:17 | 2020-10-26 15:30:00 | Fail | Returned to unit to check cable terminations, staff advise no problems with picture. Circuit is working. No further action
MSA-DCS | WA3504855 | front door not closing manually or with swipes | Rockingham | GMP-BR- HO | Security | Monitoring (SE) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 14:52:46 | 2020-07-31 16:00:00 | Fail | Technician attended the site of Rockingham Justice Complex to the Front Main Entry Automatic Door # W28535 on 31/07/2020. Following full test and inspection of door components identified fault was the access reader holding door open, door in auto mode via key switch, and remote receiver active (door in lock mode). Staff are unable to know if the remote has locked the door or not. Door requires to have a low level buzzer and light fitted, with a sign to indicate door has been locked via remote so staff are aware. Full test and inspection of door components completed prior to leaving site.Quote has declined.
MSA-DCS | WA3504919 | Kitchen - The gas rational oven stops & show the following message “Check gas supply” with a button | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Office - Main Kitchen | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-05 15:55:00 | Pass | Replaced Ignition Module & Burner Blower tested ok.
MSA-DCS | WA3504921 | Metal shop near entrance door - Fire door swollen and unopen able needs repair/changing | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Midolo **PLEASE USE VENDOR S12018** | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 11:24:22 | 2020-07-31 14:45:00 | Pass | ASSESSED JOB - NOT FOR MIDOLO
MSA-DCS | WA3504941 | Amenities - no hot water | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 11:56:28 | 2020-07-31 15:00:00 | Pass | Investigate amenities HWS. Found tripped circuit. Test HWS and amenities circuits. Discussed with plumbers. They will quote to replace HWS.
MSA-DCS | WA3504962 | Visist centre, CCTV camera monitor faulty | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 12:01:08 | 2020-07-31 15:00:00 | Pass | Attended fault and found issue with user permissions for Indigovision software. Re-set and re-programmed user group for correct privelages. Tested alarm zones and confirmed correct operation and workstation. Job complete
MSA-DCS | WA3504993 | Unit 6, Cell B5- Sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-07-31 14:02:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3504995 | Amenities - Water leak on hot water units | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-08-04 09:00:00 | Pass | nil
MSA-DCS | WA3505007 | Unit 7, Cell E24- Toilet Cistern broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-04 13:55:00 | Pass | Reconnected laundry trough and replaced trap
MSA-DCS | WA3505008 | Unit 4, B Wing cleaning cupboard- Sink hanging off wall | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-05 15:05:00 | Pass | Removed broken cistern in duct and installing new one
MSA-DCS | WA3505009 | D wing day room Door lock faulty, jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-07-31 15:15:00 | Pass | Repair to lock
MSA-DCS | WA3505017 | Unit 1, Cell A8- Vinyl Flooring Lifting Up | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-10-30 15:00:00 | Fail | DAMAGED FLOORING UPLIFTED & REPLACED WITH NEW
MSA-DCS | WA3505025 | Unit 1, At End Of A-Wing- Damaged vinyl flooring | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-09-30 12:30:00 | Fail | DAMAGED SECTION UPLIFTED & REPLACED
MSA-DCS | WA3505028 | Unit 1, At End Of C-Wing- Damaged vinyl flooring | Melaleuca Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-09-30 14:00:00 | Fail | DAMAGED SECTION OF FLOORING REMOVED/ REPLACED
MSA-DCS | WA3505029 | Unit 1, A15 - Bed panel broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 13:09:26 | 2020-08-03 16:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels.
MSA-DCS | WA3505030 | Unit 1 A8 Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-04 04:00:00 | Pass | Attended site and carried out repairs to the broken end panels on bunk beds.
MSA-DCS | WA3505048 | Unit 1 A8 broken shower tiles | Melaleuca Prison | GMP-BR- HO | Building | Internal Walls (BU) | Schlager Construction Group | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-09-10 11:00:00 | Fail | Attended site and carried out repairs to broken tiles in shower recess and cell floor.
MSA-DCS | WA3505054 | Unit 1 A11 Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-03 15:00:00 | Pass | Attended site and carried out repairs to the damaged bed panels.
MSA-DCS | WA3505131 | Kitchen - slicer plug fault casring outlet to trip | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-04 15:00:00 | Pass | Repaired faulty slicer in kitchen
MSA-DCS | WA3505172 | Mitchell house blocked toilet drains | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 31 Jul 2020 | 2020-08-01 14:17:21 | 2020-08-02 14:00:00 | Fail | Complete
MSA-DCS | WA3505195 | Unit 4 - B11 slats on top of bunk are broken. Will require a new slat and a welder. | Casuarina Prison | GMP-BR- HO | Furniture | Commercial Furniture (FU) | Midolo **PLEASE USE VENDOR S12018** | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-08-17 11:00:00 | Fail | WELD NEW PIECE OF METAL TO TOP BUNK
MSA-DCS | WA3505197 | INF(10)- Treatmean room- fluro light tube not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-08-05 11:30:00 | Pass | Repaired faulty lights in infirmary treatment room
MSA-DCS | WA3505204 | Unit 4, C wing - slight flickers on and off and cannot be switched on from outside | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-08-05 11:30:00 | Pass | Investigate and repair unit 4 cell C6 cell light
MSA-DCS | WA3505343 | Casuarina Prison - ODP Area - Fire alarm was activated. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 22:56:14 | 2020-07-31 21:15:00 | Pass | After hours call to Casuarina Prison for fire alarmODP Sprinkler valve room pressure switch activated but latched in alarm but normal device N11:M1-16 . Disabled then enabled to reset ok.Checked pumps found they hadn’t run.Left system normal.
MSA-DFES | WA3504513 | ground CL&D Male Toilet Urinal continuously flowing after flushing | DFES Regional Office - Belmont | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 31 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-04 11:30:00 | Pass | Attend site to repair leaking cistern in male toilets fit new outlet washer clean and check outlet valve set levels check operation
MSA-DFES | WA3504514 | CL&D Male toilet Light faulty | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 31 Jul 2020 | 2020-08-04 17:00:00 | 2020-08-04 15:00:00 | Pass | Complete Replaced light in male toilet all in working order
MSA-DFES | WA3504518 | ground sliding gate key pad for auto sliding gate sticking | CFRS Malaga | GMP-BR | Building | Steel Fencing & Gates (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 3 | CLOSE | 31 Jul 2020 | 2020-08-06 17:00:00 | 2020-08-13 16:30:00 | Fail | Technician attended the site of Malaga Fire Station, Sliding Gate on 06/08/2020. Following a full test and inspection of door components found fault to be external keypad intermittently not working. Keypad is sun damaged and when the tech has removed item from pillar he found cable connections to be corroded. He re-terminated cable connections and tried to refurb keypad as best he could. Keypads seems to be working better but technician would recommend replacing device to ensure operation in future.13/08/2020 Technician returned on site to remove faulty keypad and replaced it with a new one.Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3504930 | ground admin Eastern end external door of Administration Building not closing correctly. | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-03 12:15:00 | Pass | Adjusted door closer - eastern exit from admin. Door now closing properly
MSA-DFES | WA3505003 | Stair 3 door not closing | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 0 | CLOSE | 31 Jul 2020 | 2020-07-31 16:49:59 | 2020-07-31 15:00:00 | Pass | Applied loctite to door fixings and tightened all
MSA-DFES | WA3505033 | ground male toilet last cubicle toilet blocked | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-07-31 15:30:00 | Pass | UNBLOCKED TOILET AND BASIN
MSA-DTAG | WA3504673 | Office of Mazza JA - Light flickering at office entrance. Globe also out in chandelier | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-06 07:00:00 | Fail | Replaced blown lamps and tested working
MSA-DTAG | WA3504697 | registry ground Cell Camera 4 in Custody is not displaying on monitor feed.-see notes | Mandurah Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-06 13:45:00 | Fail | 31/7/20 - Dean Simpson, Joshua ParkTested camera, power supply all correct.Camera not powering up.Recommend replacement.6/8/20 - Dean Simpson, Joshua ParkReplaced faulty camera and tested.
MSA-DTAG | WA3504698 | Basement, Judicial Parking Garage - Light out above secure door. | Supreme Court | WSM-BR-SITE | Electrical | Lighting, External (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-03 09:00:00 | Pass | Replaced blown lamp and tested working
MSA-DTAG | WA3504797 | 1st floor, Court 2 Stairwell - Light out in stairwell between jury room & Court2. Access via Room221 | Supreme Court | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-04 22:30:00 | Fail | Replaced to LED due to access restitutions
MSA-DTAG | WA3504853 | main staff kitchen - No hot water from Billi unit | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-07 14:30:00 | Fail | No hot water on arrival. Not heating. Element rusted and not working. Replaced element. Unfortunately due to excess rusting, the hot tank split and needs replacing. Will return today with a loan unitHave returned and installed loan unit.Have replaced total hot tank with all the fittings and parts in the workshop. Today was only to re install and remove loan unit. Tested under pressure, normal operation
MSA-DTAG | WA3505233 | L2 Sheriff's office Excessive noise from A/C can be heard in Mark Street’s office | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-10-13 08:00:00 | Fail | Attend site. Investigate areas with issues.Carry out airflow survey on whole system. Check all outlet mounting for correct installation. Report on findings and recommendations.
MSA-DTWD | WA3504586 | T block, cafeteria - floor drain to main to kitchen is blocked and water not draining, just sitting | Murdoch Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-03 12:00:00 | Pass | Unblocked rampant and replace grates So can be cleaned out
MSA-DTWD | WA3504604 | H block, outside, ground block - drink fountain is not operating | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-03 13:25:00 | Pass | No visible cause for unit to not work. Working ok. Returned bubbler line replaced tubing had a little damage from resting on heat exchange caused leak. Tightened faucet
MSA-DTWD | WA3504681 | A block, A225b Lift lobby- Drink fountain is leaking. | Leederville Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-08-05 11:45:00 | Pass | Fountain leaking from faucet handle And running down the outside of the fountain.Cleaned up water around unit. Replaced faucet and John guest fittings and tube on the inside of the unit. Flushed and checked under pressure
MSA-DTWD | WA3504695 | A Block, Room A131 Male toilet- Toilet pan is leaking. | Leederville Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Jul 2020 | 2020-08-07 17:00:00 | 2020-08-04 14:00:00 | Pass | Complete
MSA-DTWD | WA3504825 | faulty door lock in B Block room B7 | Murdoch Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-03 12:15:00 | Pass | Job completed - replaced Cylinder 570 Restricted - and 2 restricted keys
MSA-DTWD | WA3505047 | H block (Dolls house) - Termites require treating | Fremantle Campus (formerly WA Maritime) | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-05 13:20:00 | Pass | Inspected H Block building (Dolls House). Broke open termite workings and applied 10 Litres Fipronil @ .6%. Termite damage to 2 large posts.
MSA-DTWD | WA3505150 | A-Block 1st Floor room A118 aircon not working | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Materials (AC) | Precise Air Group | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-10-02 13:00:00 | Fail | Arrived on site. Signed in, accessed roof space, found can motor seized. Found new one and submitted quote Removed and fitted fan into you unit. Once installed it ran well for around 45 mins then slipped off the bearings holder's. Need to return tomorrow to fix Reinstalled original fan that was rebuilt, working well now
MSA-DTWD | WA3505154 | block 9 ground computer lab Computer 12 has a broken power point switch. | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-03 12:15:00 | Pass | Arrived at site signed in , completed a jsa , met with site contact , located dgpo in library computer lab , switch was faulty , isolated circuit , changed PowerPoint , tested PowerPoint , re-energised circuit , re tested PowerPoint ***job completed***
MSA-DTWD | WA3505187 | Piggery 876 Faulty water line | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 31 Jul 2020 | 2020-08-03 17:00:00 | 2020-08-05 14:00:00 | Fail | job completed - Supply and install new pressure pump
MSA-DTWD | WA3505295 | E Block, E20 Male Staff Toilet – Damaged Door Stopper | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-10 10:15:00 | Fail | Have attended site and replaced damaged door closer. Will need to return to repaint the door to cover the unpainted area where the original unit was installed as the new unit id smaller Small BRAF may be required
MSA-DTWD | WA3505315 | A block, disable toilet - faulty lights | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 31 Jul 2020 | 2020-08-05 17:00:00 | 2020-08-03 08:15:00 | Pass | Attended site and signed in. Located A block. Found disabled toilet light not working. Replaced tube and starters. Tested all okay. Job complete
MSA-DCS | WA3508062 | Key has snapped in the door lock located in official visits | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 01 Aug 2020 | 2020-08-01 11:27:41 | 2020-08-01 09:00:00 | Pass | Attend site after hours, repair lock.
MSA-DCS | WA3508069 | Unit 15 is flashing a light for macerator pump station in the main control box | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 01 Aug 2020 | 2020-08-01 11:58:14 | 2020-08-01 17:30:00 | Fail | nil
MSA-DCS | WA3508070 | automatic front gate is not opening | Broome Regional Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-05 16:29:00 | Pass | Installed individual fuses for front door and MPC cameras
MSA-DCS | WA3508079 | Casuarina Prison - in rear of unit 4 there is a burst water pipe | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 01 Aug 2020 | 2020-08-01 13:30:25 | 2020-08-01 12:00:00 | Pass | nil
MSA-DCS | WA3508080 | Perimeter zone 11 OM constant false alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Aug 2020 | 2020-08-01 17:35:30 | 2020-08-07 09:45:00 | Fail | Attended site.Checked FlexPS module,connections and conducted test.All ok at departure.No fault was found.
MSA-DCS | WA3508081 | Zone 12 OX constant false alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Aug 2020 | 2020-08-02 09:40:19 | 2020-08-04 15:12:00 | Fail | Sourced parts, attended site, performed calibrations, adjustments and walk tests.Tested OKMonitored overnight logs. Confirmed zone activated on both officer walk tests and was stable overnight.Job Complete
MSA-DCS | WA3508083 | EC3 coming up as a tamper | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Aug 2020 | 2020-08-02 09:42:41 | 2020-08-06 15:01:00 | Fail | Repaired tamper fault and tested OK
MSA-DCS | WA3508084 | EC3A coming up as a tamper | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Aug 2020 | 2020-08-02 09:44:41 | 2020-08-06 15:05:00 | Fail | Repaired tamper fault and tested OK
MSA-DCS | WA3508085 | Zone 1C MW constant alarm and will not reset | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Aug 2020 | 2020-08-02 09:45:27 | 2020-08-06 16:40:00 | Fail | Repaired microwave set, calibrated and tested okJob Complete
MSA-DCS | WA3508121 | Sally port-Vehicle entry main doors cant close -electrical fault | Casuarina Prison | GMP-BR- HO | Electrical | Materials (EL) | MARSHALL BEATTIE AUTOMATION | 0 | CLOSE | 01 Aug 2020 | 2020-08-01 20:39:24 | 2020-08-05 10:00:00 | Fail | Replaced PE beams. Fit, mount slightly higher due to cable length and seal. Test, all okay. Test operation of all 3 sets of PE beams, all okay
MSA-DCS | WA3508125 | CCTV Monitor #4 is faulty - Screen is not displaying. | Pardelup Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Aug 2020 | 2020-08-03 00:46:14 | 2020-08-05 12:30:00 | Fail | Checked and tested monitor connections in Hub building and in control room. All cable plugs good and connections secure. Unable to reproduce Fault, monitor operating correctly.
MSA-DCS | WA3508126 | MDAS System Faulty - Tri 3Unit 2 Office Perimeter Zone 11 + 12 | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 02 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-04 19:01:00 | Pass | Replaced MDAS enclosure from PFM stock
MSA-DCS | WA3508128 | The cardax system is not working. | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Aug 2020 | 2020-08-02 10:14:35 | 2020-08-03 15:12:00 | Fail | Power outage this morning at 5am.Gallagher server was offline. Restored server and tested system All online and communicating
MSA-DCS | WA3508134 | In staff area, key 29 is in the keybox but it appears to be signed off- inspect and repair | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Aug 2020 | 2020-08-03 07:37:47 | 2020-08-02 12:30:00 | Pass | Key 29 reporting out. Logged in as Admin & released key slot location. Checked key back in and tested operation. Slot is reporting correctly and working fine now.
MSA-DCS | WA3508138 | Broome Regional Prison -electronic gate pedestrain gate not operating | Broome Regional Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-06 07:55:00 | Fail | Lock intermittently jamming.Attempted to clean lock, still not working correctly.Replaced ES9000 from PFM stock in WKRP
MSA-DCS | WA3508171 | The canteen store- Camera 1 is not working at all. | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Sapio Pty Ltd | 2 | CLOSE | 02 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-04 15:30:00 | Pass | Attended site. Found Camera 1 online on arrival, checked all settings and recording as normal. On arrival Visits Camera2 was offline and had factory reset itself. Reconfigured camera, now working as normal.Job completed.
MSA-DCS | WA3508185 | Unit 15 is flashing a light for macerator pump station in the main control box | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 02 Aug 2020 | 2020-08-02 16:48:35 | 2020-08-04 14:51:00 | Fail | nil
MSA-DCS | WA3508201 | internal gate is not working can't open it | Melaleuca Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Aug 2020 | 2020-08-02 19:39:54 | 2020-08-02 18:30:00 | Pass | Found loose terminal, re wire hydraulic pin, test, all ok
MSA-DCS | WA3508202 | the keys box for unit 12,13 in not working can't be open | Casuarina Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Aug 2020 | 2020-08-02 19:57:21 | 2020-08-02 18:30:00 | Pass | Keywatcher Unit 11 & 12 last set of 3 boxes not communicating, also door not releasing. Power cycled all boxes and tested operation, all is in working order.tested door release and all is ok now.
MSA-DCS | WA3508207 | alarm screen - monitor 7-10 frozen cannot be reset | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Aug 2020 | 2020-08-02 22:33:12 | 2020-08-15 16:36:00 | Fail | Repaired software issue on camera server, modified operating system to prevent fault reoccuring.Tested OKJob Complete
MSA-DCS | WA3508208 | unit 2 b5 personal key is stuck in lock | Bandyup Prison | GMP-BR- HO | Building | Materials (BU) | ACE LOCK & SAFE | 1 | CLOSE | 02 Aug 2020 | 2020-08-03 18:43:35 | 2020-08-03 10:30:00 | Pass | Replaced damaged prisoners Privacy Lock on Cell B5 Unit 23
MSA-DCS | WA3508209 | the camera in the gate house is not working | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Aug 2020 | 2020-08-03 19:29:40 | 2020-08-03 15:12:00 | Pass | Sourced spare encoder and power supply.Arrived onsite, OIC advised power problems this morning.Checked camera, confirmed ok.Located encoder, PSU had failedUsed 1x Powertrans M9391A from seme stock
MSA-DCS | WA3508431 | Cell call activating u3 house 1 ,Cell3 jamming the whole system | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Aug 2020 | 2020-08-03 10:00:00 | 2020-08-04 18:56:00 | Fail | checked cell call, found corrosion on board. disconnected push button, cell call still calling .removed and installed new CI-CC.cell call working correctly.monitored while onsite.noted that cell call was installed by different contractor.no back box, wall has been roughly cut with grinder cutting into wall, cut through wall frame and mounted to the wall frame.
MSA-DCS | WA3508285 | House 8, Toilet Rear- Light switch faulty | Boronia Pre-release-AM26 - Prisoner Accommodation House 8 and 9 | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 10:00:00 | Pass | Replaced faulty switch
MSA-DCS | WA3508290 | Grounds, Backflow valve leaking | Boronia Pre-release-External Area | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 10:30:00 | Pass | Complete
MSA-DCS | WA3508296 | Rubber strip coming away from Emergency Exit door in Interview Room 5 stops door closing properly | East Perth | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 03 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-04 10:30:00 | Pass | Attended site and carried out repairs to the door seal on frame that needed repairs.
MSA-DCS | WA3508314 | Unit 13, A Wing, Cell A10- Obs light switch on the outside of cell light switch missing | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-05 10:00:00 | Pass | Investigate and replace unit 13 A wing cell A10 obs light switch
MSA-DCS | WA3508315 | Unit 1 control room computer is not connecting and staff are unable to acess TOMS. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-03 13:30:00 | Pass | Reported connection data to IT Help Desk (see details in Work Log). IT ticket No INC0025537Noted broken Electrical mounting block for Aerial connection, SO requested it be repaired. Removed broken block, refitted aerial module and fixed plate to flush box.
MSA-DCS | WA3508322 | Main gate, sensor on my gate is faulty | Wooroloo Prison Farm | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Aug 2020 | 2020-08-03 11:37:11 | 2020-08-03 10:30:00 | Pass | Travelled to site and tested main gate operation, checked relays, reed switches and microfonics. All tested ok, reed switches measuring correct resistance. Reset controller and tested for correct operation and all working ok. Issue seems to be related to an intermittent fault on the gate mechanical side. Requires Marshall beatie to further investigate mechanical side. Job complete
MSA-DCS | WA3508334 | Unit 5, B Wing, Cell B9- Exposed wiring on light switch | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 07:51:20 | 2020-08-04 07:30:00 | Pass | Investigate and replace unit 5 cell B9 bed light switch.
MSA-DCS | WA3508340 | Zone 2, inner mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 07:55:43 | 2020-08-25 14:00:00 | Fail | Replaced a number of cable ties. 1 MOhm end of line resistance ok. Tested to gatehouse ok.
MSA-DCS | WA3508342 | Zone 2, outer mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 07:57:18 | 2020-08-07 08:45:00 | Fail | Attended site.Checked FlexPS module,connections and conducted test.All ok at departure.No fault was found
MSA-DCS | WA3508343 | Zone 4, inner mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 07:57:50 | 2020-08-24 15:00:00 | Fail | Cut out a section of cable. Replaced 1 Splice kit. Replaced a number of cable ties. End of line resistance ok. Tested ok to gatehouse. Parts used:1 x Splice kit. Consumables
MSA-DCS | WA3508346 | Zone 5, inner mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 07:58:27 | 2020-08-24 16:00:00 | Fail | Replaced a number of cable ties. 1MOhm end of line resistance tested ok. Zone tested ok to the gatehouse. Parts used Consumables
MSA-DCS | WA3508348 | Zone 6, outer mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 07:58:55 | 2020-08-04 16:00:00 | Fail | Attended site and investigated the fault.Checked microphonics cable for any damage and replaced missing cable ties (used sundries).Checked EOL and Senstar module.Conducted test.All ok at departure
MSA-DCS | WA3508350 | Zone 7, outer mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 07:59:23 | 2020-08-05 10:00:00 | Fail | Attended site and investigated the fault.Checked microphonics cable for any damage and replaced missing cable ties ( used sundries).Checked EOL and Senstar module.Conducted test.All ok at departure
MSA-DCS | WA3508353 | Zone 8, inner mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 07:59:49 | 2020-08-25 09:00:00 | Fail | Replaced a number of cable ties. IM Ohm end of line these tested ok. Tested ok to the gatehouse. Parts used:Consumables
MSA-DCS | WA3508355 | Zone 8, outer mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:00:35 | 2020-08-05 13:00:00 | Fail | Attended site and investigated the fault.Checked microphonics cable and replaced missing cable ties (used sundries).Checked EOL and Senstar module.Conducted test.All ok at departure
MSA-DCS | WA3508356 | Zone 17, omnitrax no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:01:09 | 2020-08-05 10:09:00 | Fail | Investigated fault, found there is no omnitrax technology in zone 17. Zone 17 is the intelliflex afound the new temporary sally port. Tested and checked all omnitrax near temporary sallyport, monitored overnight and confirmed no false activations and officers walk tests functioned ok.Minrophonics on temporary sallyport has been recently installed by another contractor,Job Complete
MSA-DCS | WA3508357 | Zone 17, outer mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:01:45 | 2020-08-07 08:00:00 | Fail | Attended site.Found that zone 17 microphonics is new install by Honeywell - required attendance by their technician
MSA-DCS | WA3508358 | Zone 10, outer mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:02:23 | 2020-08-06 15:30:00 | Fail | Attended site and investigated the fault.Checked microphonics cable for any damage and replaced missing cable ties (used sundries).Checked EOL and Senstar module.Conducted test.All ok at departure
MSA-DCS | WA3508359 | Zone 11, inner mircophonics no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:02:52 | 2020-08-25 11:00:00 | Fail | Replaced a number of cable ties. Replaced 1 Splice kit. End of line resistance tested ok. Tested ok to the gatehouse. Parts used:1 x Splice kitConsumables
MSA-DCS | WA3508364 | Zone 11, mircowave no activation | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:03:18 | 2020-08-05 15:49:00 | Fail | Repaired fault, recalibrated and tested okJob Complete
MSA-DCS | WA3508391 | WWTP Chlolorine doser faulty | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 15:41:00 | Pass | Changed chlorine gas cylinders
MSA-DCS | WA3508397 | Unit 3, B & D Freezer faulty | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-05 11:00:00 | Pass | Fridge has lost refrigerant. Beyond economical repair. Maintenance to organise replacement from stores.
MSA-DCS | WA3508399 | Eyre C wing part of window frame has detached | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-14 12:00:00 | Fail | window frame repaired
MSA-DCS | WA3508406 | Medical Sluice room cistern constantly running | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-05 15:05:00 | Pass | Unable to repaired faulty cistern. Replaced cistern
MSA-DCS | WA3508410 | Unit 13, A Wing, Cell A10- Broken light switch | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-06 08:30:00 | Pass | Repaired faulty lights in unit 13 a10
MSA-DCS | WA3508412 | Gate House - Front Entrance door 1 causing alarm on main security management system. | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:29:44 | 2020-08-04 10:30:00 | Fail | Changed alarm from “Armed” to “Disarmed” on operator console and confirmed that alarms were no longer alarming on system. Suspect it was changed by accident by one of the Control officers.
MSA-DCS | WA3508413 | Unit 4, Cell C6- Tap is faulty | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-03 13:00:00 | Pass | Inspected cell. Retightened loose tap in basin
MSA-DCS | WA3508415 | Unit 14, A Wing, Cell A02- toilet leaking onto floor constantly, taps need flow turned down | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-03 16:00:00 | Pass | Adjusted water pressure in plumbing duct to prevent cell from flooding
MSA-DCS | WA3508417 | Unit 14, A Wing, Cell A06- Shower pressure low & toilet seat loose | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-03 14:00:00 | Pass | Adjusted water pressure in duct. Cleaned shower head.
MSA-DCS | WA3508421 | Unit 5, B Wing, Cell B2- Leaking hand basin tap | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-03 15:00:00 | Pass | Replaced leaking spindle in basin tap
MSA-DCS | WA3508423 | Unit 13, D Wing, Cell D10 shower screeen leaking onto prisoners bed | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo Building Services | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-17 15:00:00 | Fail | RE SEAL LEAKING SHOWER SCREEN
MSA-DCS | WA3508426 | Unit 6 - Day Room Hot water urn on the A/C side is not working. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 12:05:00 | Pass | Replaced level sensors
MSA-DCS | WA3508440 | Kitchen Floor scrubber still tripping power not fixed. | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-04 15:00:00 | Pass | Investigate floor scrubber. Appears to have fault on suction motor. Advised maintenance to return to supplier under warranty.
MSA-DCS | WA3508446 | Unit 6, Vacuum cleaner appears to have a faulty connection | Casuarina Prison | WSM-BR-SITE | Equipment | Cleaning Equipment (EQ) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-06 12:30:00 | Pass | Repaired vacuum cleaner in unit 6
MSA-DCS | WA3508450 | Unit 4, A & C Toaster plug is broken | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-05 13:00:00 | Pass | Investigate and repair unit 4 a&c toaster and kitchen gpo
MSA-DCS | WA3508451 | Unit 4 - B & D domestic toaster has stopped working | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-05 13:00:00 | Pass | Repaired faulty toaster in unit 4. BD side
MSA-DCS | WA3508452 | Unit 1, B & D Wing- Regi oven is not heating up | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:53:59 | 2020-08-04 11:45:00 | Fail | Fit new doorseal, timer & screws. test ok.
MSA-DCS | WA3508456 | Unit 4, Control Room- Vesda Fire Control Box constantly faulting | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-03 14:12:00 | Pass | Unit 4 Vesda pipes two Wings A and B low flow on pipes due to sample points being blocked.Accessed roof to clear sample points to restore flow to normal.
MSA-DCS | WA3508458 | Unit 4, D Wing- 2nd fluro down hallway is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 13:00:00 | Pass | Repaired light
MSA-DCS | WA3508461 | unit 4 PRU control 13 camera's are out and no video input | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 08:58:05 | 2020-08-03 15:15:00 | Pass | Attended site checked and found around 13 cameras in PRU Control showing blank screen. Checked the cameras analog signals in equipment are ok. Further check located the problem to be the faulty power supply of the Fiber modems in main prison equipment room. Replaced the power supply and tested all ok.
MSA-DCS | WA3508472 | Unit 3, Cell D10- Cell light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 09:30:00 | Pass | Replaced cell light
MSA-DCS | WA3508476 | Unit 3, Cell C8- Cell light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 11:00:00 | Pass | New light cover
MSA-DCS | WA3508483 | Unit 2, Control Room- Control Panel for water system continually faulting | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 14:46:00 | Pass | System faulty isolated I’ve lamp
MSA-DCS | WA3508487 | Unit 2, Cell B10- Cell call faulty | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 09:09:48 | 2020-08-03 14:30:00 | Pass | Tested, quiet audio in the cell. Intercom full of toothpaste. Removed intercom and cleaned. Secured and tested ok. Parts used:Consumables
MSA-DCS | WA3508522 | West Admin Boardroom- Ceiling Fluro broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 12:00:00 | Pass | Repaired light
MSA-DCS | WA3508526 | Visits, Non contact- Speaker system not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-03 16:30:00 | Pass | All speakers on the prisoner side and the visitor side booths tested ok. There was an issue with the request to exit buzzer in the visits office. Repaired fault with the button on Booth 3 prisoner side. All buttons activate the buzzer ok.
MSA-DCS | WA3508533 | Kitchen 5 th oven showing service fault 32-1 burner malfunction. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 09:21:32 | 2020-08-04 13:30:00 | Fail | 04/08/2020Called as requested to the oven showing error 32.1.Bottom ignition failure but the unit was in working order on arrival and when tested. Checked the service log and recorded the error to report back to Rational. Also checked the bottom ignition unit and the bus cables all found to be good also checked the control board again found to be good checked neighbouring ovens to see if error codes. Reported faults and was advised that the ignition unit should be replaced so contacted Comcater as is currently under warranty.
MSA-DCS | WA3508591 | unit 2 cell 18 cell call distorted-SEME on site | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 09:39:26 | 2020-08-06 16:30:00 | Fail | Attended site and checked cell call system in unit 2.Checked cell call intercom in cell 18 for any damage.Conducted test.Received loud and clear response from control room in unit 2.No fault was found
MSA-DCS | WA3508617 | Unit 4 - B Wing Cell b7: Officers GMK keys do not work on the door.-see notes | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-06 14:30:00 | Pass | Replace barrel, door plate and lock.Weld on strike plate
MSA-DCS | WA3508626 | Unit 2, C-D Wing Common Area - Water Cooler Drain is Blocked | Melaleuca Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 09:43:46 | 2020-08-04 07:48:00 | Pass | Tryed to plunge had no luck. pulled apart trap and waste pipe all clear. Tryed big drain machine wouldn’t fit will return with smaller one
MSA-DCS | WA3508641 | Kitchen, dishwash area - Washtech Dishwasher Spray Arm Clip Broken Panel Light Broken | Melaleuca Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-31 14:20:00 | Fail | 13/08/20Called as requested to identify dishwasher parts required. Parts required 1x red neon 1x spring clip31/08/20Fitted parts, Tested all ok.
MSA-DCS | WA3508662 | hosue 6, bathroom - light not working | Boronia Pre-release-AK23 - Prisoner Accommodation House 6 and 7-Ground Floor-House 6 - Bathroom 1 | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 11:00:00 | Pass | Replaced faulty light
MSA-DCS | WA3508694 | inner gate next to visits-need to know how to manual overide | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 11:23:19 | 2020-08-03 13:15:00 | Pass | Attended site and advised security manager how to manually override vehicle gate. Job complete
MSA-DCS | WA3508716 | Unit 2 A-B Side Programmes Room Store Room Lock Wont Unlock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 09:02:51 | 2020-08-03 15:00:00 | Pass | Serviced Lock & Key Barrel. Proper function restored.
MSA-DCS | WA3508730 | Unit, A-13 - Medical hatch Jamming | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 11:31:26 | 2020-08-03 15:30:00 | Pass | Serviced lock and key cylinder. Proper function restored.
MSA-DCS | WA3508788 | Unit 6, A Wing- Water Leak in plumbing duct in the slab where the copper pipe passes through from | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-09-02 16:00:00 | Fail | 5/8/20 - investigate cause of leak. Materials list made to collect and repair.
MSA-DCS | WA3508820 | Unit 3, Cell 21 - unable to be locked | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 13:30:00 | Pass | replaced faulty ( worn out ) prisoners privacy lock on cell 21 unit 3 New lock fitted to prisons system
MSA-DCS | WA3508829 | Unit 5, staff toilet - privacy lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 15:00:00 | Pass | Supplied and installed new privacy lock.
MSA-DCS | WA3508834 | West Admin, Stationary room - water leak form ceiling | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-11-23 09:00:00 | Fail | ROOF SHEETING & FLASHING RE SEALED
MSA-DCS | WA3508842 | Unit 1, D7 - toilet leaks from base | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-07 09:30:00 | Fail | Removed door panel on side of toilet replaced key seal on flush pipe and refitted plate back on
MSA-DCS | WA3508843 | Unit 1, A11 - toielt unale to flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-07 10:30:00 | Fail | Remove cistern replaced outlet washer and flush button
MSA-DCS | WA3508859 | West side recovery, recovery room - TV Brocken not receiving any channels. Aerial issue | Hakea Prison | WSM-BR-SITE | Equipment | Electrical Equipment (EQ) | Sapio Pty Ltd | 3 | COMPFIN | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-17 09:00:00 | Fail | Repairs to antenna
MSA-DCS | WA3508866 | Unit 1 - A8 Both glass panels of the cell door viewing window smashed as well as the sliding panel | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 12:25:41 | 2020-08-04 15:30:00 | Fail | NEW OBS PANEL AND SLIDING HATCH GLASS FITTED
MSA-DCS | WA3508867 | Unit 1, control Pod passage - Officer Security Emergency Button Broken | Melaleuca Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Aug 2020 | 2020-08-03 16:25:55 | 2020-08-03 15:30:00 | Pass | Attended site, found issue related to a power outage. Reset duress button and retested, cleared alarms at gatehouse and checked for any false alarms. All cleared and working ok. Job complete
MSA-DCS | WA3508874 | Unit 1 - A8 Upper bunk side panel destroyed | Casuarina Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Midolo Building Services | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 14:00:00 | Pass | FIT NEW PANEL TO BED SIDE
MSA-DCS | WA3508895 | Control Pod Medical Centre, Entrance Door From Spine - Electrical Lock Jamming | Melaleuca Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 12:33:17 | 2020-08-04 14:00:00 | Fail | Collected parts and attended site. Replaced with new ES9000 electric lock. All replaced and tested ok. Job complete
MSA-DCS | WA3508898 | Unit 1, A11 - shower tap wont turn off | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-03 15:30:00 | Pass | Replaced Hot side quarter turn tap
MSA-DCS | WA3508934 | Industries Coordinator office- outside light not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-03 14:30:00 | Pass | Replaced 3x LED batten lights
MSA-DCS | WA3509002 | Unit 2, Control Pod- No power | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 03 Aug 2020 | 2020-08-03 17:29:01 | 2020-08-03 16:00:00 | Pass | Reset power to control
MSA-DCS | WA3509012 | Unit 1 loose reed switches - House 1 Cell 5 | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-04 18:57:00 | Pass | installed RS and siliconed into place.checked all RS in house
MSA-DCS | WA3509014 | Unit 1 loose reed switches - House 4 cell 4 verandah | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-04 18:54:00 | Pass | installed new RSsiliconed into place checked all RS in house
MSA-DCS | WA3509017 | Unit 1 loose reed switches - House 5 cell 2 verandah & 5 verandah. | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-04 18:53:00 | Pass | Installed 2x RSused silicone to secure them into door frame .checked all RS in house
MSA-DCS | WA3509031 | Unit 1 House 2 Cell 1 missing reed switch. | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-04 18:51:00 | Pass | Replaced 3x RS and resistors.used silicone to secure them into door.
MSA-DCS | WA3509035 | Metal shop near entrance door - Fire hydrant door swollen and unopen able needs repair/changing | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | Automatic Fire Protection (ARA) | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 13:47:03 | 2020-08-04 08:28:00 | Pass | Inspected fire hydrant door , door appears to have swollen with the weather , door is made out of wood will require a carpenter to plain thedoor down a little for ease of opening.Advised PFM via email 5.08.2020, have not heard back so closing out this task.
MSA-DCS | WA3509087 | Front Gate, Gate house entry- Body Xray machine bligh light continously flashing | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-07 10:45:00 | Fail | Checked reset buttons and cabling from buttons to Maxpro subrack. Checked power supply that powers the subrack. Restarted PC and subrack. Tested ok but the system should be upgraded if the prison wants to continue to use it.
MSA-DCS | WA3509094 | Turnstart - exposed wires | Melaleuca Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-04 15:00:00 | Pass | Collected site and customised and installed metal blank plate over turnstyle to hide exposed cabling. All installed ok. Job complete Sundries used.
MSA-DCS | WA3509115 | Visits camera internal 2 is offline | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-10 17:11:00 | Fail | Camera back online.During power outage, the network switch in visits drops offline.
MSA-DCS | WA3509118 | Stores Camera 1 is not recording | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-10 17:10:00 | Fail | Checked camera recordings. Camera recording is stable.Logged into the camera and checked video settings and adjusted framerate and bit rate
MSA-DCS | WA3509174 | unit 1 cell A19 and A20 toilets are overflowing | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 15:21:49 | 2020-08-03 18:35:00 | Pass | Complete 2hour
MSA-DCS | WA3509215 | Gasbar Wing C Burst pipe | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 03 Aug 2020 | 2020-08-03 21:36:05 | 2020-08-03 20:30:00 | Pass | Complete
MSA-DCS | WA3509273 | Block K - Karikan Units - Cell call is not working | Banksia Hill Detention Centre-Accommodation | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Aug 2020 | 2020-08-04 01:33:56 | 2020-08-03 23:00:00 | Pass | Karakin cell call not connecting to the officer POD, rectified and fixed. Job completed.
MSA-DFES | WA3509182 | Simulation Centre Bunker basement ops floor Projector wall mounted control panel not working. | DFES Regional Office - Belmont | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 14:15:00 | Pass | Complete Attended site and found projector control unplugged under the floor, replugged in and tested all in working order
MSA-DFES | WA3509207 | Mutiple electrical faults - seems a phase of power has may dropped out | CFRS Midland | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 03 Aug 2020 | 2020-08-03 20:37:11 | 2020-08-03 20:30:00 | Pass | Investigated issue with power outage. Have tested and confirmed voltage is not coming in from the western power side of the SPD. Notified station staff that power is estimated to be reinstated at 8pm. Have also advised that if anything is not working correctly or any other issues arise when power is reinstated. To call through another job to investigate whilst power is available.
MSA-DTAG | WA3508649 | Ground, Registry, Fluro above counter 1 is not working | Midland Courthouse | GMP-BR-HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-10 08:30:00 | Pass | Replaced LED batten light
MSA-DTAG | WA3508950 | registry ground admin Automatic front door external sensor activating when no people are present. | Mandurah Courthouse | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-03 15:43:00 | Pass | 1076449. Found internal safety sensor intermittently picking up doors and causing doors to self actuate, adjusted sensor and checked over door, tested all ok
MSA-DTAG | WA3509015 | ground front door is not closing properly. Door opens but is taking up to 5 minutes to close | Perth Children's Court | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 17:00:00 | 2020-08-03 15:56:00 | Pass | Found door working on arrivle. Suspect possible fire alarm issue have advised site to monitor sensors and have fire alarm system tested .
MSA-DTAG | WA3509105 | 1st floor, rom 221 - Air Conditioning either too hot or too cold in Court 2 jury room | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 13:30:00 | Pass | Completed works as per service report, rectified temperature issues, all appears to be functioning satisfactory.
MSA-DTWD | WA3508311 | White ants at Number 12, by the door to the Metal Workshop | Perth Campus B5 | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 3 | CLOSE | 03 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 07:20:00 | Pass | Applied 5 litres Biflex Aqua to affected area
MSA-DTWD | WA3508328 | A Block, Zip Boiler requires de scale A226 IT staff kitchen | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 03 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-05 10:00:00 | Pass | Unit tap badly scaled up. De scaled which also fixed a slight drip to tap. Recommend an scale removing filter be added to unit.
MSA-DTWD | WA3508455 | A block L2 room 208 water leak in North West corner of room | Joondalup Kendrew Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 17:00:00 | 2020-08-06 15:00:00 | Fail | Removed ceiling tiles below leak, found small box gutter above, found corner and joint to be leaking, will return on dry dayReturned to site now weather has improved, cleaned and resealed around sumo/outlet in box gutter with silicone
MSA-DTWD | WA3508532 | C Block, Cafe lunch room - gas heater not working | Bentley Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-21 14:52:00 | Fail | Main board replaced on heater under warranty
MSA-DTWD | WA3508577 | K Block - Security lights faulty | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 15:30:00 | Pass | Attended site and signed in. Located K block and checked out switchboard for security overide. Couldnt locate one in switchboard. Found pe cell on roof. Put on harness to access roof. Tested out pe cell to have no power. Invetigated to find a pveride switch inside the creche. Tested to find switch no working on terminal. Swapped all cablig over to unused terminals and re tested. Pe cell working on auto and manual. All lights okay. Job complete
MSA-DTWD | WA3508618 | C Block, Room C33- Light switch is faulty | Midland Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 17:00:00 | 2020-08-04 11:30:00 | Pass | Attended site and signed in. Located faulty switched and assessed damage. Both switched spongy and In need of replacement. Replaced both switches and tested. All ok. Completed paperwork. Job complete.
MSA-DTWD | WA3508648 | A block L2 stairwell lift lobby stairwell door handle broken | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 17:00:00 | 2020-08-03 12:45:00 | Pass | Replaced broken handle
MSA-DTWD | WA3508673 | G Block, Male toilets - Tap is running | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Water (PD) | Techworks Plumbing | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 17:00:00 | 2020-08-04 09:30:00 | Pass | Water has been isolated as a temporary fix until a replacement tap can be sourced.The site has requested that we order in the part to replace the broken tap, we are currently sourcing this and will return when it arrives.
MSA-DTWD | WA3508712 | B Block, Stair Landing- Fluro light not working | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-06 15:00:00 | Pass | Attended site and signed in. Located stair landing and found fluro faulty. Supply and replace fluro with new led fitting. Tested all okay. Job complete
MSA-DTWD | WA3508735 | B Block-Kitchen Area of student lounge room- Ceiling has water leak | Murdoch Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 12:25:00 | Pass | work completed as per signature slip
MSA-DTWD | WA3508792 | V Block- Roof leak in entryway to V7 male toilet | Rockingham Campus | GMP-BR | Roofing | Tiled Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-25 11:30:00 | Fail | Repair works are complete. Will need to monitor during next rain to confirm repairs have been successful 25/8/20 - Site confirmed leak was resolved. Installed vent in hole made to inspect the roof from below while assessing the leak. Vent installed for future ceiling space access.
MSA-DTWD | WA3508826 | block 8 ground 8G32 Computer Lab Cable operated windows in ceiling opened and can’t be closed. | Thornlie Campus | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 17:00:00 | 2020-08-04 08:15:00 | Pass | Attended site and closed cable windows that were stuck open. Removed winder handles and left with site as requested
MSA-DTWD | WA3508849 | E block kitchen E74 2x leaking taps | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 15:30:00 | Pass | Fix water fixtures
MSA-DTWD | WA3508855 | block 8 L1 8F56 L/H air conditioner tripping RCD B23 | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 17:00:00 | 2020-11-30 10:57:00 | Fail | BRAF DECLINED, CHARGE FOR INITIAL CALL OUT.
MSA-DTWD | WA3508980 | T block near vending machine roof leak | Munster Campus (ACEPT) | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 08:30:00 | Pass | Gutters and rain-heads were found to be blocked. Cleaned and cleared gutter and rain heads. Site confirmed leak resolved. job complete
MSA-DTWD | WA3508986 | North Block, Room N102- Power has tripped out | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 03 Aug 2020 | 2020-08-04 17:00:00 | 2020-08-04 12:30:00 | Pass | Job complete
MSA-DTWD | WA3508996 | J Block, Classroom J7- Roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-25 10:15:00 | Fail | Will need to return with second man to complete investigation 25/8/20 - Cleared debris from roof valleys and gutters will need to assess during next rain to determine if work has resolved the issue
MSA-DTWD | WA3509016 | D Block, BMS not indicating heating temps comms lost | East Perth Campus | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | Building Automation & Electrical Services Pty Ltd | 3 | COMPFIN | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-10 00:00:00 | Pass | works completed - Work order to be closed out at $0 cost
MSA-DTWD | WA3509032 | A Block, Office A11 - Roof leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 12:00:00 | Pass | Attended site located leak, carried out temporary repairs - COnfirmed no further leaks - job completed
MSA-DTWD | WA3509056 | Main Entrance- Fault on Fire Panel | Perth Campus B6 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 09:00:00 | Pass | Attended site - investigate fault. In logs, fault is battery missing and device missing and device missing.L4 D83 - replaced batteries in wireless base (detector) - performed loop test *2 - system and code red normal.
MSA-DTWD | WA3509062 | Lvl 3, T Block- Zone 1 hot water unit is not working | Murdoch Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 14:37:00 | Pass | Hot water system electrically fault fixed required rheem service man
MSA-DTWD | WA3509075 | Level 7, Kitchen staff office - Cabinet base is broken | Perth Campus B1 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-09-25 10:45:00 | Fail | Level 7, Kitchen staff office - Cabinet base is broken - replace with new
MSA-DTWD | WA3509102 | A block, level 3 - AHU 1 and 3 A Block not reaching Set temp Only around 18 degrees | East Perth Campus-Block A | GMP-BR | Building | Materials (BU) | Building Automation & Electrical Services Pty Ltd | 3 | COMPFIN | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-10 00:00:00 | Pass | works completed - Work order closed at $0 cost
MSA-DTWD | WA3509154 | B blcok, B16 - B16 Male toilet is blocked 2nd cubicle | Midland Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-03 16:15:00 | Pass | Cleared blockage using plunger
MSA-DTWD | WA3509157 | F block FG23 work shop Damaged Suspended 10A Outlet | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 08:45:00 | Pass | Attended site and awaited access to F23. Signed in and got keys. Located faulty gpo. Supply and replace with new 10 amp suspended gpo. Tested all okay. Job complete
MSA-DTWD | WA3509169 | E block ground Baytree Deli, the anode keeps rusting up | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 2 | CLOSE | 03 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 08:45:00 | Pass | completed 5/8
MSA-DTWD | WA3509195 | A block, level 3 rooms A347, 349, 351 - Fault security system; zone ID displaying as always 'Armed' | Leederville Campus | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-05 12:30:00 | Pass | 05/08/2020, 1200-1230User error. Area 2 is duress area. Open signals sent when disarmed
MSA-DTWD | WA3509198 | Level 2, N222 records - Broken exhaust fan | Perth Campus B1 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 03 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-10 13:52:00 | Pass | Repalced faulty exhaust fan.job completed
MSA-DCA | WA3509832 | external tap on Obs deck is leaking-see notes | Swan Bell Tower-Main Building-Level 6 - OBSERVATION DECK | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-05 09:51:00 | Pass | Replace garden tap lvl 6
MSA-DCA | WA3509840 | Toilet Exhaust fan is not working | Swan Bell Tower-Main Building-Level 1 | GMP-BR | Electrical | General Electrical (EL) | Precise Air Group | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-05 09:23:00 | Pass | Attended site and signed in.Inspected exhaust fan system and found level 1 exhaust fan interlinked with level 2 aircin which is not running due to site being closed.Could not rewire without major changes. Requires either ac1 on level 2 to be running or to manual on exhaust fan. Reported both options to staff.
MSA-DCA | WA3510261 | loading bay water leaking on the wall between loading bay and store room | Collection and Research Centre Welshpool-Harry Butler Centre | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-05 15:45:00 | Pass | Replace leaking section of 15mm pipe
MSA-DCS | WA3509361 | Remove asbestos PIT in the way of contractors works (SEME) | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 04 Aug 2020 | 2020-08-10 17:00:00 | 2020-09-09 10:00:00 | Fail | PIT REMOVED AND REPLACED WITH NEW - CONCRETED AS WELL
MSA-DCS | WA3509374 | Unit 6, Cell A6- Faulty lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 06:59:01 | 2020-08-05 10:45:00 | Fail | 04/08/2020 - Attended and determined parts required.05/08/2020 - Returned with required parts and replaced faulty components.
MSA-DCS | WA3509398 | Education, Admin external door- Door wont lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 09:00:00 | Pass | Adjusted strike and door closer to allow proper operation
MSA-DCS | WA3509405 | Education, Music Room- Gas heater again not working correctly | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-21 12:30:00 | Fail | Inspect room heater Unit under warranty Contacted manufacturer for service callWaiting on confirmation
MSA-DCS | WA3509415 | Gym, Recreation room - Door wont lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 09:30:00 | Pass | Adjusted strike to allow proper function.
MSA-DCS | WA3509430 | Laundry, Dryer No 3- Faulting . Fault Code “Check Control Board Fuse “ | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 07:36:34 | 2020-08-04 13:06:00 | Pass | AMS667612 WA3509430 - Hakea -No 3 Dryer control fuse Replaced fuse checked wiring for fault. Ran unit through 2 cycles with no fault.
MSA-DCS | WA3509432 | SHU (9),Cell B3 - Light above bed not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 15:00:00 | Pass | Repaired faulty lights in SHU b3Waited access for cell
MSA-DCS | WA3509435 | SHU (9),Cell B2 - Light above bed not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 15:00:00 | Pass | Waited in access to shuInvestigate and repair ahu cell B2 bed light and obs light
MSA-DCS | WA3509453 | Unit 1, C Wing, Cell C8- Viewing hatch smashed | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 11:00:00 | Pass | VIEWING WINDOW GLASS REPLACED
MSA-DCS | WA3509457 | Unit 1, C Wing, Cell C8- Lower shelf has been smashed | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 12:00:00 | Pass | TOOK OUT SHELF AND PATCHED UP WALL
MSA-DCS | WA3509460 | Unit 1, B Wing, Cell B4- Back window is damaged | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 14:00:00 | Pass | SPIRAL BALANCES REPLACED
MSA-DCS | WA3509463 | Unit 1, A Wing, Cell A9- Bunkbed is damaged | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 15:00:00 | Pass | FIT NEW PANEL TO BED SIDE
MSA-DCS | WA3509467 | Unit 1, A Wing, Cell A10- Toilet is constantly running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 16:00:00 | Pass | Replaced broken inlet valve which was damaged by someone other than the onsite plumber
MSA-DCS | WA3509468 | Unit 14, A Wing, Cell A4- Shower drain blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 08:30:00 | Pass | Used acid and plunger to clear blockage in shower drain.
MSA-DCS | WA3509471 | Unit 6, B & D- Hot water urn side flashing light | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 04 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-04 12:20:00 | Pass | Reset and disable filter count
MSA-DCS | WA3509475 | MPU (8)- Cell A8- Main light is flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-06 10:00:00 | Pass | Repaired faulty lights in mpu a8
MSA-DCS | WA3509492 | Outcare - Lunch Room Light in staff kitchen flickering. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-05 10:00:00 | Pass | Repaired faulty lights in outcare kitchen
MSA-DCS | WA3509503 | Admin- Air Con not working, "error U4" | Warminda Hostel | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-05 09:00:00 | Pass | Arrived on site and found unit showing U4 fault code. Reset power to the unit to reset fault. Unit running all ok.
MSA-DCS | WA3509582 | Unit 10, Cell A16 - Pin missing on bottom hinge to cell door | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 08:44:56 | 2020-08-05 11:45:00 | Fail | 04/08/2020 - attended and determined replacement required, parts needed.05/08/2020 - returned and fitted replacement hinge.
MSA-DCS | WA3509587 | Unit 10, Main Entrance door- Bottom door hinge faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 08:48:17 | 2020-08-04 14:20:00 | Pass | Adjusted both hinges on door to ensure proper operation.
MSA-DCS | WA3509592 | Unit 10, Cell A15- Lower hinge on cell door broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 08:50:08 | 2020-08-05 12:45:00 | Fail | 04/08/2020 - attended and determined replacement required, parts needed.05/08/2020 - returned and fitted replacement hinge.
MSA-DCS | WA3509598 | Unit 9, Medical Room- Light is faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-11 11:00:00 | Fail | Replaced broken lights.
MSA-DCS | WA3509606 | Unit 7, Cell G7- Light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-05 11:30:00 | Pass | Replaced switches
MSA-DCS | WA3509609 | Unit 9, D Wing- Shower light tripping out | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 08:56:46 | 2020-08-05 09:00:00 | Fail | Tripping lights
MSA-DCS | WA3509612 | Unit 6, A Wing- Water leaking from service duct between A7/A8 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 11:30:00 | Pass | Turned off mains water to unit to replace tap valve and washer
MSA-DCS | WA3509623 | unit 4 door outside control leads outside of prison swipe not working correctly | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 09:05:06 | 2020-08-05 14:00:00 | Fail | Readers on the internal and external sides of the door recognise the presented card every time. Approximately 1 in every 10 times the latch on the door strike would not open properly. Reset power to strike and sprayed with Inox lubricant. Tested ok
MSA-DCS | WA3509665 | Gate House -Door handle on the inside closest to the gate desk going through to get keys is loose | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 14:15:00 | Pass | RE-NEW DOOR HANDLE AND MADE SECURE
MSA-DCS | WA3509671 | Insense on zone 13 - constant alarm | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 09:36:43 | 2020-08-04 12:15:00 | Pass | Attended site, investigated fault and found that inner microfonics fence zone 13 was constantly activating due to join in cable damaged and disconnected from terminal block. Repaired and re-terminated device and re-cable tied section of zone 13. Re-tested and all tested ok. Job complete
MSA-DCS | WA3509678 | Pest treatment-excessive ants around demountables possibly infestation into building | Nyandi Training Academy | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-10 12:40:00 | Fail | Treatment of infestation of ants around demountable
MSA-DCS | WA3509689 | Amenities has no hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 09:48:22 | 2021-02-18 15:35:00 | Fail | Works now under a new work order
MSA-DCS | WA3509762 | Outpatients Area - Aircon for medical centre will not start up | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 10:26:45 | 2020-08-06 10:00:00 | Fail | Successfully ran up units, locked out from controller. All ok.
MSA-DCS | WA3509768 | Cleaning - Day Room The water in the water fountain isn’t tasting too good (stale), | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-07 11:40:00 | Pass | CHECKED SYSTEM NEEDS TO HAVE FILTER SYSTEM ATTACHED BUT CANNOT DO THAT SAFELY WITHOUT REPLACING DIFFERENT FOUNTAIN TYPE SO FILTERS CAN BE PLACED INSIDE CLIENT DECLINED REPLACEMENT
MSA-DCS | WA3509817 | Skills, hairdresser- Overhead lights are blown (they are dome lights), further notes below | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-26 09:00:00 | Fail | Replaced faulty lamps in workshop
MSA-DCS | WA3509839 | Visits centre, control pod- cameras screens have frozen | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Aug 2020 | 2020-08-04 15:01:40 | 2020-08-04 13:15:00 | Pass | Attended site and found visits PC frozen. Restarted PC and reloaded all camera presets. All reset and tested ok. Job complete
MSA-DCS | WA3509899 | Gatehouse- Repeating Alarm in Control (PTX Echo 4, Perimeter alarm) | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-11-12 09:00:00 | Fail | Two technicians on site. One walk tested Zone while other Tech calibrated Equipment. Zone tested to confirm activations.
MSA-DCS | WA3509909 | Ground floor, Public toilet - Replace lighting in public toilet with LED - note that existing light | Rockingham Justice Complex | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-05 14:00:00 | Pass | Replaced 2 lights in public toilet for LED lights
MSA-DCS | WA3509915 | Unit 5, B Wing Cleaning Cupboard- Electrical Wall socket has come away from the way | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 11:51:16 | 2020-08-05 08:30:00 | Pass | Investigate and repair unit 5 b wing cleaning cupboard gpo
MSA-DCS | WA3509939 | Gascoyne B1 and B2 have mould present and require urgent clean | Wandoo Rehabilitation Facility | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | DUNBAR SERVICES (WA) PTY LTD | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 12:00:18 | 2020-08-05 10:00:00 | Pass | Mould cleaned from walls
MSA-DCS | WA3509996 | Kitchen - Large Bell #1 slow to heat up | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 12:25:00 | Pass | Carry out pressure relief to bring unit into vacuum ok
MSA-DCS | WA3509997 | Kitchen - Large Bell #2 slow to heat up | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-27 11:50:00 | Fail | Replace pressure guage. Re-vacume kettle & test operation ok.
MSA-DCS | WA3510022 | Unit 1, Cell C5- GPO Broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-05 14:30:00 | Pass | Replaced gpo + antenna point
MSA-DCS | WA3510026 | Farm kitchen- Water cooler tripping RCD | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 13:00:00 | Pass | Investigate and repair farm kitchen water cooler
MSA-DCS | WA3510037 | Social Visits, Staff lunch Room- Zip Hydro Hot/Cold Tap Broken | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 12:32:00 | Pass | THIS IS A DUPLICATE WORK ORDER WORKS WERE COMPLETED ON WA3499691 SAME SYSTEM PLEASE CLOSE OUT NO CHARGE
MSA-DCS | WA3510045 | Unit 2, upper level 9.3.4 MDAS - no response | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 12:59:09 | 2020-08-06 10:00:00 | Fail | On arrival checked MDAS workstation noted that there were no alarms on screen at this time. Identified location of MDAS Rx ( S/W end of Unit 2). Arranged access to Rx vis Site Maintenance staff and inspected Receiver. Advised that this alarm activated during very heavy persistent rain, there is evidence of water in housing and on PCB but was dry at time of inspection. Cleaned Rx PCB with Contact Cleaner and checked seal around housing cover. Replaced cover and confirmed new alarms from this device had cleared.
MSA-DCS | WA3510060 | various areas intercoms saying network error | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 13:09:16 | 2020-08-04 15:34:00 | Pass | Network error due to power interruption from Urquart , restart all nodes and test cell call. Job completed.
MSA-DCS | WA3510079 | Admissions, Movements Co & laundry room - Air con not heating (multiple complaints) | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-05 10:00:00 | Pass | Work carried out as per signature slip reads:Arrived on site signed in and signed in tools. Located admissions laundry unit, Found unit tripped, Re-set power, checked pressures, washed filter. Ran unit up and monitored. All OK
MSA-DCS | WA3510097 | WWTP- 2 tanks 50mm gate valves broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-05 13:12:00 | Pass | Organised fittings and dropped them off to Karnet WWTP
MSA-DCS | WA3510112 | internal 8BMX not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-04 16:00:00 | Pass | Could not reset zone on EBI. No resistance 1MOhm measured. Found fault with Splice kit join. Repaired join. Cable tied and calibrated zone. Tested ok. Parts used:Consumables
MSA-DCS | WA3510123 | Unit 7, S wing - Wing light fitting needs replacing/repair faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 13:46:00 | 2020-08-05 10:00:00 | Pass | Repaired light
MSA-DCS | WA3510136 | Unit 6, Cell A18- Toilet flush button broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 12:20:00 | Pass | Replaced flush button in cell
MSA-DCS | WA3510140 | Unit 6, Cell D12- Toilet not flushing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 13:15:00 | Pass | Pulled apart cistern replacing outlet washer
MSA-DCS | WA3510145 | ground Rec Auto Entrance Door - Remote locking of door required-Reed Switch not working-see notes | Rockingham Justice Complex | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-26 16:00:00 | Fail | Installed LED indicator and relay to show the state of airkey.
MSA-DCS | WA3510146 | Unit 6, Cell A12- Metal bed base loose requires welding | Hakea Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-24 11:30:00 | Fail | RE WELDED METAL MESH BACK TO BED FRAMEWORK
MSA-DCS | WA3510161 | metal workshop 3 phase plug faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-04 16:30:00 | Pass | Repaired damaged outlet
MSA-DCS | WA3510189 | Unit 2, D wing - D1,D2,D3 and D4 toilets all blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 14:31:47 | 2020-08-05 12:55:00 | Pass | Drain machine used to clear blockage
MSA-DCS | WA3510195 | education, prisoners toilet - toilet not flushing and isolation tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 14:35:42 | 2020-08-05 13:50:00 | Pass | Removed cistern from wall raplacing outlet washer then reinstalled unit
MSA-DCS | WA3510200 | Security flood light outside signage w/s not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 15:00:00 | Pass | Investigate and repair signage workshop security flood light
MSA-DCS | WA3510206 | Unit 3, Cell D10- Desk light faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 08:30:00 | Pass | Investigate and replace unit 3 cell d10 desk light
MSA-DCS | WA3510209 | Amenities central training room- 2x lights are flickering | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 11:00:00 | Pass | Repaired damaged lights in amenities training rooms
MSA-DCS | WA3510210 | Security Area - Security Office assistance with camera footage | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-13 12:00:00 | Fail | Downloaded CCTV video from the Cell as requested. While doing so noted poor quality of image. Investigated in cell and saw window on outside of camera housing badly scratched. Ordered replacement window and, when access to cell available, installed on site.
MSA-DCS | WA3510213 | Unit 2, Cell 18 - lock barrel faulty, ( officers key will not unlock lock ) | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-11 10:40:00 | Pass | Attended site, removed lock from cell door, repinned lock to operate on all the required keys, refitted lock. Checked operation with guard.Date on site: 11/08/2020Time on site: 09:40am - 10:40am
MSA-DCS | WA3510306 | door between and crisis and medical centre - key isnt working | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 16:17:29 | 2020-08-05 11:45:00 | Pass | Replaced lock cylinder on door between CCunit and MedicalNew Cylindere built and keyed to GMK,OIC,OFR and Sisters Keys
MSA-DCS | WA3510344 | Duress alarrm is not activated any where in the Prison | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Aug 2020 | 2020-08-04 23:29:41 | 2020-08-04 22:00:00 | Pass | Rectified and fixed the mdas fault, job completed.
MSA-DFES | WA3509716 | Fault with external security self closing doors x2 - they are not self closing. | DFES Regional Office - Belmont | GMP-BR | Building | Doors (BU) | AWB Co. | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-04 14:00:00 | Pass | Attended site to inspect the two fire exit manual swing doors at the North building kitchenette entry and the amenitiesroom end exit.Found that the doors wouldn't always lock when staff exit through them due to two factors.1) doors have not been serviced in a while resulting in hinges and door handles were binding, adding additionalresistance during closing.2) door closer over time do need adjustments as they wear out.Remedy:Lubricants applied to hinges and door handle mechanism. This made doors open and close with less resistance.Adjusted the hydraulic closer action to make sure that the door is closed every time.In the future regular maintenance is recommended to prevent additional deterioration of hardware.Closers can be adjusted further if required
MSA-DFES | WA3509847 | Security alarm system fault | CFRS Daglish | GMP-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-05 12:00:00 | Pass | Found detector to be faulty. Pick up new part. Fit and test. All OK.
MSA-DFES | WA3509853 | Fire alarm system fault | CFRS Daglish | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-05 14:30:00 | Pass | Faulty detectors - fixed already by SEME
MSA-DFES | WA3510316 | Ground, reception area - Entry door to workshop is not closing properly. | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-24 14:30:00 | Fail | Attended site and assessed door - will need to organise parts and return to completeRescheduled for August 18th Replaced hinges and filled previous hinge cut outs. Will need to return to sand back repairs and paint Painting completed 24/8/20
MSA-DFES | WA3510317 | Ground level 1 - small animals roaming roof space area | CFRS Wangara | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 10:45:00 | Pass | High level of rat activity evident in roof void areas, baited throughout roof void areas, above suspended ceiling panels.
MSA-DTAG | WA3509647 | auto security building alarm - time change required, From 9pm to 10pm as the cleaning hours | Rockingham Justice Complex | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-04 13:45:00 | Pass | Programmed auto arm for 10PM on areas. Programmed new access group for Victim Support as per instruction. Tested and all is working.
MSA-DTAG | WA3509711 | L11 staff corridor Aluminium skirting has detached from corridor wall in several areas | Central Law Courts | GMP-BR-HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-28 09:00:00 | Fail | SKIRTING RE ATTACHED & PAINTED
MSA-DTAG | WA3509906 | Lvl 7, Quasi-Judicial- Temperature on level seven is quite cool | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-05 09:00:00 | Pass | Adjusted temp settings. Adjusted flow rates.
MSA-DTAG | WA3510155 | Sallyport 2x single fluro lights have blown | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-11 09:30:00 | Fail
MSA-DTAG | WA3510305 | Level 1, Outside Magistrate Chamber 2 - Fluorescent outside needs replacing/repairs | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 09:00:00 | Pass | Replaced tubes and starters
MSA-DTWD | WA3509500 | tower block L3 west flickering light | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-04 11:30:00 | Pass | Job complete
MSA-DTWD | WA3509553 | A Block, Room A250- Fluro & down lights missing & diffusers missing | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-17 13:15:00 | Fail | Attended site, signed in, completed jsa, changed 30 tubes and 30 starters , replaced 3 ES globes , replaced 8 diffusers , site happy , signed out
MSA-DTWD | WA3509602 | L3 & 4 staff and RM 406 room to cold | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-07 16:13:00 | Fail | Returned to site with new belts for AHU and left with equipment. Rechecked control settings and areas for appropriate temps. All ok. Work area left tidy.
MSA-DTWD | WA3509620 | A Block, Room A333- Room is very cold (VAV 7.21 AHU 7 ) | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-12 15:30:00 | Fail | Someone had changed the minimum air flow for the VAVs on the graphics package to 100 on all four, when 7.21 should have been 800, 7.19, 7.20 should of been 320 and 7.17 should have been 280. Once done, the temperature did rise a bit but will have to wait to see if that has solved the problem, otherwise we will have to balance them and re-do the k-factors in all of them
MSA-DTWD | WA3509640 | Room AT251 "Water leak " has been logged | Kwinana Automotive Centre | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 15:00:00 | Pass | 5.5 m tall wall 10m long. Will need scaff to access safely. Will return when raining to locate leak point.
MSA-DTWD | WA3509688 | Female Toilets- Broken hinges on door | Perth Campus B1 | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 12:45:00 | Pass | Complete
MSA-DTWD | WA3509692 | Exit door next to BMS office- Broken door closer | Perth Campus B2 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-04 12:45:00 | Pass | Re-secured door closer, adjusted and tested operation.
MSA-DTWD | WA3509736 | U Block, Workshop North side around duct - Roof Leak | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-09-29 14:00:00 | Fail | Attended site located leak, carried out temporary repairs - Will need to review during next rain period. Further works may be required.Works are now complete and site has confirmed repairs have resolved the issue
MSA-DTWD | WA3509752 | D Block- Exterior Key barrel to D106 is worn out | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 13:30:00 | Pass | service to ecternal lock and repair to internal door strike. D106 store area
MSA-DTWD | WA3509831 | L6 West- Air Con fault, Cold on Level 6 West - Toasty in the foyer though.... | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-18 15:57:00 | Fail | Checked BMS operation and found secondary hot water pump not operating. Initiated operation. Made adjustments to AHU 2 set point to allow for longer hot water valve operation. Each VAV has a hot water reheat coil fitted with control acutaor. It is unclear if water reheat valve are driving correctly as they can not currently be controlled directly at BMS. As BMS upgrades are scheduled contro for vav zones will be upgraded rectifying temp issues. Tafe facilities have previously been advised of this.
MSA-DTWD | WA3509965 | E block, E49 - fault lock on cabient | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-11 11:35:00 | Pass | Cabinet Lock - E Block - E49Cabinet lock repaired, faulty keys replaced.
MSA-DTWD | WA3509968 | E block staff female/male toilet blocked sewerage line | Bentley Campus | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-05 08:35:00 | Pass | Unblocked drains
MSA-DTWD | WA3509985 | Block 8, first floor, plant room - A/H 4 in plant room not heating. | Thornlie Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-31 16:30:00 | Fail | Works completed as per BRAF
MSA-DTWD | WA3510039 | E block, level 2, E204 - Air/Con is not working on heating. | Mount Lawley Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-05 13:10:00 | Pass | Attended site and signed in.Inspected ac in e204.Found unit switched to auto mode.Switched to heating mode and checked operation.Found heating works correctly.Switched to cool and confirmed correct gas charge.Switched back to heat and monitored.Found all operating ok.Suspect fault is due to system running on auto as the system will take longer to start due to changes in proportional settings on auto.Left in heating mode. Staff had left site so could not explain findings.
MSA-DTWD | WA3510082 | Canteen, GPO pendant is faulty | Rockingham Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 12:15:00 | Pass | Attended site and signed in. Locate canteen ad spoke with staff regarding the faulty gpo.Found gpo to be for deep fryer. Tested to find intermittently working. Supply and replace with new single 15amp gpo. Tested all okay. Job complete
MSA-DTWD | WA3510087 | Ladies toilet Canteen- Toilet is slow to drain after flushing | Rockingham Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 09:08:00 | Pass | Unblocked sewer for canteen
MSA-DTWD | WA3510117 | Classroom 2 - no power to 1 aircon and the other unable to maintain constant temperature | Armadale Campus - 145 Jull Street | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-05 13:00:00 | Pass | Adjusted temperature for apac supplying classroom 2
MSA-DTWD | WA3510126 | B Block, Ground Level - West End External door not closing properly | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-12 13:00:00 | Fail | Attended site and assessed door. Aluminium door and frame need to be re-aligned- Glasier arranged to attend
MSA-DTWD | WA3510153 | T Block, lvl 2 outside lift & around corner - lighting issues as per below | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 09:00:00 | Pass | Attended site and signed in. Located T block level 2 with staff on site. Found multiple fluros out. Replaced tubes as required. Fittings are tricky to worth with as they fall daisy chain and fall down when you take one down. Replaced tubes and ballast to lights. Tested all okay. Job complete
MSA-DTWD | WA3510178 | Multiple alarm faults - ( possible software glitch ) see long description | Rockingham Campus | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-25 15:00:00 | Fail | 06/08/2020, 1345-1515Attended site and uploaded Tecom System.Ran report of Tecom system.Ran report of Gallagher system.Took data away for analysis.Will need to return after solution found25/08/2020, 1300-1500Check / alter Gallagher system programming as required to match EdSec account numbers
MSA-DTWD | WA3510230 | A block L3 A310 has no gas to Portable Burners | East Perth Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 15:05:00 | Pass | COMPLETED
MSA-DTWD | WA3510284 | L2 B254 Faulty Air Con split unit | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 04 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 12:53:00 | Pass | Returned to wij materials for deep clean on A/C once confirmation of room booking. Collected keys gained access and isolated and locked out equipment. Set area up an completed deep foaming clean of under celling cassette unit. Self cleaning agent left in unit. Mold deposits removed from condition tray. System reassemble and test run through full cooling. Self cleaning agent will help to maintain and prevent further mold build up. Work area left tidy.
MSA-DTWD | WA3510312 | Library - broken detector boxes. | Perth Campus B2 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 04 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 09:00:00 | Pass | Complete
MSA-MRWA | WA3510290 | Refurbish fluro light fitting | Don Aitken Centre MRWA Head Office-Main Building-Eighth Floor-821-Office | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-06 07:45:00 | Fail | updateAttended 05.08, found faulty light,advised to return on 06.08 in the morning to repair,replaced fluros and starters, all now working
MSA-MRWA | WA3510297 | Level 5, Blocked toilet please remediate | Don Aitken Centre MRWA Head Office-Main Building-Fifth Floor-A5.01-Toilet-Male | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Aug 2020 | 2020-08-05 17:00:00 | 2020-08-05 07:43:00 | Pass | Investigate blocked toilet in level 5 all toilet working fine.
MSA-DCA | WA3510822 | Water streaming through external downpipe | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Maritime History | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 15:30:00 | Pass | Attend to investigate leaking 225mm storm water pipe. Was notified by frank that this morning he had noticed the external storm water pipe was leaking a large volume of water, suspect aircon related issue as there was no rain last night or day before, have notified staff that if it happens again to get an air conditioning technician on site.
MSA-DCS | WA3510430 | ISU, Cell A04- 2x smashed cell windows | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 05 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 14:00:00 | Pass | CELL WINDOWS REPLACED
MSA-DCS | WA3510507 | External exit door from MPU wing to rear of MPU exercise yards lock faulty | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 07:37:46 | 2020-08-07 12:30:00 | Fail | Unable to complete due to access being denied.Remove lock, service and reinstall.
MSA-DCS | WA3510512 | Unit 2, Cell C3- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 08:30:00 | Pass | Plunged basin to clear blockage
MSA-DCS | WA3510608 | control cell call system fault | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Aug 2020 | 2020-08-05 12:09:42 | 2020-08-12 17:02:00 | Fail | Repaired Cell Call System fault. Investigated and repaired cell call ACM fault. Rested OKJob Complete
MSA-DCS | WA3510650 | units 1 & 2 Control Pod Staff kitchen Area Passage Duress Alarms not working | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 08:23:06 | 2020-08-24 16:30:00 | Fail | Replaced damaged duress button, job completed.
MSA-DCS | WA3510658 | Unit 2 A1 Door Dropped jamming in Frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 08:26:28 | 2020-08-05 14:30:00 | Pass | Adjusted/repaired hinges as required to restore normal function
MSA-DCS | WA3510682 | Unit 2, Cell A12- Shower Glass Aluminium Frame Broken | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 08:19:34 | 2020-08-07 07:30:00 | Fail | Attended site and assessed damaged to shower screen.Supply and install new shower screen using 10mm safety glass.
MSA-DCS | WA3510716 | Assessments - Air-con not working | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-26 11:00:00 | Fail | Repairs rejected. Submitting claim for costs to date.
MSA-DCS | WA3510723 | Abattoir condensers in fridge 2 and freezer 4 icing up | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-06 13:00:00 | Pass | essential Ref. attended , found chiller 2 compressor faulty. quote to replace declined fridge 4 de iced coil test heaters all operational.
MSA-DCS | WA3510724 | Unit 2, SO office the air vent failed top open therefore its on but not working | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-05 12:30:00 | Pass | Units were in the wrong mode as set by the user. Staff have been informed on how the unit operates.
MSA-DCS | WA3510730 | Abattoir - water leak in prison dayroom | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-06 08:30:00 | Pass | Repaired pipe in abattoir wash room
MSA-DCS | WA3510751 | Unit 1, D Wing- waterpipe has a hole , leaking on the floor | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-21 11:30:00 | Fail | 7/8/20 - Asked all staff in unit and inspected entire wing. No leaks located. Will return on Monday for further investigation when reporting officer is in unit.11/8/20 - Reattended job . Located leak which had been wrapped in tape to seal. Water also leaking though shower tap holes. Created materials list to repair.21/8/20 - collected parts offsite. Repaired leaking pipes in duct and sealed leaking penetrations.
MSA-DCS | WA3510841 | Turner, B wing ( living area ) - smashed window approx 1450x500 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-13 10:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3510851 | Laundry drain for washing machines is blocked up at the back of the laundry | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 10:38:53 | 2020-08-06 11:30:00 | Fail | 5/8/20 - attended job. Lifted pit lid and inspected blockage. Partial unblocked to get system working to allow for full clean following day.6/8/20 - collected materials offsite. Lifted lids. Removed 2 x lint catch boxes. Removed all rubbish on both lint boxes and inside pit. Washed till clean. Reinstalled boxes and shut lid.
MSA-DCS | WA3510866 | West Side Chaplain, Office- Lock broken on door | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-05 13:15:00 | Pass | Repaired lock. Supplied and fitted required replacement parts
MSA-DCS | WA3510868 | Unit 14 - A2 when toilet is flushed it leaks underneath between sink and door | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-07 08:30:00 | Pass | Replaced leaking spindle in basin which was leaking over edge of basin onto floor.
MSA-DCS | WA3510939 | Unit 1, D Wing- Bathroom grout on the bottom of tiles around tap area need regrouting | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo Building Services | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-13 13:00:00 | Fail | TILES RE GROUTED
MSA-DCS | WA3511053 | Unit 2, D-6 - Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-06 11:00:00 | Pass | Attended site and carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3511070 | Unit 2, Cell B7- Sink taps leaking | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-13 10:10:00 | Fail | Once gained access replaced air rader and removed dirt from line
MSA-DCS | WA3511071 | Unit 2, D-4 - Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-06 11:00:00 | Pass | Attended site and carried out repairs to the damaged bed panels on bunk beds
MSA-DCS | WA3511075 | Unit 2, B-1 - Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-11 14:30:00 | Fail | Attended site and carried out repairs to the damaged bed panels.
MSA-DCS | WA3511077 | Unit 2, Cell B2- No Water Pressure to Sink | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-13 12:00:00 | Fail | Once gained access flexi and filter were blocked, replaced air rader and cleaned out sand from flexi and spout
MSA-DCS | WA3511083 | Unit 2, B-2 - Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-11 11:30:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3511085 | Unit 2, Cell B6- Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-14 13:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3511087 | Unit 2, B-3 - Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-14 10:00:00 | Fail | Carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3511088 | Unit 2, Cell B4- Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-14 10:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3511109 | Unit 5, B & D - Oven extractor fans are not working due to the filters being filthy and damaged | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | DUNBAR SERVICES (WA) PTY LTD | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 13:00:00 | Pass | Staff instructed on how to start oven extractor fans
MSA-DCS | WA3511236 | Ed volt 2, classroom 5 - door lock is not working, unable to secure room | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 14:21:41 | 2020-08-05 16:00:00 | Pass | Replaced failed lockset.
MSA-DCS | WA3511246 | video links loss of electrical power | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 05 Aug 2020 | 2020-08-05 18:29:59 | 2020-08-05 16:30:00 | Pass | Reset power and recommended new circuit
MSA-DCS | WA3511258 | Unit 13 - A5 shower screen in Cell A5 is leaking onto the lower bunk. Requires resealing. | Casuarina Prison | GMP-BR- HO | Building | Internal Screens (BU) | Midolo Building Services | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-17 12:00:00 | Fail | RE SEALED LEAKING SHOWER SCREEN
MSA-DCS | WA3511330 | Unit 1 D3 door Jamming in Frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-05 16:35:00 | Pass | Repaired/adjusted hinges as required to restore normal function.
MSA-DCS | WA3511340 | unit 16 no hot water HW system will not reset | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 05 Aug 2020 | 2020-08-05 19:48:10 | 2020-08-05 19:30:00 | Pass | Investigated fault. Fire control panel has isolated power to gas reset button and needed to be reset before gas could be reset. Hot water working and heating when left unit.
MSA-DCS | WA3511348 | Unit 15, Fire panel showing faults - tried to reset alarm. false alarms | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 05 Aug 2020 | 2020-08-05 20:31:13 | 2020-08-05 20:30:00 | Pass | Unit 15 & 16 fire system compromised
MSA-DFES | WA3511095 | Main admin, CL&D offices - Aircon has lost its setting and is too cold again | DFES Regional Office - Belmont | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-06 11:00:00 | Pass | Completed works as per service report, reset boiler, all appears to be functioning satisfactory.
MSA-DFES | WA3511123 | ground Front Reception/Security Foyer-4x Automatic Window blinds (3 units per window-see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Windows (BU) | NEYLOR | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-09-11 14:03:00 | Fail | COMPLETED
MSA-DFES | WA3511272 | Hanger door sliding parts of the panel of door has detatched | DFES Rescue Helicopter Base | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 16:30:00 | Pass | Technician attended the site of 9 Bell Court, Jandakot, WA to the Hanger Sliding door W22151 on 05/08/2020. Following a full test and inspection of door components found fault to be large sliding door has come out of top track and hanging precariously at end of overhead rail. Unable to access door with scissor lift as sliding door is over grassed area, required to return to site with extra personnel and AWD knuckle boom EWP to attempt repair. Technician has temporarily secured door panel via tiedown strap and ground stake.06/08/2020 Technician reattendedReattended site with knuckle boom EWP and extra personnel, reinstated large sliding door backonto ground and overhead track, adjusted clearances, refixed cladding and test operation multipletimes, all ok. Full test and inspection of door function completed prior to leaving site.
MSA-DTAG | WA3510641 | Basement custody cells walls are showing signs of water penetration | Joondalup Courthouse | GMP-BR-HO | Building | Internal Walls (BU) | GREENCAP PTY LTD | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-31 16:05:00 | Fail | Works completed and Report Issued
MSA-DTAG | WA3510781 | Registry - alarm system on site fault - SYSTEM REPORTING BATTERY TEST FAIL DGP 4 | Mandurah Courthouse | GMP-BR-HO | Security | Security Management System (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-06 15:15:00 | Pass | 6/8/20 - Dean Simpson, Joshua ParkReplaced faulty battery and tested all ok.No call out fee as already onsite.
MSA-DTAG | WA3510783 | L4 Room 4.2 (Police Prosecutions) Door handle stiff and catching on the inside of the door | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-07 07:45:00 | Pass | CLEAN AND LUBRICATE LOCK AND HANDLE
MSA-DTAG | WA3510892 | the electronic door release on the fire exit next to the security office door is not working | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 12:00:00 | Pass | 5/8/20 - Dean Simpson, Joshua ParkDoor release not working.MCB tripped, reset MCB and tested. Door release working ok.
MSA-DTAG | WA3511252 | L4 Court 41 Jury seat armrests are loose | Central Law Courts | GMP-BR-HO | Furniture | Office Furniture (FU) | Midolo Building Services | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-07 08:45:00 | Pass | RE-SECURE ARM RESTS
MSA-DTAG | WA3511322 | Level 2 - Air Con Plant Room Unable to access the BMS system remotely to change the A/C temp-notes | Midland Courthouse | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Icon Logic Pty Ltd | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-10 11:30:00 | Pass | Repairs to BMS
MSA-DTWD | WA3510406 | 25Ab L2 east - auto doors not working | Perth Campus B1 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 05 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 13:11:00 | Pass | Carried out reset to door, checked over, cleaned sensors etc and tested operation. All ok
MSA-DTWD | WA3510484 | L2 rear auto doors (walkway) - Broken switch | Perth Campus B5 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 05 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 12:49:00 | Pass | Replaced damaged key switch with replacement, tested and left in good working order.
MSA-DTWD | WA3510518 | N Block - N321 - Broken blinds | Perth Campus B1 | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 05 Aug 2020 | 2020-08-11 17:00:00 | 2020-09-22 10:49:00 | Fail | COMPLETED
MSA-DTWD | WA3510685 | Fire door L1 near lifts 1&2 jammed | Perth Campus B1 | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-06 15:00:00 | Pass | Complete
MSA-DTWD | WA3510747 | D Block, Room D219- Broken toilet full flush | Perth Campus B4 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 10:00:00 | Pass | Fix broken toilet replace parts
MSA-DTWD | WA3510763 | L1 IT office worn out carpet tiles | Perth Campus B2 | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-18 12:20:00 | Fail | Purchase order issued to carpet layer Works completed as per quote
MSA-DTWD | WA3510778 | D Block, Boiler Plant Room, Circulating Pump wont activate for supply to floor pads | East Perth Campus | GMP-BR | Mechanical Services | Pumps (MS) | Precise Air Group | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-09-17 14:00:00 | Fail | Attended site and inspected d block heating water system with cpi.Found a few issues with the make up water system andrelief valves. DAS submitted for repairs.
MSA-DTWD | WA3510780 | A Block, AHU 1 & 3- heating coils as they are blocked | East Perth Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-06 09:30:00 | Pass | Attended site and signed in.Inspected ahu 1 and 3 on a block and checked heating water.Found both ahu have heating water flow.Checked water temps and found supply temp is 68 degrees and return water temp is 51 degrees.Heating water systems are working correctly.Checked bms and found heating water system appears to be operating correctly.The supply air temps for the ahus are low but i suspect this is due to the amount of outside air coming into the system as the minimum outside air is about 25% of total air volume and the ambient air is only 15 degrees.Could not find any faults with the heating water system.
MSA-DTWD | WA3510883 | Block 1, G Floor- Lights out in foyer | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-21 15:15:00 | Fail | Arrived on site, signed in, located light,completed jsa,set up work area,isolated lighting,removed old lights, replaced with new led , cleaned up work area, re energised, tested , all lights working good ***job complete***
MSA-DTWD | WA3510886 | Graffiti - Main sign on simpson ave and multiple other locations | Rockingham Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-10 12:40:00 | Pass | Removal of graffiti from various locations
MSA-DTWD | WA3510941 | Q block, ground, Q010 - Faulty power point | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-05 14:15:00 | Pass | Attended site and signed in. Located Q block and spoke with lecturer. Found double gpo not able to plug in 2 power packs. Relocated double gpo on wall and installed single gpo next to double. Tested all okay. Job complete
MSA-DTWD | WA3510978 | Block 6 ground floor TIG welding room in Vehicle Body Building some lights not working | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-24 14:45:00 | Fail | Arrived on site , signed in , completed jsa, located lights , isolated lights , removed old lights, replaced with new lights , re energised lights , tested lights , working all fine ***job completed ***
MSA-DTWD | WA3510994 | Plant room - Chiller 1 keeps randomly faulting - please invesigate | Perth Campus B2 | GMP-BR | Air Conditioning | Materials (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2021-02-02 08:49:00 | Fail | Returned to site gained access to plant and completed BRAF repairs. Completed refit of remaining chiller pannels, checked and confirmed equipment operation and settings. Completed clean up of plant area and removal of waste matairls from plant. Work area left tidy.
MSA-DTWD | WA3510995 | A block AM135 noisey extraction fan | Munster Campus (ACEPT) | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 14:00:00 | Pass | Replaced contactors for TEF 1 and 2 in a block
MSA-DTWD | WA3511026 | K block, Canteen kitchen - Bain Maire faulty drain tap, need repair and check deep fryer safe to use | Midland Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 05 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-07 15:00:00 | Pass | COMPLETED REFER TO SERVICE REPORT FOR IMPORTANT INFORMATION ON EQUIPMENT STATUS.
MSA-DTWD | WA3511145 | Plant Room - Broken 42886 lock on boiler room door | Perth Campus B6 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-06 12:00:00 | Pass | replace 42886 570 cylinder on Plant room door
MSA-DTWD | WA3511165 | B block, reception - circuit breaker keeps tripping to aircons | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 13:30:00 | Pass | HWU was found to be the cause of tripping RCD, removed HWU from the isolator and applied out of service tag, HWU has been decommissioned.
MSA-DTWD | WA3511171 | A block, level 2, rooms A236 & 237 - has no lights | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 05 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-05 15:30:00 | Pass | Rectified blown fuse in lighting circuit in room 237 level 2 block A
MSA-DTWD | WA3511207 | Rooms A212 A213 fans running constantly | Perth Campus B5 | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 10:30:00 | Pass | Complete
MSA-DTWD | WA3511229 | L1 E200 lock is jamming | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-06 10:40:00 | Pass | Adjustment to strike E200
MSA-DTWD | WA3511235 | L3 B314 No power supply to display rooms attached to B314 | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-20 08:28:00 | Fail | Repalced faulty lamps and rcd .tested all working properly.job completed
MSA-DTWD | WA3511262 | crech no warm air | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-07 16:06:00 | Pass | Returned to site gained access and rechecked settings on equipment. All ok. No further action is required.
MSA-DTWD | WA3511298 | L3 ladies toilet keeps running | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 05 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 11:00:00 | Pass | Fixed leaking taps toielt
MSA-DCA | WA3512287 | FOHM Office/Box Office- Fire Panel - Fire Panel zone #57 is not going into alarm when tested | State Theatre Centre (Heath Ledger Theatre)-Main Building-Level 1-Box Office | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-07 09:30:00 | Pass | On arrival investigate zone not alarming on FIP (Z57)Upon investigation found no issue with zone alarming, was able to alarm via FIP- zone is system 3 (valve tamper) suspect possible operator error as cause of issue- spoke with manager who activated during fire testing and no bells and alarms activated - explained that monitor valves activate system 3 alarms that do not activate ewis or call out brigade
MSA-DCS | WA3511444 | Kitchen- Power keeps tripping out to brat pan | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 07:07:14 | 2020-08-06 11:00:00 | Pass | Investigate and repair kitchen brat pan tripping circuit
MSA-DCS | WA3511445 | Kitchen- Filters to rational oven not filling | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 07:10:12 | 2020-08-06 14:45:00 | Pass | 06/08/2020Check flow of water Trace to blocked filter Filters replaced on seperate job Flush and test ok
MSA-DCS | WA3511461 | Unit 1, Cell D9- Toilet broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-11 13:00:00 | Fail | Removed stainless panel on toilet rennet into shape and pot riverted panel back on
MSA-DCS | WA3511464 | Unit 4, vesda fault on fire panel | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 07:40:31 | 2020-08-06 14:11:00 | Pass | Attended site and carried out the following works in unit 4.1: found flow in pipe 4 to be high corrected when normalised.2: found pipe 1 D wing low flow due to many sample points being blocked cleared sample points and raised flow and normalised and left normal.Note many of the capillary tubes are getting old and brittle through all four wings and should be replaced.
MSA-DCS | WA3511468 | Kitchen,Turbofan oven- switch intermittent in operation | Boronia Pre-release-AM06 - Prisoner Accommodation House 1 and 2-Ground Floor-House 1 - Kitchen Area | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 06 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-12 14:45:00 | Fail | Replace Encoder Kit test ok.
MSA-DCS | WA3511555 | Unit 2, A & C side- wire fence has been badly damaged/bent | Casuarina Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-09-30 08:00:00 | Fail | 17/08/20Inspected and measured works to repair/replace fence at Unit 2. Waiting for quotes on like for like fence panels so BRAF can be submitted.
MSA-DCS | WA3511557 | Unit 14, Fridge in B/D keeps triping out, when reset will trip straight out | Casuarina Prison | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 11:00:00 | Pass | Compressor faulty. Not economical to repair. Maintenance to arrange replacement from stores
MSA-DCS | WA3511558 | Unit 14 - A11 shower constantly dripping and blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 08:00:00 | Pass | nil
MSA-DCS | WA3511614 | Unit 4 C wing grille failure- manual operation only | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 08:26:32 | 2020-08-06 10:15:00 | Pass | 06/08/20Inspect faulty grille motor.Expect over heating.
MSA-DCS | WA3511625 | Dairy - Leaking water pipe on wall near pasturiser | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-06 13:00:00 | Pass | Repaired burst pipe on back wall of Pasturiser
MSA-DCS | WA3511670 | SITE COST CCU/medical lock on the door not working | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 06 Aug 2020 | 2020-08-06 12:45:31 | 2020-08-06 11:30:00 | Pass | Reported by officers as keys getting stuck in lock Officers keys are bent , will jamm in new Lock cylinder that was replaced tried multiple keys whilst on site all functioning recoment bent keys be replaced and keys not be used as door handles
MSA-DCS | WA3511675 | Cyrenian House Demountable - Leaking pump under sink water everywhere | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 06 Aug 2020 | 2020-08-06 12:48:33 | 2020-08-06 10:00:00 | Pass | Repaired leak to Saniflow
MSA-DCS | WA3511699 | unit 4 main office door to prison yard not unlocking with swip | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 08:56:19 | 2020-08-11 13:43:00 | Fail | replaced electronic lock with new (seme stock)/ tested working ok. job complete
MSA-DCS | WA3511747 | Cell call system is in network error for whole centre | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Aug 2020 | 2020-08-06 13:32:33 | 2020-08-06 11:23:00 | Pass | Arrived onsite Node 3 and controller 15 had gone offline at the same time. Electricians advised they have shut power off to Karakan.System is back online after electricians had finished
MSA-DCS | WA3511816 | main kitchen blocked drain | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 09:39:26 | 2020-08-06 14:45:00 | Pass | Complete
MSA-DCS | WA3511821 | Unit 14, Cell A11- Bottom shelves in cell are missing | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-09-17 10:30:00 | Fail | INSTALLED NEW SHELF TO STORAGE UNITALSO RE-SEALLED SHOWER SCREEN WHILE THEY WERE THERE
MSA-DCS | WA3511848 | Unit 14 tea room tap is loose | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 10:00:00 | Pass | nil
MSA-DCS | WA3511889 | Unit 7, Cell H6- Light switch not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 14:00:00 | Pass | Replaced light switch
MSA-DCS | WA3511890 | Unit 7, Cell E8- Light not working and screws to diffuser broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-07 10:30:00 | Pass | Repaired light
MSA-DCS | WA3511891 | Unit 9, C&D Dayroom- Flickering light on High Level light fitting | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-26 14:30:00 | Fail | Repaired lights
MSA-DCS | WA3511901 | Unit 10, Cell D5- Huge piece of ceramic missing from the rim of the toilet pan | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 10:53:25 | 2020-08-07 08:30:00 | Pass | Replaced smashed toilet in cell
MSA-DCS | WA3511903 | Unit 9, A wing, cleaning cupboard - leaking tap | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-11 14:18:00 | Pass | Isolated water and replaced both hot and cold taps for cleaning cuboard
MSA-DCS | WA3511907 | Unit 9, C 13 - main lock on cell door difficult to operate resulting in possible injury to staff | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 10:56:13 | 2020-08-06 16:00:00 | Pass | Supplied and fitted new hinges and realigned door.
MSA-DCS | WA3511966 | Unit 4 - B13 Window frame in cell B13 is partly broken. Window drops. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 11:15:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3511972 | Kitchen, Middle size bell - Not heating up. Does have power to bell. | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 11:32:49 | 2020-08-06 12:55:00 | Pass | Top up with distilled water. Test unit up to temp ok. Carry out pressure relief to bring unit back into vacuum ok.
MSA-DCS | WA3511977 | Unit 14 - C Wing Cell C07 shower drain is repeatedly blocking when is use and flooding cell, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 09:00:00 | Pass | nil
MSA-DCS | WA3512034 | SOG Base - Mens toilets are blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 12:12:56 | 2020-08-06 14:05:00 | Pass | Flushed every single toilet and basin in the men bathroom- drains not blocked. Replaced faulty inlet valve in the 2nd toilet from the right(cistern not flushing properly)
MSA-DCS | WA3512051 | control - PDA unit 1 fault (no response) | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Aug 2020 | 2020-08-06 16:21:49 | 2020-08-07 14:00:00 | Fail | Replaced water damage and coroded pcb bosch mdas receiver, job completed.
MSA-DCS | WA3512141 | ISU smashed observation window | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-06 15:00:00 | Pass | OBS WINDOW REGLAZED
MSA-DCS | WA3512199 | Bakery - Workshop Sensor taps to the basin next to the dough mixers are not activating. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 13:50:43 | 2020-08-12 16:00:00 | Fail | Taps were repaired using left over solenoids from job no wa347 3555. Both taps tested and working correctly.
MSA-DCS | WA3512215 | gate house boom gate main entry to prison not working,, | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-18 12:00:00 | Fail | Tested and confirmed operation of boom gate. Confirmed operation of safety ground loop under boom gate.
MSA-DCS | WA3512227 | I R boom gate faulty stopping half way up | Karnet Prison Farm | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-13 12:30:00 | Fail | 13/08/20Inspect boom gate.No fault found.Apply lubricant.
MSA-DCS | WA3512230 | Unit 2 top landing ablutions - main extraction system faulty not working properly | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-09-22 15:00:00 | Fail | Investigate unit 2 top landing extraction system. Requires replacement.Source parts.Remove existing extraction fan.Install adaptor and new extraction fan.
MSA-DCS | WA3512234 | Bakery - Fluro light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 12:00:00 | Pass | Repaired faulty lights in bakery
MSA-DCS | WA3512255 | Garments- roof above garments is leaking | Casuarina Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2021-03-15 09:00:00 | Fail | SOURCE OF LIKELY ENTRY POINT LOCATED & RECTIFIED
MSA-DCS | WA3512266 | laundry roller press gas not turning on | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | VEECO PTY LTD | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 14:53:53 | 2020-08-27 13:53:00 | Fail | Checked ironer lots of build up of lint. Requires moving machine to clean burner tubes and tune flame. Returned to site once BRA approved and completed job
MSA-DCS | WA3512268 | POD - MSA system - constant Alarm | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Aug 2020 | 2020-08-06 18:53:29 | 2020-08-06 16:15:00 | Pass | Alarm is a SYNCRONISATION LOSS on the EBI. System recently upgraded by HONEYWELL and still under warranty. Control room officers aware that they may have to contact Honeywell directly.
MSA-DCS | WA3512281 | Unit 3, turnsile intercom is not working 1 side | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-07 12:30:00 | Pass | On arrival found master Station in Control Room Off. Tested intercom units on entrance and exit side of Turnstile, both units provided audible alarm when Button pushed and had good audio to control. Unable to reproduce Fault.
MSA-DCS | WA3512320 | message on m-dash system: no response outside social club | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-07 11:00:00 | Pass | Travelled to site and tested duress reciever fault. Located device and tested and found receiver not working due to wear and tear.Replaced with new receiver kit, installed and tested ok. Job complete. Seme stock used
MSA-DCS | WA3512324 | SITE COST cool room - faulty refrigeration unit | Karnet Prison Farm | WSM-BR-SITE | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 0 | CLOSE | 06 Aug 2020 | 2020-08-06 21:40:31 | 2020-08-19 12:00:00 | Fail | essential ref. attend , found coil iced up.de ice coil and do further tests and install high temperature alarm as per quote.
MSA-DFES | WA3511703 | FF bathroom- light/fan switch has produced an electric shock | CFRS Canning Vale | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 14:15:00 | Pass | Signed in at 13:17 to inspect FF bathroom light switch. Replaced with weatherproof IP66 rated double light switch so no water can interrupt circuits. Signed out at 2:08
MSA-DFES | WA3511835 | Engine room - roller door not working has been tag out. | VFRS - Armadale | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 12:15:00 | Pass | Technician attended the site of Armadale Volunteers Fire Station to the Vol Rear Door No. W22532 on 07/08/2020. Following a full test and inspection of door components found fault to be door tagged out and nonoperational. Technician checked springs, axle and all mechanical components before energizing controller, door was showing multiple faults on controller. He addressed all the faults and reset door and limits, door is now working as should. However, he's not convinced that issue will not reoccur due to most faults showing a controller issue. The door is working ok now but if issue persists tech would recommend replacing controller. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3511864 | Engine room - rear roller door - mechanical fault, lift mechanism | CFRS Canning Vale | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | COMPFIN | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 16:00:00 | Pass | Completed Repair under warranty
MSA-DFES | WA3511939 | Groundl, staff entry/exit door-rubber on bottom of door is stopping door closing correctly-see notes | DFES Education and Heritage Centre | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-18 14:00:00 | Fail | Door closer was hitting wall causing hinge screws to come out. Back check on closer adjusted to stop it hitting wall and screws refixed in top hinge. Door now closes properly and doesn’t rub along the bottom which was the initial breakdown report.
MSA-DFES | WA3512115 | Various lights out throughout the building, powerboard states lights on | CFRS Midland | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 17:30:00 | Pass | Investigated fault with lights not working throughout building. Identified that The S.S.L lighting chassis had no power. I traced the voltage down three line and found a Contactor that has failed and will need replacement. Have ordered parts and will return to replace.
MSA-DFES | WA3512237 | engine room frnt and rear doors will not open | CFRS Midland | GMP-BR | Building | Fire Door (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 17:30:00 | Pass | Technician attended the site of 158 Morrison Rd, Midland, WA to the Engine room roller door on the 06/08/2020. Following a full test and inspection of door components found engine door rooms were not working.Spoke to an electrician who was working on site and he said he had shorted out a cable when working on the flashing lights for the doors.Reset the controller and everything seems to be working as should.Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3512259 | ground stores area Fire Suppression Unit leaking-photo's to follow in email | Fleet Management Services - O'Connor Workshop | GMP-BR | Plumbing & Drainage | Water (PD) | Critical Fire Protection & Training | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-07 09:45:00 | Pass | Leak from sprinkler valve - flush and seal valve
MSA-DTAG | WA3511826 | Level 3, court 37 - light out over the witness box | Central Law Courts | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 14:00:00 | Pass | Job complete
MSA-DTAG | WA3511881 | ground echo chamber Broken network port | Perth Children's Court | WSM-BR-SITE | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 08:00:00 | Pass | Job complete
MSA-DTAG | WA3512316 | Level 1,Magistrate Chamber 1 - Fluorescent in Magistrate 1 Chambers need replacing | Midland Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 09:30:00 | Pass | Replaced tubes and starters and led light
MSA-DTAG | WA3512511 | RETROSPECTIVE WO (already attended 06/08/20) - lift reader (east) not scanning | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 1 | CLOSE | 06 Aug 2020 | 2020-08-06 17:00:00 | 2020-08-06 09:00:00 | Pass | Attended site for reported Lift Lobby on Level 31 Reader offline. Access programming and all readers are online.Reported reader fault on Lift Reader. Lift Reader maintained by Schindler.Job completed
MSA-DTWD | WA3511480 | B103- Floor vent is blocked | East Perth Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 06 Aug 2020 | 2020-08-06 11:55:50 | 2020-08-06 16:20:00 | Fail | blockage cleared
MSA-DTWD | WA3511720 | E-Café / toilets behind Electro Metals blocked drain draining slowly | Clarkson Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-11 11:30:00 | Pass | COMPLETED
MSA-DTWD | WA3511750 | Lvl 5, Female staff room - Flush toilet button missing | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 15:18:00 | Pass | New dual flush cistern and button
MSA-DTWD | WA3511760 | H block ground H05 Power out in half the classroom | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 14:00:00 | Pass | Attended site and signed in. Located H block. Got access keys from office. Located classroom and found gpos with no power. Circuit W2 tripped. Reset and tested gpos. Found kettle in classroom to be faulty and when plugged into any gpo power shuts off. Tested kettle faulty. Removed from service. Power now all okay. Job complete
MSA-DTWD | WA3511791 | T Block Lift right side not working “No entry sign lit up on panel” | Murdoch Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2021-08-06 13:16:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTWD | WA3511823 | ground Loose tap in Male toilets behind Bricklaying and Carpentry | Clarkson Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-11 12:29:00 | Pass | COMPLETED
MSA-DTWD | WA3511829 | Hoist No 8 broken release lever - further info below | Kwinana Automotive Centre | GMP-BR | Lifts | Vehicle hoists (LI) | Precision Automotive Equipment/Bapcor | 0 | CLOSE | 06 Aug 2020 | 2020-08-06 13:51:14 | 2020-08-06 12:00:00 | Pass | Repairs to lift
MSA-DTWD | WA3511904 | T, U and V blocks BMS issue settings (heat and cooling) are not switching over on automatic-see note | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Icon Logic Pty Ltd | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-06 15:00:00 | Pass | rectified fault and tested operation, all functioning correctly.
MSA-DTWD | WA3511930 | G floor, G12 - Door key locks are jamming /stuck | Fremantle Campus (formerly WA Maritime) | GMP-BR | Security | Locksmith (SE) | GRONBEK SECURITY | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-09-02 14:15:00 | Fail | Replaced faulty lock cylinder at he G Floor, G12 key at he South metro TAFE.
MSA-DTWD | WA3512010 | L3 T block hot water boiler checked as the pressure is to low for the system | Murdoch Campus | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-07 14:45:00 | Pass | Attended site, checked accumulator for leaks - none. Checked accumulative pressure -150KPA.With portable compressor recharged accumulator tank to 300KPA
MSA-DTWD | WA3512057 | A&B Block, Unit not working - Fan Fault for AAC2 and AAC1 & DAHU2 DAHU3 not showing readings on BMS | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-10-15 08:30:00 | Fail | Works and report completed by Icon Logic.BRAF WORKS COMPLETED 15.10.20, TESTED ALL OK
MSA-DTWD | WA3512133 | K Block, K02 - Deep clean excesive grease & grime from deep fryer, oven & bain marie kitchen equip | Midland Campus | GMP-BR | Cleaning | Cleaning (CL) | DUNBAR SERVICES (WA) PTY LTD | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-08 11:20:00 | Pass | No-one there to sign paperwork - security would not sign. (Saturday works)
MSA-DTWD | WA3512148 | E Block, E63 - Bad smell coming from Bistro Bar’s waste pipe | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-07 15:45:00 | Pass | Fixed dishwahser multiple issues
MSA-DTWD | WA3512152 | E Block, Staff Toilets – Sewage line blockage | Bentley Campus | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-09-15 08:20:00 | Fail | Sewer divert
MSA-DTWD | WA3512196 | G block - Power continually tripping in G Block fabrication workshop | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-26 16:45:00 | Fail | Attended site and signed in. Located welders and organised how we would replace plugs as half of welders were in use. Replaced all plugs and tested all plugs. All plugs ok. Informed staff of completion. Competed paperwork and signed out. Job complete
MSA-DTWD | WA3512260 | P Block, ground, P001 (entry) - Damaged platersboard wall | Balga Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 15:30:00 | Pass | Complete
MSA-DTWD | WA3512279 | A block A26 male toilet door closer faulty | Bentley Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 06 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 14:00:00 | Pass | Replaced worn door closer with new. No further adjustment available in old closer
MSA-DTWD | WA3512280 | D block stairs leading D207 staff room lights not working | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-17 10:30:00 | Fail | Attended site and signed in. Located d block stairwell. Met with scaffold. Replaced 3 x lights using scaff in middle. Light at bottom on stairs has no power can not source power as no access from ceiling. Need techworks to return and rectify. Other 2 on stairs working. Job complete
MSA-DTWD | WA3512283 | level 7, Staff kitchen - Tap Leaking | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 06 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-27 12:00:00 | Fail | Replaced chiller unit and tap
MSA-DTWD | WA3512329 | Bentley Campus, E Block, Kitchen E58 - Taps not turning off. | Bentley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 06 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 08:00:00 | Pass | Replaced broken taps
MSA-DCA | WA3512358 | Polly Cafe- High external light is faulty | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 1 | CLOSE | 07 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 13:30:00 | Pass | re directed 3 x light fittings up along the walk way between AGWA Admin building and new multiplex museum site. Replaced 1 x failed SAL led flood with brand new Clipsal 50w LED flood, provided new connections. all tested ok.
MSA-DCA | WA3512445 | fire panel fault zone fire L1 plantroom | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 07 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-07 11:31:00 | Pass | System status displaying normal on departure
MSA-DCA | WA3512912 | West end of A shed - Water leaking through broken skylight. Inspect and seal gaps | DO NOT USE TO BE DECOMMISSIONED A Shed, Victoria Quay, Fremantle-A Shed | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 07 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-12 08:30:00 | Fail | Inspected Leak around skylight - submitted BRAF - BRAF Declined. Closing out and charging costs to date as requested. Refer to Reese Withey
MSA-DCS | WA3512376 | Unit 1, toilets- last toilet cistern broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-07 13:06:00 | Pass | Replaced cistern and pan rubber, aslo repaired leak in plumbing duct.
MSA-DCS | WA3512385 | MPU (8)- Cell light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 10:00:00 | Pass | Repaired faulty lights in mpu
MSA-DCS | WA3512387 | INF (10), Control room- 2x lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Aug 2020 | 2020-08-11 17:00:00 | 2020-09-11 15:00:00 | Fail | Replaced damaged lights in infirmary control rooms
MSA-DCS | WA3512389 | Security Area- Download footage Cell M17, incident 01/08/20 | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 07 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 08:30:00 | Pass | Checked with Security SO regarding video required as a download of video was carried out on 04/08/2020 for same date and time. (WA3510210) Located memory stick with data on Security Managers Desk. Confirmed required video was available on memory stick.
MSA-DCS | WA3512411 | ground staff kitchen urn on the wall not working no water coming out | Warminda Hostel | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 12:15:00 | Pass | Replaced outlet tap . Tested and all ok
MSA-DCS | WA3512439 | Unit 2, Cell 49 door skin seperated and twisted | Karnet Prison Farm | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2021-01-18 11:45:00 | Fail | NEW DOOR INSTALLED
MSA-DCS | WA3512440 | Unit 2 lower inside landing- toilets exhaust fan faulty making grinding noise | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 08:30:00 | Pass | Investigate unit 2 lower landing toilet exhaust fan.Fan requires replacement
MSA-DCS | WA3512451 | unit 1 hut toilets exhaust fans not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 10:00:00 | Pass | Investigate unit 1 huts toilet exhaust fan.Fan requires replacement.
MSA-DCS | WA3512485 | Unit 4, PRU perimeter, not unable to reset zones | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Aug 2020 | 2020-08-07 16:48:47 | 2020-08-07 18:15:00 | Fail | Option to SECURE/ACCESS the PRU microphonics zones were greyed out and inaccessible on the Cardax workstation. Controllers 27, 28 and 29 not communicating. Controllers and modems tested ok. Found Comms had been disabled on Command Centre program. Enabled Comms and reset the 3000 controllers via the Command Centre software. Fence zones secured ok.
MSA-DCS | WA3512487 | Medium prison control room - CCTV monitors has no imput | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 08:50:58 | 2020-08-07 15:00:00 | Pass | Fault had rectified itself before I arrived on site. Control room officer explained that earlier there was no CCTV image displayed when a perimeter alarm activated. Further investigation points towards a power issue. All cameras now ok. Alarm monitors ok.
MSA-DCS | WA3512503 | control faulty desk monitor-SEME on site | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 09:02:59 | 2020-08-07 13:30:00 | Pass | Attended site and found monitor in Gatehouse faulty. Replaced with new 27inch Dahua monitor - Seme stock used, Purchase order no is 64018240.All installed and tested ok. Job complete
MSA-DCS | WA3512522 | Abattoir- Coolroom fan in boning room fridge not working | Karnet Prison Farm | GMP-BR- HO | Refrigeration | Coolroom (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-10 16:00:00 | Pass | attended site and repair wiring to fan motor in boning room. test , all is operational
MSA-DCS | WA3512604 | Reception glass security door not latching closed-alarm swipe entry door | Mandurah | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-10-21 08:30:00 | Fail | Technician attended the site of Department of Corrective Services 7328 to the Admin Reception Swing Door on 12/08/2020. Following a full test and inspection of door components found fault to be door latch is worn and needs replacing. Quote was submitted. Technician retuned on site on 21/10/2020 to change internal lock in door as part of quote. Full test and inspection of door function completed prior to leaving site.Breakdown of cost: Labour = $260.00Parts = $ 1392.00
MSA-DCS | WA3512661 | Unit 5, Cell D6- Toilet leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-10 12:00:00 | Pass | nil
MSA-DCS | WA3512694 | gate house sallyport outer roller door jammed in up position | Banksia Hill Detention Centre | GMP-BR- HO | Building | Automatic Doors (BU) | AFD Contracting | 0 | CLOSE | 07 Aug 2020 | 2020-08-07 14:47:29 | 2020-08-07 12:40:00 | Pass | 07/08/20Inspected door.Found to be rolled up wrong way.Un-rolled door and rolled up proper way, drive chain fell off during rolling.Left door in open position for replacement / repair.
MSA-DCS | WA3512703 | Unit 1, Cell 50 - broken ceiling light | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 10:53:11 | 2020-08-08 10:30:00 | Pass | replaced cell light with LED
MSA-DCS | WA3512711 | monitor room door not opening- SEME on site | Wooroloo Prison Farm | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 10:58:02 | 2020-08-13 18:45:00 | Fail | sourced sundries and reed switch as technician advised reed switch is damaged.attended site and removed the lock from the door, powered lock, can hear lock attempting to open, strike is jammed.cleared obstruction from door lock. reinstalled door lock and replaced damaged 19mm reed switch.tested door, working correctly. tested interlock fucntion on Gallagher and confrimed correct operation
MSA-DCS | WA3512714 | Unit 1, D wing cleaning cupboard- light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 09:00:00 | Pass | Repaired light
MSA-DCS | WA3512717 | Boilerhouse, Timer to compressor broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-13 11:00:00 | Fail | Air compressor timer not working.
MSA-DCS | WA3512723 | Boilerhouse, Compressor 2 - Compressor not running. No Power | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-09-03 14:30:00 | Fail | Compressor power
MSA-DCS | WA3512727 | unit 1 C-D Common Area Kitchen Sink Spout Is Broken | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-09-01 14:45:00 | Fail | Outlet was missing tryed to replace with new outlet didn’t work need hole new set had to order in
MSA-DCS | WA3512743 | Unit 2 B7 Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-14 13:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk.
MSA-DCS | WA3512745 | Unit 2, B-10 - Bed panel broken | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-25 13:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3512747 | Unit 2, B-09 - Bed panel broken | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-25 10:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3512749 | Unit 1 B/D Dayroom has had 2 large windows smashed completely | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 0 | CLOSE | 07 Aug 2020 | 2020-08-07 15:21:33 | 2020-09-01 14:30:00 | Fail | SMASHED WINDOWS RE GLAZED
MSA-DCS | WA3512752 | Unit 2, B-08 - Bed panel broken | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-25 16:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk.
MSA-DCS | WA3512754 | Unit 2, B16 - Bed panel broken | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-24 10:30:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3512756 | Unit 2 S/O Office- tombstones are broken on the fluro lights | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-19 12:00:00 | Fail | Investigated damaged lights in unit 2 s/o office. Tried to source replacement parts with no success. Ordered replacement fittings and installed
MSA-DCS | WA3512757 | Unit 2, B15 - Bed panel broken | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-27 16:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunks.
MSA-DCS | WA3512758 | Unit 6, Cell C2- Bed light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-10 08:30:00 | Pass | Repaired faulty lights in unit 6 c2
MSA-DCS | WA3512759 | Unit 2, B14 - Bed panel broken | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-27 13:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunks.
MSA-DCS | WA3512760 | Unit 2 B13 Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-27 10:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunk beds.
MSA-DCS | WA3512788 | Abattoir multi stage pumps faulty (ROLLED GROVED) | Karnet Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-11-27 09:27:00 | Fail | 10,8,20Traveled to Karnet pick up stagging pumps with trolley one by one.11,8,20Took staging pumps to Perth Rewind explained what had to be done to the motors and impalas
MSA-DCS | WA3512918 | Front gate master control pod Cameras 3 & 12 Fault Not Connecting | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 13:02:58 | 2020-08-11 11:34:00 | Fail | Rectified and fixed camera 4 and 12 . Port assigned to camera 4 is faulty, to be completed with WA3454453.
MSA-DCS | WA3512938 | control room PDA monitor sender output 12 are on and should be off | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 13:19:22 | 2020-08-07 15:00:00 | Pass | Job complete
MSA-DCS | WA3512973 | Unit 6 D wing roof Air-conditioning unit on roof has a leaking pipe | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 13:45:14 | 2020-08-10 14:30:00 | Fail | Identified leak as small pinhole leak on flexible hose. Hose has been replaced.
MSA-DCS | WA3512975 | Kitchen- Water pipe is broken- (water has been isolated) | Boronia Pre-release-AM06 - Prisoner Accommodation House 1 and 2-Ground Floor-House 1 - Kitchen Area | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 13:48:13 | 2020-08-07 15:15:00 | Pass | Attended site,Locate leaking 15mm copper water main to kitchen, use kempress to repair leaking pipe. Tested works on completion
MSA-DCS | WA3513007 | Unit 14, B & D- Prisoners personal lock is not working & prisoner stuck in cell. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-10 09:00:00 | Pass | Cut open jammed lock, require parts.Replace mortise lock.
MSA-DCS | WA3513028 | Gwynlea Building ground entry Hard to shut door possibley due to door closer. | Nyandi Training Academy | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 11:00:00 | Pass | Attended site and carried out repairs to the hydraulic door closer on front entry door to Gwynlea building
MSA-DCS | WA3513042 | sewage plant - soda ash pipes are blocked | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Plant & Pumps (WM) | Daniel Chrisp Pty Ltd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 14:28:32 | 2020-08-08 15:45:00 | Fail | Watercon employees attended site 08/08/2020Flushed the line, replaced soda ash dose lines.Materials in stock value $100.00 excluding gst.Minimum 6 hour callout fee $960.00 excluding gst (Weekdays) includes travel within metro area.
MSA-DCS | WA3513051 | Unit 1 Prisoner Lock Tongue Jamming and Door Rubbing on Frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 15:18:24 | 2020-08-10 12:00:00 | Fail | 07/08/2020 - Attended at 16:15 but site could not facilitate escort. Advised to return Monday10/08/2020 - Realigned door to restore proper function.
MSA-DCS | WA3513053 | Unit 1, B 11 - No Water to Sink Taps | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 15:22:22 | 2020-08-08 10:20:00 | Pass | Service cold water tap to basin and replaced split pin.
MSA-DCS | WA3513055 | Unit 1 B10 No Water to Sink Taps | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 15:23:55 | 2020-08-08 11:50:00 | Pass | Reported fault was in unit D cell10.Replaced cold water spindle to basin,installed mini stop to adjuste water flow to basin.
MSA-DCS | WA3513083 | SO Visits CCTV monitor 2 not working at fault. | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Aug 2020 | 2020-08-08 16:13:41 | 2020-08-07 17:48:00 | Pass | Loose connection monitor power, fixed. Monitor back to normal operations. Job completed.
MSA-DCS | WA3513092 | SITE COST Key watcher door - hinges are loose on door | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 07 Aug 2020 | 2020-08-07 20:58:15 | 2020-08-21 10:45:00 | Fail | Rang Prison after job called through to me ( Friday evening 7/8/20)Spoke to Officer in Charge - Angela Cosgrove- she advised - job can be done Saturday Morning.(8/8/20)Attended saturday Morning , made temporary repaires to Door .Waiting on parts to finish repairs .Returned to site 21/08 7:30AM - replaced middle hinge made repairs to other hinges finished 10:45AM
MSA-DCS | WA3513104 | Unit 4 - Perimeter fence is not alarming | Bunbury Regional Prison-Administration | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 07 Aug 2020 | 2020-08-08 05:10:28 | 2020-08-08 11:30:00 | Fail | Attended and check the status of all controller connected not alarming as per job request. Conducted full test PRU microphonics ok working as normal.
MSA-DFES | WA3512398 | admin building faulty door lock | FESA RHQ - Forrestfield | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 0 | CLOSE | 07 Aug 2020 | 2020-08-07 12:00:59 | 2020-08-07 08:55:00 | Pass | Replace knob set to room 10 demountable
MSA-DFES | WA3512545 | ground boom gate Intercom audio not working correctly-see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-13 14:00:00 | Pass | 10/8/20 - Ryan VestyChecked boom gate intercom, staff unable to hear from exit unit, entry unit ok.After investigation, found microphone in unit weather damaged, replacement required.13/8/20 - Ryan Vesty, Dylan ParslowProgrammed IP address for new intercom unit, replaced exit gate intercom.Advised by IT that they need to finish off programming as it is on the site network.
MSA-DFES | WA3512881 | ground dorm bedside light switch not working | CFRS Duncraig | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 17:15:00 | Pass | Located faulty switch on end dorm room. Replaced with new switch and tested for function. Notified staff of works and left site at 1715
MSA-DFES | WA3512904 | Admin- Staff Dining Room- Urn is leaking water at filter connection under the sink | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 08:40:00 | Pass | Replaced broken fitting to filtration stem elbow
MSA-DFES | WA3512950 | Rear yard- Burst hot water pipe | CFRS Ellen Brook | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 07 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-07 16:14:00 | Pass | Repair burst on hot supply from h w u
MSA-DFES | WA3512953 | Approx 7 fluro lights not working in below locations | CFRS Armadale | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-21 15:45:00 | Fail | Located 5 x Faulty fluro lights in Engine room. Fittings are cracked and are not longer suitable. Have spoken to the station officer and would like them swapped out. Have ordered parts to complete works and left site. Will return to complete installation.Returned and installed 5 new LED lights in Truck Bay
MSA-DTAG | WA3512448 | Lvl 10 - Stainless steel sign has detached from wall outside male staff toilet | Central Law Courts | GMP-BR-HO | Signage | General Signage (SI) | Midolo Building Services | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-07 09:15:00 | Pass | FIX SIGN TO WALL
MSA-DTAG | WA3512519 | Contol room unable to log into unison on one of the monitors | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 07 Aug 2020 | 2020-08-07 13:18:03 | 2020-08-07 11:00:00 | Pass | Restarted SQL. All working OK. Checked all functions.
MSA-DTAG | WA3512546 | 1903, Female Bathroom, Barristers Robing Room- Flooding from water leak behind cistern | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 07 Aug 2020 | 2020-08-07 13:32:11 | 2020-08-07 13:00:00 | Pass | Replaced cistern and WC seat
MSA-DTAG | WA3512732 | 1903, Female Bathroom, Barristers Robing Room- Taps on both sinks faulty/damaged | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-07 14:30:00 | Pass | Re washer 2x basin
MSA-DTAG | WA3512750 | 1903, Female Bathroom, Barristers Robing Room- No hot water to sinks | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-07 15:21:00 | Pass | After investigation male and female toilets are only supplied by cold water, they have never had hot water running to them.
MSA-DTWD | WA3512391 | Q Block, No heating to building ( CH2 in fault ) | Joondalup McLarty Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 07 Aug 2020 | 2020-08-07 17:00:00 | 2020-08-07 16:00:00 | Pass | Accessed site and q block. Plant area bms showing chiller 2 fault. Plant area chiller compound checks of pumps , valves and switching ok. Chiller 2 showing lock out due to flow error and then press transducer fault. Keypads lock rectified and flow returned providing lower head press. Bms fault cleared and heating water operation monitored to ahu and vav units.Settings and functions checked as hot water now increasing supply air temps as required. Set points reached and heater ramped down. Unit in auto.
MSA-DTWD | WA3512531 | I Block, Room I009- Broken Window | Balga Campus | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-10 16:30:00 | Pass | ATTENDED SITE, REGLAZED BROKEN GLASS TO WINDOW 6.38 CLEAR LAMINATED SAFETY GLASS 1 - 1153 X 730
MSA-DTWD | WA3512558 | Lvl 1 & 2 Mezzanine- South Staircase- Lighting has blown | Perth Campus B4 | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 16:15:00 | Pass | COMPLETED
MSA-DTWD | WA3512578 | A block A237 Faulty air quality being reported-See notes | Leederville Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-27 15:04:00 | Fail | No further works required PFM have rejected submitted BRAF.
MSA-DTWD | WA3512614 | F Block, FG02, Male toilet- Toilet Exhaust Fans Not Working- see further info below | Carlisle Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 10:30:00 | Pass | Replaced snapped belts
MSA-DTWD | WA3512617 | Kitchen behind BLD 838- Hot water system faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Lane's Plumbing | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-07 15:35:00 | Pass | job completed - Replace faulty over temp switch and section of corroded pipework and isolation valve
MSA-DTWD | WA3512664 | J block copper piping has been stollen, remove what is left replace with PVC | Rockingham Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-20 15:00:00 | Fail | Have attended site rescheduled 19/8/20
MSA-DTWD | WA3512794 | E Block, Restaurant Kitchen, the flat top grill pilot light does not stay on | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-07 16:00:00 | Pass | REPLACED REGULATOR.
MSA-DTWD | WA3512813 | F-Block ( shed ) Eco 1 blown fluro's | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 07:00:00 | Pass | Replaced faulty components to lights out in f block shed
MSA-DTWD | WA3512814 | G block ground G129 male toilets 2nd and 3rd cubicles blocked | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 13:40:00 | Pass | Cleared blockage and adjusted outlet valves
MSA-DTWD | WA3512843 | T-Block, level 1, room T107,108 - water leak in new ceiling in hallway above roomT107, T108, this wa | Joondalup McLarty Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 07 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-10 09:00:00 | Pass | Inspected roof void above ceiling tile all insulation was found to be dry, checked roof- window in open position - closed window will get site to monitor.
MSA-DTWD | WA3512941 | U block U015 Fault to diamond edger (suspect new bearing required) | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-20 11:30:00 | Fail | U Block U015 Fault to diamond edger. Check grinder & controls. Dismantle shaft & housing. Remove to workshop. Shaft & bearing cap to be machined as required. Angular Contact bearings to be replaced with same type of bearings. Replace shaft seals. Return, assemble & test.
MSA-DTWD | WA3513006 | B block L3 has power surge issue-see notes | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 07 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-11 09:30:00 | Pass | Attended site and signed in. Located L3 room with power issues. Spoke with staff and IT regarding the issues about the power. Inspected and tested power to computers and outlets. Found 250v to all circuits powering the computers. Turned on all computers and all fired up and all monitors working, we were advised that some random monitors turned off. Whilst we were on site and checking all monitors in the classroom works even the 1 that pushed to the back of the row and said to be not working, did everything it supposed to. The manufactures info on the monitors says 100v to 240v. Power on site is high but not uncommon. Tested and checked terminals and load in switchboard. Nothing can be found. Suggest maybe issue with cords and programming. All PCs turn on and all monitors work. Advised site. Job complete
MSA-DTWD | WA3513010 | Zone 27, G block - low battery alarm | Leederville Campus | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 07 Aug 2020 | 2020-08-10 17:00:00 | 2020-08-11 11:00:00 | Fail | 07/08/2020, 1500-1530Room is a studio, occupied until 7pm. Unable to access device. Had to disable zone for now return early morning ifpossible10/08/2020, 815-830Room occupied again unable to access11/08/2020, 1045-1100Replaced back up battery and reactivated zone
MSA-DTWD | WA3513046 | Block 6 Bricklaying Faulty lid support to pugmill | Thornlie Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 07 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 12:00:00 | Pass | Replaced safety latches to pugmill mixer in block 6
MSA-DCS | WA3513112 | Front gate key watch is not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Aug 2020 | 2020-08-08 10:10:35 | 2020-08-08 08:30:00 | Pass | Reset machine and gave out IDs in question tested ok
MSA-DCS | WA3513123 | Karnet Prison Farm - in Unit 2 in toilet block broken window | Karnet Prison Farm | GMP-BR- HO | Carpentry | Materials (CA) | Midolo Building Services | 2 | CLOSE | 08 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-14 14:00:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3513128 | Hakea Prison - DVM database constant alarming | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Aug 2020 | 2020-08-08 12:27:56 | 2020-08-11 15:53:00 | Fail | Invetsigated software fault and repaired operating system. Tested OKJob Complete
MSA-DCS | WA3513139 | Bakery has had a breakdown. The bakery prover has tripped and all the breakers have tripped | Casuarina Prison | GMP-BR- HO | Catering | Catering Services (CT) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 08 Aug 2020 | 2020-08-09 09:32:59 | 2020-09-14 13:30:00 | Fail | 08/08/20Arrived at site liaise with reception, walk to bakery, identify faulty proover, supply isolate, test/fault find diagnose and found front right side wet element was short circuiting to earth, removed replaced with new element, reassembled all components and tested okay but fans weren't activating, tested and found relay block was loose and the pins were bent, repaired, reassembled all components and tested all components to correct heat, opened doors and retested all components and tested all okay.10/08/20Called as requested to the prover fans not running. Found the fan relay intermittently failing so bypassed temporarily until a new relay and base can be supplied and replaced. Parts required: 1x 24v relay 1x relay base 14/09/20Sign in on site Escorted to bakery area Gain access to cabinet Isolate proover Remove and replace faulty relay Heat and test proover Found fans working and heating.Manager approved proover operating ok
MSA-DCS | WA3513140 | Unit 2 camera in the pod is frozen | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Aug 2020 | 2020-08-08 13:24:37 | 2020-08-08 11:30:00 | Pass | Refreshed cameras and brought them back onscreen
MSA-DCS | WA3513246 | Cell intercomm is not working-Unit 4 C-8 and Unit1 B-5 cell calls are not hanging off | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 08 Aug 2020 | 2020-08-09 14:44:55 | 2020-08-08 17:00:00 | Pass | Tecera fault due to damage Cat5 patch lead, replaced. Job completed
MSA-DCS | WA3513263 | Hakea Prison-Main Gatehouse - Control Room - DVM Database in constant alarm. | Hakea Prison-Main Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 08 Aug 2020 | 2020-08-08 23:14:18 | 2020-08-11 15:56:00 | Fail | Investigated server issues, repaired faults and tested ok.Modified operating system to prevent this fault reoccuring.Job Complete
MSA-DCA | WA3513315 | Cetenary Plant room- AC leaking in plant room. | Art Gallery of WA - James St - Centenary Gallery Ground Floor - Plant Room | GMP-BR | Air Conditioning | Building HVAC Maintenance (Major Plant) (AC) | EQUANS Mechanical Services (WA) Pty Limited | 0 | CLOSE | 09 Aug 2020 | 2020-08-09 13:47:27 | 2020-08-13 09:30:00 | Fail | Job completed. Cracked pipwork replaced and pump bracket re secure.
MSA-DCA | WA3513323 | Revolving doors are not operating, unable to to secure building. | Maritime Museum Victoria Quay-Main Building | GMP-BR | Building | Materials (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 09 Aug 2020 | 2020-08-09 14:16:06 | 2020-08-10 14:30:00 | Fail | Technician attended the site of WA Maritime Museum to the Main Entry Auto Door No. W21057 on 09/08/2020. Following a full test and inspection of door components found fault to be a lot of water damage to controller and water dripping through ceiling. Looks like pb board for door is faulty due to water damage, could not lock door, client to arrange static guard for tonight and tech will reattend tomorrow. Need 2 techs to see if door can be locked.Technician/s re-attended site on 10/08/2020 to diagnose problem with revolving door. Door has water damage which has caused controller to fault. Technicians cleaned all corrosion from terminals and internal control board see if they could get controller working to lock door, also found ioa 1 controller to have shorted out and was unable to lock door electrically. They have wedged door in closed position so it cannot be moved, and door is now secure and a new control board is required. Issue with leaking roof needs to be addressed to pr
MSA-DCS | WA3513274 | Cell call system - Network Error | Broome Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Aug 2020 | 2020-08-10 01:18:20 | 2020-08-10 07:30:00 | Fail | Contacted site,Confirmed cell call system had been working and no faults have appeared in 24 hours
MSA-DCS | WA3513299 | Front Gate- Seme to attend - Key watch system has malfunctioned. | Casuarina Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 09 Aug 2020 | 2020-08-09 12:44:12 | 2020-08-09 10:30:00 | Pass | Reset key watcher and tested ok
MSA-DCS | WA3513321 | Security Office -CCTV screen is blank no reception | Banksia Hill Detention Centre-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 09 Aug 2020 | 2020-08-10 10:05:54 | 2020-08-09 14:15:00 | Pass | Power outage on site and both ebi and geutebruck ws failed to communicate, fixed the network switch. Job completed.
MSA-DCS | WA3513355 | Melaleuca Womens Prison- IN ECR Control room locking mechanism is working randomly | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 09 Aug 2020 | 2020-08-09 17:30:51 | 2020-08-09 14:45:00 | Pass | Adjust and tighten loose air lock electric strike.
MSA-DCS | WA3513360 | Bandyup Prison - Water leak from the roof in cell L3 | Bandyup Prison | GMP-BR- HO | Roofing | Roof Safety Systems (RF) | Midolo Building Services | 3 | CLOSE | 09 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-10 12:59:00 | Pass | REPAIRS TO ROOF SHEETING AND FLASHINGS
MSA-MRWA | WA3513295 | Fire indication panel fault-Investigate and report | Don Aitken Centre MRWA Head Office-Main Building-Basement-FB02-Fire Equipment Riser-East | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 09 Aug 2020 | 2020-08-09 12:17:11 | 2020-08-09 09:45:00 | Pass | Isolated zone 30 placed info tag on FIP & advised FM.
MSA-DCA | WA3514268 | Leak in ceiling. Please isolate/shit off power to light fitting | State Library of WA-Main Building-Level 3-Print Room - Next to Finance | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 16:03:00 | Pass | Located leaking light in print room level 3 new office, removed light fitting, moved 413 out of the way of water drop, showed leak to Ben , Reece and Dan , leak is from upstairs slab. Put light fitting in level 3B switchboard to dry out, as was still working
MSA-DCA | WA3514359 | fire panel dressing room 3 WC detector in fault - resulted in full evac from building | His Majesty's Theatre-Theatre Building-Ground Floor-Stage Area | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 15:15:00 | Pass | Zone 005 in alarm, brigade cleared alarm. Thermal detection in alarm while venue was in performance mode. No one using changerooms at time of alarm.Further investigation required.
MSA-DCA | WA3514437 | return air fan No9 VSD in fault | State Library of WA-Main Building-Level 5-Main Plant Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:44:00 | Pass | Attended P2 call-out. AHU 9 on BMS not indicating any alarms. SAF VSD had active Fire Mode alarm and RAF had Overcurrent Alarm. Reset both. Fans started, monitored operation, no issues found with start-up or staging. Likely event of power loss causing SAF to alarm following RAF to trip on overcurrent trying to maintain static pressure. No further alarms present on AHU 9 during inspection.
MSA-DCS | WA3513401 | Fault coming up in the fire panel. Shows earth fault. | Wooroloo Prison Farm | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 05:37:01 | 2020-08-10 15:00:00 | Pass | System status displaying normal on departure
MSA-DCS | WA3513415 | Video is frozen in the control room. | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 10 Aug 2020 | 2020-08-10 10:05:07 | 2020-08-10 08:00:00 | Pass | Job completed - After hours call out for camera issues
MSA-DCS | WA3513487 | Kitchen - 3 tiered pizza oven - broken glass panel | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 07:08:07 | 2020-08-19 15:30:00 | Fail | 10/08/20Called as requested to the oven door glass smashed. Found the the door smashed as reported took the Necessary details down for replacement. 19/08/20Returned to site with the parts required fitted tested all working correctly now.
MSA-DCS | WA3513533 | Jeelia, C3 - door wont lock from inside cell | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 10 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 09:30:00 | Pass | Adjusted hinges and strike to restore proper function.
MSA-DCS | WA3513539 | Jeelia, A1 - Door will not align with lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 10 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 10:45:00 | Pass | Replaced faulty lock, replaced worn hinges and realigned door.
MSA-DCS | WA3513547 | Skype, Cleaning Cupboard - door closer damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 10 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-14 13:30:00 | Fail | New door closer installed
MSA-DCS | WA3513559 | Barista - window near barista leaking. | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 13:00:00 | Pass | WINDOW RE SEALED
MSA-DCS | WA3513561 | Jeelia, B1 - Cell window leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 09:00:00 | Pass | WINDOW SEALS REPAIRED
MSA-DCS | WA3513568 | Gascoyne, A2 - window mesh is loose | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 11:00:00 | Pass | WINDOW MESH RE SECURED
MSA-DCS | WA3513589 | Security Area, Lobby area - Lobby monitors are not working - power in on | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 07:58:08 | 2020-08-10 09:30:00 | Pass | Attended lobby, found two of three monitor screens, displaying video, overplayed on one monitor. Corrected problem and instructed Lobby Officer on how to resolve problem in future.
MSA-DCS | WA3513593 | unit 6, B wing, Cell B01 - Vent under window will not close | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 14:30:00 | Pass | LUBICATE VENT
MSA-DCS | WA3513605 | MPU, M3 - SPU Ceiling light flickering when turned on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 08:30:00 | Pass | Repaired faulty lights in mpu m3
MSA-DCS | WA3513612 | MPU, M8 - SPU light not working at all | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:00:00 | Pass | Repaired faulty lights in mpu m8
MSA-DCS | WA3513616 | Unit 7, B wing - camera frozen | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-13 09:30:00 | Pass | No video on B wing Unit 7, fixed the decoder fault. Job completed.
MSA-DCS | WA3513634 | Lvl 4, Male toilets- Water leak from malehole | East Perth-Main Building-Level 4 | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-11-20 12:30:00 | Fail | Attended site and sealed additional roof penetrations on roof area.
MSA-DCS | WA3513636 | laundry - hot water pipe leak | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 08:15:49 | 2020-08-11 12:00:00 | Fail | Investigate water leak to laundry,Locate blocked rain head and down pipe external to building, also locate blocked box gutter to roof of laundry. Supply and install new 100mm down pipe from rainhead and divert as required for repair. Access roof and clean out box gutter. All water lines appear to be in good working order, further water ingress to be monitored.
MSA-DCS | WA3513645 | Unit 3, Cell B9- Window doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 15:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3513648 | Unit 2, Roof - water everywhere in roof space, we believe it is the aircon unit. | Casuarina Prison | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 08:22:57 | 2020-08-11 12:30:00 | Fail | Barrier to redirect water from condenser. All ok
MSA-DCS | WA3513650 | Unit 3, Cell D7- Window doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 10:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3513652 | Unit 5, Cell C2- Window doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 09:15:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3513657 | Unit 3, Cell A3- Window doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 12:15:00 | Pass | RE-NEW SPIRAL BALANCES
MSA-DCS | WA3513660 | Unit 3, Cell B3- Window doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 14:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3513664 | Unit 13, Lobby on both sides - near the control windows are leaking water | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 10:45:00 | Pass | REPLACED OLD SEALER - REPAIRED EXPANSION JOINTS TO WALLS OF BOTH SIDES
MSA-DCS | WA3513670 | Unit 3, A7 - window doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 13:15:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3513677 | Unit 4, D8 - cell alarm not very clear | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 13:00:00 | Pass | Clean and clear the toothpaste from the cell call front plate. Test the cell call ,ok and working. Job completed.
MSA-DCS | WA3513681 | Unit 5, Cell A3- Toilet cistern running constantly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 10:30:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3513685 | Unit 3, Cell D4- Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-10 13:00:00 | Pass | nil
MSA-DCS | WA3513713 | Urquhart, C Wing- Fire alarm activated, Further info below | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 14:00:00 | Pass | detector disabled, reset and all ok
MSA-DCS | WA3513717 | Level 4, New zip water tap - has ‘zapped’ (electrocuted) a staff member a few times. | East Perth | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 08:35:45 | 2020-08-10 12:07:00 | Pass | Staff reported being ‘zapped’ when using the cold side of the zip dispenser. Visually checked earth connections internally and all other connections, no defects found. Probably caused by static, but advised to have an electrician check the unit. Zip unit left unplugged.
MSA-DCS | WA3513719 | Zone 2- IR beam not armed & falling to activate | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 11:00:00 | Pass | Checked for power at all TX and RX beams. Checked for alignment and cleaned all beam covers. Enabled scanning on EBI software. Tested ok to control.
MSA-DCS | WA3513723 | Jasper, B Wing- HWS no power & no hot water | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 09:15:00 | Pass | Replced faulty thermostat at the hwu in jasper b wing
MSA-DCS | WA3513727 | Unit 3, Cell D12- Copper pipe leaking under the sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-10 16:09:00 | Pass | nil
MSA-DCS | WA3513728 | Unit 6, A & C day room - hot water urn faulty again, the water draining out. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 10:30:00 | Pass | Replaced inlet solenoid and controller pcbRecal hot
MSA-DCS | WA3513732 | Unit 3, Cell D8- Toilet seat broken & bowl cracked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-11-17 11:30:00 | Fail | Staff informed that cellIs out of action for 24hours to allow pan to set
MSA-DCS | WA3513734 | Unit 1, Cell B9- Cell call not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 08:49:45 | 2020-08-13 12:00:00 | Fail | Replaced vandalised and damaged cell call unit. Job completed.
MSA-DCS | WA3513735 | Unit 1, Cell B8- Cell call not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 08:51:09 | 2020-08-12 09:30:00 | Fail | Cell call vandalised with toothpaste, dismantled and cleaned.job completed.
MSA-DCS | WA3513737 | Unit 1, Cell C5- Cell call not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 08:52:16 | 2020-08-12 15:25:00 | Fail | Dismantle and replaced the defective cell call, replaced with and test ok. Job completed.
MSA-DCS | WA3513746 | Unit 3, Cell D9- Toilet continues to run after flushing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-10 15:00:00 | Pass | nil
MSA-DCS | WA3513751 | Unit 13, Cell A7- Shower leaking into bottom bunk | Casuarina Prison | GMP-BR- HO | Glazing | Shower Screens (GL) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 13:30:00 | Pass | RE SEAL LEAKING SHOWER SCREEN
MSA-DCS | WA3513759 | Unit 14, A Wing, Cleaning Store- water damage | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-10 11:00:00 | Pass | nil
MSA-DCS | WA3513772 | Unit 6, A19 - Broken window | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 08:51:35 | 2020-08-11 11:30:00 | Fail | WINDOW RE GLAZED
MSA-DCS | WA3513776 | Unit 6, D8 - Broken window | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 09:04:13 | 2020-08-11 15:00:00 | Fail | CELL WINDOW RE GLAZED
MSA-DCS | WA3513780 | Reception - All window louvres require fixing as rain water is leaking on X-ray machine | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 09:05:24 | 2020-08-11 13:30:00 | Fail | MANUALLY CLOSED WINDOWS - WILL MONITOR OVER NEXT FEW DAYS
MSA-DCS | WA3513787 | Gatehouse- Outer D fence in fault | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2021-04-06 13:30:00 | Fail | Transmitter on E2 outer replaced tested ok.
MSA-DCS | WA3513789 | Unit 6, Cwing, Cleanig cupboard - Light switch pushed in resulting in lights not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 14:00:00 | Pass | Replaced light switch
MSA-DCS | WA3513797 | ground Rear of Kitchen (near exit/ fire door) Water leaking from hose near joint. | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:57:00 | Pass | nil
MSA-DCS | WA3513835 | main building, A-Wing Scenario Cells toilets - Toilet in Cells 5 water leaking into bowls. Cells 3 & | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:00:00 | Pass | nil
MSA-DCS | WA3513861 | Unit 7, Roof- Potiental Rat issue, further info below | Casuarina Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 13:25:00 | Pass | Treated reported rat problem in self care by installing rodent baits in roof space
MSA-DCS | WA3513911 | Visits booking office roof leak | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-12-10 14:15:00 | Fail | roof repaired to rectify leaking
MSA-DCS | WA3513934 | Unit 2 A/C hot water urn leaking behind the wall area and onto floor. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-18 11:30:00 | Fail | Collected parts offsite. Installed and calibrated new unit. Removed old unit
MSA-DCS | WA3513935 | gate house PO4and PO3 tamper alarms activated - SEME on site | Karnet Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 10:19:41 | 2020-08-11 19:02:00 | Fail | Sourced heavy duty roller reed from seme stock x2removed reed switches, modified mounting brackets and installed 2x new reed switches and 2k2 resistor.checked Senstar, all faults have cleared
MSA-DCS | WA3513954 | Veg preparation - Potato Rumbler not working | Casuarina Prison | WSM-BR-SITE | Equipment | Electrical Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-21 09:00:00 | Fail | Potato Peeler faulty. Check peeler, remove for repair. Dismantle, remove motor & bearing housing, motor has broken shaft. Check bearings & seal. Assemble & test. Return to store, return & install in vegie prep.
MSA-DCS | WA3513960 | Bakery, workshop - Mixer is jammed | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 10:33:07 | 2020-08-10 14:00:00 | Pass | 10/08/2020Called as requested to the mixer bowl lift seized. Stripped out the whole bowl lift mech and gearing. Found the gear shaft from the handle to be seized so freed off lubricated assembled tested all ok. Shaft and gear mech should be replaced due to wear. Parts required (no Model # serial number - not available)1x gear shaft assemblyNot Available
MSA-DCS | WA3513971 | Unit 5, B Wing Shower - tap not working, just spinning | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-11 08:30:00 | Pass | Replaced missing split pins in shower taps.
MSA-DCS | WA3513977 | reception Leaks to louvered windows in storm happens everytime heavy weather | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2021-03-15 09:00:00 | Fail | THE LOUVRES HAVE BEEN REPAIRED AS NOT CLOSING PROPERLY DUE TO BEING WOUND TOO TIGHT -ADVISED STAFF TO CLOSE GENTLY & NOT LET PRISONERS OPERATE CLOSING MECHANISMS
MSA-DCS | WA3513986 | Reception Louver window winders not working | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 10:42:54 | 2020-08-10 12:30:00 | Pass | INSPECTION ONLY - RRP have no costs - this job was invoiced/completed on wa3513977
MSA-DCS | WA3513990 | Unit 5, Cell A1- Window guide rails faulty | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 10:00:00 | Pass | RE NEW SPIRAL BALANCES
MSA-DCS | WA3514010 | Kitchen, bain marie water tap leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-10 14:00:00 | Pass | Replaced bain Marie broken water tap
MSA-DCS | WA3514087 | staff gym, female toilets - Light switch next to female toilets faulty | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-14 10:00:00 | Fail | Repaired broken lights
MSA-DCS | WA3514094 | Unit 1, C10 - light broken in cell | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 14:00:00 | Pass | Repaired broken light Unit 1, C10
MSA-DCS | WA3514103 | Unit 5, C7 - shower screen cracked | Hakea Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-31 15:00:00 | Fail | REPLACE SHOWER SCREEN
MSA-DCS | WA3514111 | Laundry - No 4 Washing maching - not spinning | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 11:54:49 | 2020-08-10 14:55:00 | Pass | Hakea - AMS669667 WA3514111- No 4 Washing maching - not spinningInspect & test WM. Trace no spin to errors on the computer. Reset oil injection times and modify programme spin time. Test WM - OK
MSA-DCS | WA3514117 | Unit 4, D Wing Yard Door- Lock faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 14:15:00 | Pass | Replaced hinges and realigned door
MSA-DCS | WA3514122 | Unit 2 C3 blocked toilet | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 11:57:19 | 2020-08-11 07:20:00 | Pass | Plunger used to unblock toilet
MSA-DCS | WA3514126 | Kitchen, Older rational- Failing to perform a wash cycle | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:45:00 | Pass | Replaced Pump test ok
MSA-DCS | WA3514153 | Unit 1, Cell B15- GPO Faulty. Trips RCD when used | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 15:00:00 | Pass | Replaced broken gpo
MSA-DCS | WA3514168 | Centre car park staff entry - Ceiling water leak | Walcott Centre (Central West Metro ) | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-13 13:00:00 | Pass | Attended site and carried out inspection to roof area, safety harness required due to height and pitch of roof.All valley gutters cleaned due to the excessive build up of leaves.
MSA-DCS | WA3514171 | Entry to the old psych area - Ceiling water leak | Walcott Centre (Central West Metro ) | GMP-BR- HO | Building | Ceiling (BU) | Schlager Construction Group | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-19 14:00:00 | Fail | Attended site and carried out inspection to roof area safety harness required due to height and pitch of roof.Replaced several broken tiles and repointed ridge capping.
MSA-DCS | WA3514182 | Main Kitchen tap is faulty, has become loose from the sink. | Walcott Centre (Central West Metro ) | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:30:00 | Pass | Complete
MSA-DCS | WA3514200 | Bakery One blade to the bun rounder has snapped requires tig welding | Casuarina Prison | WSM-MW-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 12:35:37 | 2020-08-17 13:43:00 | Fail | 17/08/20Called as requested to BDR blade broken. Welded the old blade back in position tested oiled freed up all ok.
MSA-DCS | WA3514205 | Unit 9 A and B wing pipe in ceiling leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 12:38:12 | 2020-08-12 10:30:00 | Fail | Located burst pipe under concrete, cut up concrete dug up pipe locating burst pipe can not repair until after 6pm as mains water needs to be turned off
MSA-DCS | WA3514215 | Meduim prison - perimeter zone B1 in constant alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 15:30:00 | Pass | BI microphonics fence contants alarming, trace fault and fixed. Job completed.
MSA-DCS | WA3514222 | Medium prison, gate control - PA system not working | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-10-30 15:00:00 | Fail | Prefabricate brackets in WS.Replace all speakers and containment on oval PA tower as per attached photos.
MSA-DCS | WA3514241 | Bakey Rotel Oven has steam jets stuck on. | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 12:55:21 | 2020-08-10 14:30:00 | Pass | 10/08/20Called as requested to the oven top two decks not operating correctly. Found neutral wire out due rodent infestation made good tested ok. Pest control are required.
MSA-DCS | WA3514245 | Bakery Large Hobart Mixer mechanism to raise and lower the bowl has ceased. | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 13:00:43 | 2020-08-10 14:30:00 | Pass | 10/08/2020Called as requested to the oven top two decks not operating correctly. Found neutral wire out due rodent infestation made good tested ok. Pest control are required.
MSA-DCS | WA3514251 | Staff room, hallway rear - smoke detector is broken (water damage from leak) | Banksia Hill Detention Centre | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-09-04 12:03:00 | Fail | 10/8/20 JNConventional tyco smoke detector in staff amenities hall area damaged due to water leak. Bypassed detector until leak fixed, maintenance toadvise when repaired. 1x tyco conventional smoke detector and base required on revisit4/9/20 KSAttended site and fitted new smoke detector and base and left normal.
MSA-DCS | WA3514287 | Level 4, New zip water tap - has ‘zapped’ (electrocuted) a staff member a few times. | East Perth | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 13:32:14 | 2020-08-11 11:45:00 | Pass | Tested boil/chill tap and unit and all tested ok. Suspect shock reported was static discharge from victim to tap .
MSA-DCS | WA3514290 | Kitchen - hot box not heating properly | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 12:45:00 | Pass | Replaced Element foil pads.
MSA-DCS | WA3514301 | Unit 5, A & C Wing door locking mechanism moves inside the door frame. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 13:36:36 | 2020-08-10 17:30:00 | Pass | Remove edge capping, remove lock, repair/weld/rebuild lock in workshop, reinstall repaired lock and edge capping with new fixings
MSA-DCS | WA3514341 | Bakery Coving either side of the door in the cool room is required. (Missing) | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-09-01 10:00:00 | Fail | COVING FITTED
MSA-DCS | WA3514389 | stores portable electrical equipment with power supply issues | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 10 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-10 11:30:00 | Pass | Replaced faulty plugs
MSA-DCS | WA3514410 | Gate house, key control room - unable to open key watcher (door has been taken off to access keys) | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-09-04 00:06:00 | Fail | Replaced powerboard, power to lock restored, lock intermittently firing, replaced lock.Keywatcher system operational
MSA-DCS | WA3514414 | Health Administration Blocked drain, appears to have sewege coming out and flooding the room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 10 Aug 2020 | 2020-08-10 18:27:17 | 2020-08-10 17:00:00 | Pass | nil
MSA-DCS | WA3514524 | Unit 1 C7 blocked toilet | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 15:27:06 | 2020-08-11 15:55:00 | Fail | Faulty macerator. Pits full. Mario ad.
MSA-DCS | WA3514539 | Main front gate- Key watch system is not functioning | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 10 Aug 2020 | 2020-08-10 19:36:11 | 2020-08-14 13:00:00 | Fail | Slave board in KW-3 identified as faulty, causing communication loss to two other cabinets attacked to KW-3 console. Replacement card was arranged to be sent from supplier and replaced in arrival in WA. Keys were programmed for this cabinet and functionality tested and confirmed correct.
MSA-DCS | WA3514566 | gate house cameras zone 14 camera 2 zone 15 camera 1-SEME on site | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 15:58:22 | 2020-09-15 11:30:00 | Fail | Replaced Cameras and housing.programmed on Indigo and tested recordings.both cameras upgraded to IP and integrated into Indigo
MSA-DFES | WA3513999 | ground gym water leak through ceiling next to skylight opp glass doors-see notes | CFRS Canning Vale | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-21 14:45:00 | Fail | Have attended site and applied silicone to screws and rivets suspected to be the cause of the leak. Heavy weather is expected early next week which will test repair. Will contact site on Monday to see if the leak has been resolved 21/8/20 Leak resolved. Returned to site to patch and paint water damage to the ceiling
MSA-DFES | WA3514541 | Gym- roof and wall leak (external downpipe not attached) | CFRS Daglish | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:15:00 | Pass | GYM roof leak found splits in silicone, seal along fire wall on roof, cleaned and resealed
MSA-DFES | WA3514543 | Main Building hallway- roof leak inside entrance way | CFRS Daglish | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:45:00 | Pass | Accessed main building roof leak, found roof access ladder, roof was not under sealed, cleaned and sealed.
MSA-DFES | WA3514603 | office area The decorative vinyl has come away from a wall panel in the hall admin area | Fleet Management Services - O'Connor Workshop | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-09-07 15:30:00 | Fail | Vinyl panel has shrunk after coming away from panel. Have used contact adhesive and pins to try and stop it shrinking back. Chip board panel is in OK condition24/8/20 -Have been to site and removed the damaged panel for repair and replaced it with a temporary infill boardWorks completed -
MSA-DTAG | WA3513879 | Water dripping in LINKS office from first light, next to door of office. Red bucket on desk collecti | Perth Children's Court | GMP-BR-HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 17:00:00 | 2020-10-08 11:50:00 | Fail | repairs to roof in various locations to eliminate leaking
MSA-DTAG | WA3513939 | Various lighting out please see notes for locations- | Rockingham Justice Complex | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 10:00:00 | Pass | Inspected and replaced faulty lamps and failed fittings to courts rooms 1- 3 and multiple rooms throughout court
MSA-DTAG | WA3514007 | unable to log into unison and open doors remotely from our control room at DMJC and SAT. | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 0 | CLOSE | 10 Aug 2020 | 2020-08-10 14:54:41 | 2020-08-11 08:00:00 | Fail | Work performed by Ken Moore & Michael Tomlinson (10/08/2020 & 11/08/2020):Attended site. SAT Pacom Server offline and unable to read SQL database. Attempted to run on DMJC Pacom virtual butdue to current !SCSI failure in machine unable to accommodate. Decision made by Mark field to shut down Intercomservers onsite to free up resourcing in the SAN unit and attempt to restart Pacom Server. Server up and running again.Began re-sync of SQL database with unison software and field controllers. Once initialisation of controllers and downloadwas complete - Job closed, Works are being completed under WA3591334.
MSA-DTAG | WA3514043 | Ground - Disabled toilet blocked (opposite Caffisimo) | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 12:15:00 | Pass | Complete
MSA-DTAG | WA3514044 | Ground – opposite Caffisimo, Female toilet seat broken | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 13:15:00 | Pass | Complete
MSA-DTAG | WA3514583 | L4 room 4.13 The room is quiet warm. | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-09-04 14:00:00 | Fail | Attend site. Check temps and make another slight adjustment. Temps now look ok.
MSA-DTAG | WA3514590 | basement mens change room A broken toilet lid. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 10:00:00 | Pass | Complete
MSA-DTAG | WA3514594 | registry ground Front Door wont shut | Mandurah Courthouse | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-11 09:51:00 | Pass | On inspection, found ext sensor with an intermittent fault causing door to to self actuate.Replaced faulty sensor as required, tested and adjusted, all ok.
MSA-DTWD | WA3513600 | Block 10, Room 10G76- Faulty fluros | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-12-23 12:27:00 | Fail | invoice costs to date
MSA-DTWD | WA3513714 | A 301 - broken window, frame intact | Leederville Campus | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 16:00:00 | Pass | ATTENDED SITE, REGLAZED BROKEN GLASS TO WINDOW 5.38 CLEAR LAMINATED SAFETY GLASS 1 - 417 X 660 SILICONE USED
MSA-DTWD | WA3513770 | I Block, Transformer Room- No light in transformer room | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 14:00:00 | Pass | Repalced faulty fuse to lights/power. Repalced faulty fluro lamps. Job completed
MSA-DTWD | WA3513775 | L1 to 7 Lifts 5 & 6 Not working | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMPFIN | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-10 12:15:00 | Pass | Power issues Will chase up ups to be installed so parameters are not lostTo be closed out at $0
MSA-DTWD | WA3513777 | U Block, Room U022.3- 2x small water leaks | Balga Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 10:00:00 | Pass | Leaks around redundant penetrationResealed flashingEVAP PenetrationDektitesfixed vent system
MSA-DTWD | WA3513823 | D block nursing lab D7 aluminium sliding door will not slide or lock | Murdoch Campus | GMP-BR | Building | Automatic Doors (BU) | AWB Co. | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-18 14:00:00 | Fail | as per CSS + BRAF
MSA-DTWD | WA3513882 | Childcare Facility, room T3- Reverse cycle A/C not heating | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-14 13:00:00 | Fail | Arrived on site signed in checked in with Phil. Assisted by Dave removed covers and cleaned. Cleans all coils reassembled and tested all ok. Cleaned up and completed paperwork.
MSA-DTWD | WA3513917 | G level outside- Remove graffiti around outside of building | Perth Campus B1 | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-11 10:30:00 | Pass | REMOVAL OF GRAFFITI FROM OUTSIDE OF BUILDING
MSA-DTWD | WA3513978 | Classroom B7- Roof leak over lecturers desk | Rockingham Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-20 09:00:00 | Fail | Currently rescheduled to attend 20/8/20 - subject to weather
MSA-DTWD | WA3513983 | Room F47 back corner near heater- Faulty 4’ batten light fitting, replace with LED | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 13:45:00 | Pass | Attended site and signed in. Located faulty light fittings and asked teacher if we could replace them. Isolated power and replaced light fittings with new LED battens. Tested all ok. Completed paperwork and signed out. Job complete
MSA-DTWD | WA3513988 | Lvl 5 - Rectify door latch in store room E520 | Perth Campus B1 | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-10 14:45:00 | Pass | Liam Hanlon (10/08/2020) - Work NoteAttend site Get shown storeroom Door Get keys and tools Remove top hinge from door and dowel holes fit Phillip head hinge screws Adjust middle and top hinge to lift door latch up Refit striker plate with Phillip head screwsTest door is closing and latching correctly Clean up Return keys
MSA-DTWD | WA3514038 | E block, ET14 - Toilet flush button in Female Toilets - 1st cubicle broken. | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-13 14:04:00 | Pass | Installed new dual flush toilet cistern
MSA-DTWD | WA3514057 | External- Security lighting constantly on (suspect faulty PE cell) | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 12:30:00 | Pass | Repalced faulty pe cell to K block. Tested all working properly job completed
MSA-DTWD | WA3514076 | Block 1, 1st Floor, Room 1F11- Water leak | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-11-26 13:45:00 | Fail | Replace tech screws to roof from ridge to eave line and Install access panel in ceiling.
MSA-DTWD | WA3514088 | tower building whole site boiler has tripped-see notes | West One Services | GMP-BR | Mechanical Services | Boilers (MS) | Precise Air Group | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 10:00:00 | Pass | Attended site, investigated for fault, tested and cleaned components, re-secured mating plugs, test fired gas burner, left working ok.
MSA-DTWD | WA3514093 | A Block, 2nd Floor, Room A237 has a faulty light switch | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 07:00:00 | Pass | Replaced light switch which tafe lecturers have had issues with not working properly.
MSA-DTWD | WA3514144 | L Block, External and L014.3 (Shower)- Leaking taps and blocked stormwater | Balga Campus | GMP-BR | Plumbing & Drainage | Water (PD) | ECO PLUMBING AND GAS PTY LTD | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 16:30:00 | Pass | Serviced and repaired taps
MSA-DTWD | WA3514202 | D block - Main front sliding door is faulty, not operating on Automatic, it just stays open | Murdoch Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 10 Aug 2020 | 2020-08-11 17:00:00 | 2020-08-10 15:30:00 | Pass | Unable to find fault with door. Checked all sensors and reduced sensitivity on internal motion. Cleaned pes. Replaced backup battery that was three years old. All ok.
MSA-DTWD | WA3514402 | Lvl 3 Mezzanine at top of main staircase- no lights on (CUBS issue) | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-09-16 13:15:00 | Fail | Arrived on site. Replaced the 11 light fittings on level 3 mezzanine that was discussed. All working.
MSA-DTWD | WA3514404 | P Block, P008 (tea prep) - Water leak from roof | Balga Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-11 12:00:00 | Pass | Ceiling damage - cleaned roof laps above area and sealed fixing points to anchor system
MSA-DTWD | WA3514428 | North Block, N227- Roof leak above desk | Mount Lawley Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2021-06-28 09:15:00 | Fail | lift sheets and flashings to locate water ingress, lift edge of overlap and wait for rains. Re do along roof as required.
MSA-DTWD | WA3514450 | L1 passage S200 Leak in passage outside S200 | Mount Lawley Campus | GMP-BR | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2021-06-28 15:15:00 | Fail | box gutter repaired and new downpipe installed
MSA-DTWD | WA3514471 | A Block, Room A113- Tap female toilet student services hard to turn off | East Perth Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 12:58:00 | Pass | COMPLETED
MSA-DTWD | WA3514497 | Block 7, 1st Floor- Student common room- Water leak | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-11 11:03:00 | Pass | Leak reported by site to have been resolved
MSA-DTWD | WA3514508 | block 3 ground 3B36 Automotive Workshop Evacuation P/A speaker broken. | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 10 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-19 09:30:00 | Fail | Arrived on site , signed in, got keys from John , located where speaker needing replacing , set up work area , removed old cable and bracket from the wall , drilled new holes for the bracket, mounted bracket , mounted speaker to bracket , connected new cable , tested speaker , all working , cleaned up work area , *** job completed ***
MSA-DTWD | WA3514604 | E block E601 : We have water leaking down a hanging power point | Midland Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 10 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 13:15:00 | Pass | Found multiple penetrations over area with perished silicone. cleaned dried and resealed all penetrations
MSA-DCA | WA3520767 | Blocked toilet | PICA-Main Building-Ground Floor-Dressing Room Bathroom | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 10:35:00 | Pass | Unblocked badly blocked tpilet
MSA-DCA | WA3520771 | blocked urinal | State Library of WA-Main Building-Level 3-Male Toilets - West | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 16:53:00 | Pass | Unblocked urinal
MSA-DCA | WA3520919 | Main building entrance - reposition of external lighting | Perth Cultural Centre Precinct | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 14:00:00 | Pass | Adjusted the flood lights as Reece requested.
MSA-DCS | WA3520270 | Pole 2A - light not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 11 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-26 10:00:00 | Fail | Tested pole lights
MSA-DCS | WA3520392 | Kitchen, Entrance Double Doors- Lock jamming when opening | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 11:45:00 | Pass | Supplied and installed blocker plates to ensure normal function
MSA-DCS | WA3520396 | Medical Centre, passage way double doors- Lock jamming when opening | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 10:30:00 | Pass | Supplied and installed blocker plates to ensure normal function
MSA-DCS | WA3520399 | Social Visits, External yard double doors - Lock jamming when opening | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 13:45:00 | Pass | On site 12/08/2020 - parts required to complete repairs.On site 14/08/2020 - Supplied and installed blocker plates to ensure normal function.
MSA-DCS | WA3520516 | Unit 2A- Shower block 1- windows are broken | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-18 12:30:00 | Fail | windows reglazed
MSA-DCS | WA3520517 | Unit 2B- Last toilet block -2 x windows are broken | Wooroloo Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-18 15:30:00 | Fail | windows reglazed
MSA-DCS | WA3520545 | SOG base kitchen - hot water urn, tap is broken off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 15:07:00 | Pass | Broken tap replaced. All working ok.
MSA-DCS | WA3520597 | Education Office Outside ( door facing Gascoyne) door lock catching | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-11 11:15:00 | Pass | Repaired door closer, replaced lock strike and realigned doors
MSA-DCS | WA3520629 | Kitchen- bug zapper not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-20 13:00:00 | Fail | Replaced bug zapper
MSA-DCS | WA3520640 | Unit 1, A4 - Blocked toilet | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 10:29:21 | 2020-08-11 12:15:00 | Pass | Plunged main drain in both plumbing ducts, all clear now
MSA-DCS | WA3520643 | Turner, C lounge room- Smashed window approx 450x300 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-13 13:30:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3520650 | Turner, C Wing, Roof Leaking between C02 & C04 | Banksia Hill Detention Centre | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-09-04 14:04:00 | Fail | REPAIR ROOF AND FLASHING AND AIR BLOWER
MSA-DCS | WA3520658 | Unit 3, Control room - air conditioner has broken down again | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-11 15:30:00 | Pass | Set remote to correct code. All ok.
MSA-DCS | WA3520663 | Sally port, outer roller door (closest to RAM barrier)- Roller door hass a split approx 200mm long | Banksia Hill Detention Centre | SPA-BR | Building | Automatic Doors (BU) | AFD Contracting | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-10-20 14:00:00 | Fail | 14/08/20Inspect roller door and measure up.BRAF to be submitted.Waiting on quote from supplier.20/10/20Replace with industrial roller shutter (shutter similar to other sallyport doors)
MSA-DCS | WA3520678 | ablutions at rear of Demountable 6 - Sewer Pipes - Water leaking from sewer pipes | Nyandi Training Academy | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-11 14:30:00 | Pass | nil
MSA-DCS | WA3520702 | Medical Centre, Outpatients Area- Water Fountain is leaking | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-25 12:59:00 | Fail | Restarted work at 9.00am 25/08/2020Replaced fault bubbler on fountain. Added new capex asset filtration system A40184999X to unit as approved. Completed work at 9.50am 25/08/2020
MSA-DCS | WA3520734 | Unit 3 Officer toilet is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-11 14:25:00 | Pass | Plunged toilet to clear blockage.
MSA-DCS | WA3520759 | Lightings around internal ring road not working | Nyandi Training Academy | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 16:00:00 | Pass | Repaired lighting around internal roadway.
MSA-DCS | WA3520764 | Perimeter camera 18 Not functional | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 11:40:58 | 2020-08-11 16:00:00 | Pass | Issue with communications between camera and DVM. Repaired network connections. Tested ok live. Recording ok.
MSA-DCS | WA3520872 | uint 4 PRU zone 8 in constrant alarm, 2+9.1 pou fence has change to open | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 12:30:16 | 2020-08-12 13:00:00 | Fail | Replaced cable ties on the upper and lower parts of the fence. Calibrated and tested ok. Parts used:Cable ties
MSA-DCS | WA3520931 | Recovery West Room- MKH Lock on the door faulty | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 13:00:00 | Pass | Replaced lock cylinder to restore normal function
MSA-DCS | WA3520946 | Unit 1, B3 - main lock faulty, cant be opened | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 13:08:23 | 2020-08-11 16:30:00 | Pass | Repaired and serviced lock to restore proper function.
MSA-DCS | WA3520950 | Unit 1, D12 safe cell - Main Lock Faulty, has become non- operational. | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 13:10:35 | 2020-08-11 16:00:00 | Pass | Door and lock had been painted over. Repaired lock and removed paint from lock bolt to restore proper function.
MSA-DCS | WA3520952 | Gym, Male Changeroom- Vanity is water damaged | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2021-06-14 13:54:00 | Fail | ADVISED TO CLOSE OFF JOB COST TO DATE. JOB TO BE RE ISSUED IN FUTURE, POSSBILE LVM
MSA-DCS | WA3520960 | Gym, Female Changeroom- Wall tiles seperating from wall | Casuarina Prison | SPA-BR | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-12-08 10:30:00 | Fail | GYM - BENCH REMOVED, NEW TILES INSTALLED, BENCH REPLACED EXOTEC PANELS INSTALLED
MSA-DCS | WA3520961 | Turner, B wing - smashed window approx 1200x500 | Banksia Hill Detention Centre | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-13 12:00:00 | Pass | WINDOW RE GLAZED
MSA-DCS | WA3520968 | Gym- Floor has possible water and/or termite damage | Casuarina Prison | GMP-BR- HO | Flooring | Timber (FL) | Midolo Building Services | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2021-01-05 13:07:00 | Fail | advised to close off job cost to date - termites still evidence - once eradicated job will be re-issued
MSA-DCS | WA3521070 | Gate house - camera PTZ 3 is not clear, all fuzzy | Karnet Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-09-17 12:30:00 | Fail | Replaced an programmed PTZ 3
MSA-DCS | WA3521073 | Gate house - EC2 network switch fault | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-11 19:04:00 | Pass | Ruggedcom RS900G port 10 has failed in EC 2.swapped patch leads with known working set, no connection.Installed 1x Planet IGS-624HPT - from Seme stock2x Planet SFP MGB-TSX - from Seme Stock1x 24vdc Sinpro power supply - from Seme stockprogrammed and tested network.confirmed connection with EC 1 switch and EC 3 switch.
MSA-DCS | WA3521077 | Gate house - EC4 network switch fault | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-27 13:13:00 | Fail | Sourced Planet IGS-100200MT, 2x Planet MGB-SX and 2x DM1-LCST1M-3OR from seme stockProgrammed network switch in Comms room and installed into EC5.fibre connection with EC3 and EC5
MSA-DCS | WA3521080 | Gate house - EC5 network switch fault | Karnet Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-27 13:12:00 | Fail | Sourced Planet IGS-100200MT, 2x Planet MGB-SX and 2x DM1-LCST1M-3OR from seme stockProgrammed network switch in Comms room and installed into EC5.fibre connection with EC4 and EC6.
MSA-DCS | WA3521119 | Recovery Office (rear door)- Unable to lock door as lock isfaulty | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 13:30:00 | Pass | Replaced faulty lock.
MSA-DCS | WA3521206 | female toilets 2x taps continue to drip even after tap is turned of tight | Walcott Centre (Central West Metro ) | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 16:00:00 | Pass | Complete
MSA-DCS | WA3521217 | Sewer line/macerator is blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 11 Aug 2020 | 2020-08-11 19:36:21 | 2020-08-11 19:10:00 | Pass | Collected van with confined space equipment. Attended site drained pit manually switching on. Macerator jammed and unable to reverse to unjam. Accessed pit, removed access panel and cleared fabric blockage. Blockage looked like 2 shirts tied in a knot. Tested macerator and reinstalled covers. Opened valves and tested pumps. Tank at 50% full and still draining when all lids replaced and job completed.
MSA-DCS | WA3521238 | DDU office gate to the office area lock sticking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 15:53:43 | 2020-08-12 10:00:00 | Pass | Repaired gate lock to restore proper function.
MSA-DCS | WA3521247 | A wing blocked toilets | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 16:05:30 | 2020-08-12 10:59:00 | Pass | Attended site, Used drain machine to clear tree roots from drains to unit 1, A wing.Tested works on completion
MSA-DFES | WA3520393 | Level 1, toilet in the middle (2nd) FF dorm ensuite - leaking toilet tap & float mechanism for water | CFRS Midland | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 14:49:00 | Pass | Servicing toilet cistern.
MSA-DFES | WA3520422 | main building, ground, Watch Room - security UPS is not functioning. | CFRS Midland | GMP-BR | Security | CCTV Surveillance (SE) | Securex Security Systems & Services | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-11 10:45:00 | Pass | (11/08/2020) - Work NoteReplaced ups battery
MSA-DFES | WA3520792 | Skylight Perspex in the Gym Courtyard was blown down during storm and smashed on the ground | CFRS Kiara | GMP-BR | Roofing | Rooflights and Skylights (RF) | AWB Co. | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-26 08:05:00 | Fail | Found diffuser for skylight removed by storm, measured for replacement.Fitted new diffuser and secured with silicone, added silicone to other diffusers to combat wind
MSA-DFES | WA3520809 | Admin ground Appliance Garage/Change Room 2/3 light issues-see notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 12:45:00 | Pass | COMPLETED
MSA-DFES | WA3520995 | Ground floor, Mens Toilets (Near Stores Area) - The toilet seat in the toilet closest to the wall is | Fleet Management Services - O'Connor Workshop | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-12 12:46:00 | Pass | Replaced toilet seat
MSA-DFES | WA3521034 | Front Yard- Letter box has broken off the post. | DFES Baldivis | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-20 11:30:00 | Fail | Carried out repairs to refurbish broken letterbox, repainted and re-erected on site
MSA-DFES | WA3521036 | L1 ICT kitchen key broken and stuck in paper wipes dispenser-see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 09:00:00 | Pass | remove broken key from paper wipe dispenser and replace key
MSA-DFES | WA3521038 | Ground - Security system is not working properly. Key pad next to southern door is very difficult to | DFES Baldivis | GMP-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-18 08:30:00 | Fail | Replaced keypad. Tested OK
MSA-DFES | WA3521194 | rear left door broken a spring and does not go up | Kensington (old) | GMP-BR | Building | Fire Door (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 17:00:00 | 2020-09-15 12:15:00 | Fail | Technician attended the site of Kensington Fire Station to the engine room door no. 4 on 11/08/2020. Following a full test and inspection of door components found fault to be door wasn't opening, upon further inspection found door had a broken spring, detailed for repairs. 17/08/2020 Returned on site to carry out repair work to sectional door as per quotation, removed broken springs,supplied and installed new springs & tested operation, found wrong springs supplied, required to return to site with correct springs. Door not operational & left in down position.10/09/2020 Returned on site and found that door was closed, cables off no tension, top panel bent. Retention springs and put cables back on to open door. Left door in open position as requested by site. Made safe and left tagged out and isolated. Quote to follow. More damage to door than in previous quote. Noted wrong size cable drums for springs fitted.15/09/2020 Technician returned on site and completed quoted works. F
MSA-DTAG | WA3520405 | level 2, Sheriffs office - Sheriff’s Office Lift is out of order | Supreme Court | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 11 Aug 2020 | 2020-08-11 12:11:12 | 2021-08-11 12:45:00 | Fail | Equipment fault, covered under contract- no charge therefore no invoice, Please close workorder
MSA-DTAG | WA3520490 | Ground, registry - Q ticket machine base plate fixings are loose | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-14 08:00:00 | Pass | BASE PLATE RE SECURED
MSA-DTAG | WA3520514 | L4 Female staff toilet door not closing properly – door closer seized | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 10:30:00 | Pass | DOOR CLOSER ADJUSTMENT MADE
MSA-DTAG | WA3520677 | Registry - 1x Single fluro light has blown | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 08:30:00 | Pass | Replaced faulty light fitting due to age
MSA-DTAG | WA3521269 | lift is not working someone stuck inside | Rockingham Justice Complex-Main Building-Ground Floor | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 0 | CLOSE | 11 Aug 2020 | 2020-08-11 21:44:13 | 2021-10-31 15:00:00 | Fail | Job completed
MSA-DTWD | WA3520338 | Workshop - few roof leaks, spray booth C001 & F001 - just above the welding bay | Naval Base | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Aug 2020 | 2020-08-13 17:00:00 | 2020-09-09 10:30:00 | Fail | 9/9/20 - Works started yesterday, will be completed this morning
MSA-DTWD | WA3520407 | T Block, Room T011 - Blown LED bulb over sink area left corner of room | Joondalup McLarty Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-13 07:30:00 | Pass | Attended site and inspected light, found light to be faulty. Sourced replacement and returned and replaced light
MSA-DTWD | WA3520431 | T Block, Room T105 - Door lock not locking | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 11:30:00 | Pass | Replace internal and external handles to T105
MSA-DTWD | WA3520434 | G/Floor - inter leading door not locking | Joondalup McLarty Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 09:30:00 | Pass | repairs to lock
MSA-DTWD | WA3520439 | S Block, Room S100- Female toilet tap is broken | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 12:30:00 | Pass | Complete
MSA-DTWD | WA3520453 | G block, Administration - SW corner entry door, digital key pad cover faulty; | Rockingham Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-24 12:30:00 | Fail | Investigated faulty keypad door lock - arranged for faulty keypad to be replaced with new. Job complete.
MSA-DTWD | WA3520479 | E Block, Male toilets - 1st cubicles blocked. | Midland Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 14:40:00 | Pass | Cleared blockage using plunger and adjusted outlet valves
MSA-DTWD | WA3520531 | Q block L1 board room kitchen the zip urn is not heating | Joondalup McLarty Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-27 12:07:00 | Fail | Timer had a low battery fault. Replaced. No power coming out from timer, even though the symbol was on for heating. Timer requires replacing, ordered. Also noted tap on the urn is dripping and requires replacing. 27/08/20Replaced Timer and tap. Unable to log on ProMAP (internal server error) completed manual ‘Take Five’ form. 10.50 to 12.00
MSA-DTWD | WA3520549 | L3, water leak in B314 still there, another has appeared | Perth Campus B6 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 15:15:00 | Pass | Roof leaks L3 B314 found rust holes to stop end of gutter, sealed all
MSA-DTWD | WA3520569 | L2 A260 roof leaking | Perth Campus B5 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 14:15:00 | Pass | Roof leak L2 A260 found support for all deck had perished seals, cleaned and resealed
MSA-DTWD | WA3520619 | Q block Q009 roof leak | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-11 15:00:00 | Pass | Large fix - vent system leaking. Re-sealed around vent lifted sheet and undersealed skylights, rejointed surrounding flashings
MSA-DTWD | WA3520671 | Dempster Hall BLD 822, Flat C, Hallway- Leaking Roof | Muresk Institute | GMP-BR | Roofing | Metal Roofing (RF) | Lee Carpentry | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 11:00:00 | Pass | Replaced tiles
MSA-DTWD | WA3520703 | Basketball Court - Replace/repair shed entry door lock that has been forced | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 0 | CLOSE | 11 Aug 2020 | 2020-08-11 14:54:06 | 2020-08-11 12:30:00 | Pass | job completed, deadbolted hatch
MSA-DTWD | WA3520704 | E block ground deli the dishwasher has stopped working | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 15:55:00 | Pass | Completed 12/8
MSA-DTWD | WA3520748 | C Block, CG01- Cornice from upper ceiling has fallen through lower ceiling tiles. | Carlisle Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-09-11 16:00:00 | Fail | - Saw tooth roof leaking above CG01 and CG02. Roof access needed but raining on first visit. - Removed flashing and sealed area suspected as causing the leak - Waiting on rain to confirm leak resolved - Site confirmed leak was resolved - Water stains on ceiling tiles and one 600 x 600 tile missing.- Currently rescheduled for 19/8/20 - 11/9/20- Leak resolved and 5 x water damaged ceiling tiles replaced with new
MSA-DTWD | WA3520769 | B block L1 B107 blocked toilet ground floor | East Perth Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-12 09:30:00 | Pass | Complete
MSA-DTWD | WA3520869 | B Block, TIWA B208 Photocopy room- Light Tube is out | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 11 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 09:15:00 | Pass | Arrived on site , signed in, completed jsa, located lights (not in b208 photocopy room all lights are operational ,the problem was in b209 after asking staff about the photocopy rooms )removed globes , replaced globes , all working now and operational , job complete
MSA-DTWD | WA3520879 | toiltes ground Student female toilet blocked | Armadale Campus - 40 Commerce Ave | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-11 15:33:00 | Pass | Unblock toilet
MSA-DTWD | WA3521014 | D block L1 server room GSM SIM card to D Block has failed to communicate | East Perth Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 11:30:00 | Pass | 11/08/2020, 1545-1600Tested sim and unit with butt phone ok. Reset gsm unit and tested comms confirmed all signals received12/08/2020, 1115-1130System B is actually the one effected, Edsec told me wrong system yesterday. Reset gsm unit and tested with buttphone and tested comms confirmed all signals received.System A no: 0405209469System B no: 0405221710
MSA-DTWD | WA3521226 | ground 19Ab carpark relief pipe overflowing some sewage | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 11 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-12 15:13:00 | Pass | Unblocked sewer install new grates
MSA-MRWA | WA3520512 | External LED Light as entering the East Reception door LHS is not working please remediate | Don Aitken Centre MRWA Head Office-Main Building-Ground Floor-Reception Area | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 11 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-20 09:00:00 | Fail | Arrived on site, signed in, completed jsa, painted light black to suit others on site , located light , isolated lighting, removed old light, re fitted new light , re energised circuit *** job completed ***
MSA-DCA | WA3527117 | 2 large pieces of graffiti need to be moved | His Majesty's Theatre-Theatre Building-Ground Floor-Stage Door Entrance Area | GMP-BR | Cleaning | Graffiti (CL) | FCT SURFACE CLEANING | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-13 10:00:00 | Pass | removal of Graffiti
MSA-DCA | WA3527121 | flexi hose on toilet broken and to be replaced-toilet isolated | King Street Arts Centre-Main Building-Level 1-Female Toilets - Back of Stair Foyer | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Techworks Plumbing | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 12:30:00 | Pass | Replaced flexi hose in cistern.
MSA-DCA | WA3527154 | Kitchen tap is very stiff and hard to turn on and off | Short Street Theatre-Main Building-Level 1-Kitchen | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 12:10:00 | Pass | Replaced kitchen tap mixer
MSA-DCA | WA3527172 | Dripping tap in the male toilets-see notes | Short Street Theatre-Main Building-Ground Floor-Male Toilets | GMP-BR | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 12:52:00 | Pass | Replaced tap washer and valve
MSA-DCA | WA3527413 | BMS controls not responding | Maritime Museum Victoria Quay-Main Building-First Floor-Control Room | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-25 11:30:00 | Fail | Attended site. Issue with chiller 3 control staging and chiller 2 mismatch fault. Engaged Iconlogic to check controls and BMS operation. Applied tests and checks to find chiller 2 condenser water pump CB to have tripped. Reset breaker and checked operation of electrical switching gear (ok). Recorded current of pump/motor (ok). Investigation found chiller 2 fault due to a miss match error of no condenser water flow being picked up during chiller start. System operating correctly.
MSA-DCA | WA3527457 | public female toilet leaking | State Library of WA-Main Building-Ground Floor | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-13 15:10:00 | Pass | Couldn’t locate leak from toilet check all toilets and basin working fine went and looked at leaking tap in males bathroom advised they will need new tap and order one in
MSA-DCS | WA3526887 | Unit 14, tearoom - Tap loose again (see notes) | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 09:30:00 | Pass | Collected parts offsite. Replaced sink mixer. Mixer was corroded underneath preventing from being fully tightened.
MSA-DCS | WA3526889 | kitchen cctv wont reboot no cameras showing | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 08:03:56 | 2020-08-12 13:53:00 | Pass | Camera system online
MSA-DCS | WA3526890 | SOG POD, Perimeter fence - zones F01 & F02 IDF wont reset. Inner defence FO1 & FO 3 faulty | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 08:04:11 | 2020-08-12 13:56:00 | Pass | Contractors working along side inner perimeter.F01 secured while contractors were working on F2 and F3.Officers advised system was stable when contractors are off-site
MSA-DCS | WA3526892 | Unit 5 - MDAS system, Low battery tamper Unit 6 | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-09-14 10:45:00 | Fail | Attended site and repconfigured programming to suit new Transponder. Reprogrammed and retested. All alarms cleared and tested ok. Job complete
MSA-DCS | WA3526895 | Vegi Prep area Power was tripped - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-09-04 15:00:00 | Fail | Replaced damaged 3phase outlet, 2 circuit breakers, 1x shunt trip contactor. Removed rodent remains and cleaned switch board chassis
MSA-DCS | WA3526898 | POD, Fire control panel - wing JANA wing D3 cell - L5s72 z20st maintenance fault sensor fault 1of1 | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-13 16:43:00 | Pass | 13/8/20Checked detector status, all showing normal (analog value 24).Performed loop test and cleared fault.Left system in normal working order.
MSA-DCS | WA3526902 | Canteen roller door - alarm fault | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-09-11 10:00:00 | Fail | Attended site and replaced canteen reed switches with 2 x new heavy duty reed switches. All replaced and tested ok. Job complete
MSA-DCS | WA3526972 | unit 10 control room dead rat smell | Hakea Prison | WSM-BR-SITE | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 08:56:23 | 2020-08-12 10:45:00 | Pass | Carried out a service to Hakea prison, unit 10. There was an odour coming from the control room which was caused by a deceased rat which has very likely fed on some of our rodenticide. Searched the entire area, pulling out boxes and other items to try and locate the carcass. Determined that the carcass had deceased in the sealed roof void which was inaccessible. Installed 2x odour bags to the control room. Please allow 24 hours for the bags to activate in order to eliminate the odour.
MSA-DCS | WA3527089 | unit 10 D/D entry door Entry door will not open remotely only with a key | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Aug 2020 | 2020-08-12 13:03:03 | 2020-08-12 11:51:00 | Pass | Removed lock, found brake in cable. Repaired cable and tested door.Door fully operational
MSA-DCS | WA3527114 | Prisoners clothing store - a electrical burning smell from hot water system please investigate | Boronia Pre-release-AJ14 - Health and Education Centre-Ground Floor-Store Room - End of Corridor - Health | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 15:15:00 | Pass | Replaced faulty element in hws
MSA-DCS | WA3527196 | Control room /Staff room Hot water tap will not turn off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 10:33:22 | 2020-08-12 12:23:00 | Pass | Turned off main water replaced quarter turn hot tap only turned water back on
MSA-DCS | WA3527260 | Unit 13, cell B15 - the shower is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-13 16:00:00 | Pass | Used acid and plunger to clear blockage in shower drain
MSA-DCS | WA3527283 | Unit 13, B02 - sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-13 15:00:00 | Pass | Plunged basin to clear blockage.
MSA-DCS | WA3527287 | Unit 13, D08 - shower pressure is down | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-13 14:00:00 | Pass | Adjusted water pressure and cleaned shower head.
MSA-DCS | WA3527288 | CCU (11) - D Wing D6 Cell floods whenever shower is used CCU | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 15:00:00 | Pass | Cleaned shower head. Plunged shower drain. Installed control valve in shower outlet.
MSA-DCS | WA3527294 | Unit 13 B01 - Little pressure in tap, Pressure needs increasing. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-13 13:00:00 | Pass | Adjusted water pressure and cleaned shower head.
MSA-DCS | WA3527385 | permitrax intermitently alarming on zone 12 PX | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 12:10:13 | 2020-08-12 17:04:00 | Pass | Investigated and found fault with Sennet Module on perimeter. Repaired module and performed calibrations on Zone 12 and adjacent zones. Monitored for correct operation and tested ok.Job Complete
MSA-DCS | WA3527392 | Bakery cutting blade has broken on the second bun rounding machine. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | CPB ELECTRICAL SERVICE | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-09-30 15:30:00 | Fail | 30/09/20Called as requested to a blade broken. Welded the blade back in position tested all working correctly now.
MSA-DCS | WA3527450 | CCU, cell H9 - cell call button is stuck on the on positon | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 12 Aug 2020 | 2020-08-12 16:45:53 | 2020-08-13 09:00:00 | Fail | Unable to activate intercom. Removed and found button mount is broken. Replaced with new intercom. Secured and tested. Loud and clear audio in cell and in control. Parts used:Cell Guard intercom CI-CCConsumables
MSA-DCS | WA3527585 | Gym office carpet tiles containing blood spill need attention | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2021-05-18 13:00:00 | Fail | NEW CARPET TILES SUPPLIED & INSTALLED
MSA-DCS | WA3527665 | Unit 3 cell M4 toilet not flushing correctly | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 15:57:21 | 2020-08-13 10:18:00 | Pass | COMPLETED
MSA-DCS | WA3527721 | Significant water leak from pipe in rear of Unit 2. | Casuarina Prison-Prisoner Accommodation Unit 2 | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 12 Aug 2020 | 2020-08-12 23:02:37 | 2020-08-12 21:31:00 | Pass | Attended job. Water has small leak in exposed pit which is currently being repaired under job no wa3496005. Area is taped of and water is not flooding the area.
MSA-DFES | WA3527226 | Main Drive/Heritage Shed & Dome-Self-Seeded Trees to be removed from Main driveway-see notes | FESA RHQ - Forrestfield | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | Dom's Total Grounds Maintenance | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-15 07:30:00 | Pass | D Coniglio, K Skulley & B Coniglio 15/08/20
MSA-DFES | WA3527402 | ground maintenance office lights faulty may need changing | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 16:15:00 | Pass | Replaced faulty tubes with new
MSA-DFES | WA3527424 | Mens Toilets (Near Gym) button is sticky on occasions causing water to overflow | Fleet Management Services - O'Connor Workshop | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-13 10:49:00 | Pass | Repairing toilets
MSA-DFES | WA3527470 | Passageway light is out in hallway and various other places-see notes | DFES Regional Office - Belmont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 14:30:00 | Pass | Referred to Email sent regarding light not working located in hallway. We repaired that light and also did a walk around for any other faulty lights. We found 2 others and repaired accordingly.
MSA-DTAG | WA3526980 | Lower Ground Floor, Family Court Chambers, Chambers 3 next to Court 7 - AC breakdown, no heating | Supreme Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 15:00:00 | Pass | Attend site. Sign in and access lower ground office. Check controller and found to be blank. Use 8ft ladder to access unit in ceiling space. Found unit to have option card installed. Found push button switch on wall that start AC unit. Remove push button from wall and check for power. Found to have no power supply. Locate electrical switchboard and found unit circuit breaker tripped. Carry out inspection of unit wiring. Remove outdoor unit cage and inspect isolator. Found to have moisture in isolator. Dry out isolator and reseal. Reset circuit breaker and found power to be at push button switch. Press push button and test operation of unit. Found unit to start and operate as normal. Moitor operation. Due to ceiling being so high setpoint has to be set to 30 to get the warm air down. Supply air 50 degrees, return air 28. Unit is working as normal.
MSA-DTAG | WA3527276 | Carpark entrance ramp - Light fitting broken | Perth Children's Court | WSM-BR-SITE | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-28 13:45:00 | Fail | Job complete
MSA-DTWD | WA3526877 | Admin - alarm fault, when leaving alarm is set then 2 minutes later is activated | Naval Base | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 12 Aug 2020 | 2020-08-12 17:00:00 | 2020-08-12 12:30:00 | Pass | 12/08/2020Door wasn’t closed properly casing the wind to open it slightly causing false alarms
MSA-DTWD | WA3526909 | A block ground East Auto Door the door adjustment control switch is broken door not opening | Joondalup Kendrew Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 12 Aug 2020 | 2020-08-13 17:00:00 | 2020-08-12 09:41:00 | Pass | Found that the mode switch has come loose and was spinning around, refit and secured switch, tested all ok.
MSA-DTWD | WA3526962 | Glass house - 1 roof panel has blown off and there are several panels loose | Murdoch Campus | GMP-BR | Building | Materials (BU) | ARGOSEE GREENHOUSE TECHNOLOGY PTY LTD | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-28 16:00:00 | Fail | Repairs to roof
MSA-DTWD | WA3526971 | T block, main server room - low battery fault on the Fire curtain controller in the main server room | Murdoch Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Firesafe Service & Maintenance Pty Ltd | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 11:30:00 | Pass | RECEIVED CALL OUTCustomer: Programmed Facilities ManagementSite: South Metro Tafe - MurdochSite contact: Mike Day- 0407 476 354Work Order Number: WA3526971 Priority #: 2Call out Date: 12/08/2020Target finish: 17/08/2020Work order contact: Department of Training and Workforce Development - MSAOriginal information: T block, main server room - low battery fault on the Fire curtain controller in the main server roomAttended siteDate: 12/08/2020Start Time: 1045hrsFinish Time: 1130hrsWorks Carried Out:Attended site and T block curtain in low battery fault. Measured batteries and sitting at 27v. Charger also sitting at 27v. Followed Coopers Fire procedure for resetting the system which includes dropping the curtain and powering down the controller. Fault stayed clear for 10 mins. Kevin said they may have had a power surge a few days ago which could’ve caused the fault.
MSA-DTWD | WA3527224 | Keys required to be cut 55, 56 & 85 - re-cut required as damaged locks. | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 12:15:00 | Pass | Key cut
MSA-DTWD | WA3527373 | K block K02 aulty heating element replaced in LH Bainmarie-see notes | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-12 14:00:00 | Pass | Job completed
MSA-DTWD | WA3527432 | ground workshop Plastering area has a large water leak | Clarkson Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 13:00:00 | Pass | Works completed, pending trade notes and documents to upload
MSA-DTWD | WA3527539 | V008 Male student toilet - leaky taps (easy push button tap) | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 10:45:00 | Pass | Replaced cartridge
MSA-DTWD | WA3527553 | IT office - office too hot - temp is 26.1 | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-20 10:50:00 | Fail | Attended site collected keys and gained access to IT office. Carried out investigation and inspection of FCU equipment due to hot complaints. Chiller water lockout found active due to low load. It was also noted that the economy cycle for the independent equipment was not active preventing cool air from being drawn into area. Economy damper have been manually forced to 100% open as a trial. Temp has dropped in area and keeping to 21°. Please note as there are a large amount of computers in the sealed area the heat load can change rapidly. Unit set points have been confirmed as 21°. As we can not see the economy cycle lock out the campus are going to trial the area by manual open outside air to draw air into the office. It was recommended to involved Alerton controlls. The site BMS contractor to confirm economy cycle and setting and make adjustments for the independent units in IT office. Site facilities have asked to currently hold off on that action. Work area has been left tidy. Can
MSA-DTWD | WA3527578 | K block, laundry - faulty taps | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 09:30:00 | Pass | Replaced old tapware and reseated seats
MSA-DTWD | WA3527614 | E block E201 faulty light | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 13:30:00 | Pass | Attended site and signed in. Located E201. Found flickering light. Investigated and replaced tube and starter. Cleaned diffuser and tested all okay. Job complete
MSA-DTWD | WA3527623 | level 1, Outside S107 - Repair paving outside S107 | Mount Lawley Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-18 13:15:00 | Pass | relayed pavers to S107 - collapsing due to being undermined by ants
MSA-DTWD | WA3527624 | L1 has suddenly dropped | Bentley Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 0 | CLOSE | 12 Aug 2020 | 2020-08-12 18:59:10 | 2020-08-12 17:00:00 | Pass | Lift attended to, and made operational
MSA-DTWD | WA3527628 | F block IT section F55 Cassette A/C not operating | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 16:00:00 | Pass | Assisted by Dave, started fault Check on a/c. No power received, checked breaker all ok Checked timer, checked outdoor unit repaired Hot joint. Checked isolator no power going through reset isolator power restored, monitored found isolator switch faulty purchased new isolator and changed internal mechanism, turned unit back all ok, monitored operation. No new faults reoccurring. Cleaned up Work area. Completed paperwork signed out
MSA-DTWD | WA3527634 | Block 9 L1 boiler room Hot water pump on boiler noisy and vibrating | Thornlie Campus | GMP-BR | Mechanical Services | Boilers (MS) | Equans Mechanical Services Australia | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-10-19 16:30:00 | Fail | HWP2 has been overhauled as per braf
MSA-DTWD | WA3527659 | block 2 Blocked soak well outside main entrance | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-19 10:09:00 | Pass | Fixed stormwater issues
MSA-DTWD | WA3527675 | Block 10 10G74 Worn and loose door hinge screws | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-13 15:30:00 | Pass | Replaced hinge screws with new
MSA-MRWA | WA3527278 | Asphalt Cutting room (behind concrete lab) cutting room inoperative ceiling lights | Materials Engineering Branch | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-13 12:30:00 | Pass | Arrived at site , signed in , completed induction , completed jsa, located lights that weren't working , tested for voltage at the rcd, tested for voltage at the fitting , adjusted sensor , lights back to working order , job completed
MSA-MRWA | WA3527438 | signs yard Automatic gate not opening. Reader acknowledges card-see notes | Materials Engineering Branch | GMP-BR | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 12 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-12 16:15:00 | Pass | 1078235 sign store. Found gate track completely over grown with grass and soil. Gate jammed in closed position as a result. Dug out 7 metres of earth around gate track. Checked condition of track wheels. Lubricated top guides. Tested safety beam. Operation ok.
MSA-MRWA | WA3527619 | front office, mens toilet - End tap is constantly running | Materials Engineering Branch | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-13 10:52:00 | Pass | Replaced corroded, leaking and sezied basin set
MSA-MRWA | WA3527661 | ground Female toilets - hot water is tepid, requiring a service. | Heavy Vehicle Services | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 10:10:00 | Pass | Valves for recirculating syetm on l1 had been turned off and pumped switched off. Turned valves and swithc back on
MSA-MRWA | WA3527668 | ground Middle kitchen – hot water is tepid, requiring a service. | Heavy Vehicle Services | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 12 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 11:30:00 | Pass | Inspected hot water unit in the kitchen cupboard. No faults found. The unit is a 10L storage electric hot water system. Once the hot water in the unit runs out it will take approx 10-12min to heat up again.
MSA-DCS | WA3530417 | Zone 1 C on perimetre is continually activating | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Aug 2020 | 2020-08-13 10:23:29 | 2020-08-13 10:15:00 | Pass | Travelled to site and found zone 1c beam set constantly activating. Located zone in perimeter and found vegetation/shrubs blocking zone. Attended with maintenance officer and had vegetation cleared out. Retested zone and all tested ok alarms all cleared ok. Job complete
MSA-DCS | WA3530456 | Gatehouse - key control lock is faulty tounge will not throw | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 13 Aug 2020 | 2020-08-13 11:12:48 | 2020-08-13 08:15:00 | Pass | Inspected and tested but could not find fault. Operating normally.
MSA-DCS | WA3530492 | Unit 2, top landig ablutioins - broken glass window | Karnet Prison Farm | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 13 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 15:00:00 | Pass | REPAIRED & RE SET GLASS
MSA-DCS | WA3530496 | Health, whole unit - drains are blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-18 10:30:00 | Fail | cleared blockage, Wandoo to raise another work order as they would like us to return and put camera down drain
MSA-DCS | WA3530500 | Unit 4, D9 - toilet leaking from back | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 07:29:51 | 2020-08-13 13:18:00 | Pass | Removed cistern to remove flush pipe and replaced key seal
MSA-DCS | WA3530501 | Control room - CCTV camera 4 not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 07:32:02 | 2020-08-19 16:45:00 | Fail | Investigated fault, repaired intermittent fault with camera 4.Monitored for stable operation.Tested OKJob Complete
MSA-DCS | WA3530542 | UNIT 9, A10 - toilet is constantly running, the plunger seal at the bottom of the cistern appears | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-20 14:00:00 | Pass | Investigated job with unit staff and maintenance staff. Unable to locate job . No action taken.
MSA-DCS | WA3530547 | INF - no wall power in the treatment room | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-14 10:00:00 | Pass | Restored power to infirmary treatment room
MSA-DCS | WA3530561 | back shed one of the light switches has been pushed in | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 08:18:45 | 2020-08-13 10:15:00 | Pass | Replaced failed light switch.
MSA-DCS | WA3530563 | control room - external zone 1A microwave - constant alarming | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 08:12:20 | 2020-08-14 16:40:00 | Fail | Investigated, repaired fault with microwave beam set, recalibrated and tested ok.Job Complete
MSA-DCS | WA3530567 | master control fire panel showing 7 faults | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 08:21:09 | 2020-08-14 10:18:00 | Fail | VESDA status’s displaying normal on departure
MSA-DCS | WA3530586 | Eyre, Whole Unit - TV reception cutting out channels | Wandoo Rehabilitation Facility | GMP-BR- HO | ICT/Audiovisual | Hardware / Equipment (AV) | Sapio Pty Ltd | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-27 09:00:00 | Fail | Site advised to close the job off as it has been misunderstood since being raised.
MSA-DCS | WA3530596 | Kitchen - water leak on pot wash roof | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 10:45:00 | Pass | SOURCE OF LEAK - COMING FROM BOX GUTTER, REPAIRED
MSA-DCS | WA3530598 | Kitchen - leak on B side dinning roof | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-09-04 14:12:00 | Fail | REPAIR SARKING, INSTALLED FLASHING, REPAIRED A/C FLASHING
MSA-DCS | WA3530600 | Unit 2, D - top hat vent has come off in bathroom | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 14:49:00 | Pass | REPLACE FLUE, RESCREW SHEETING, CLEAN GUTTERS AND VALLEYS, REPAIR RIDGE CAPPING
MSA-DCS | WA3530673 | PDA Transponder not working in industries qaudrangle. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-09-03 11:00:00 | Fail | Job complete
MSA-DCS | WA3530677 | Gate house - Camera 29 have Horizontal lines through gate house display monitor, however required. | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-17 17:15:00 | Pass | Traced fault to transmitter fiber modem in Unit 2. Repaired fiber modem. Picture and PTZ functions tested ok from gatehouse. Parts used:Consumables
MSA-DCS | WA3530699 | Old Ambulace bay rear SHU - Handle on gate difficult to open from external side & has pinch points | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-09-08 14:30:00 | Fail | NEW HANDLES FABRICATED & FITTED
MSA-DCS | WA3530737 | Male toilets Taps in male toilets are faulty, water is not coming out | Walcott Centre (Central West Metro ) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-14 14:00:00 | Pass | Complete
MSA-DCS | WA3530742 | Unit 13 - D6 Shower screen Leaking | Casuarina Prison | GMP-BR- HO | Building | Internal Screens (BU) | Midolo Building Services | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-17 14:15:00 | Pass | RE sealed shower screen
MSA-DCS | WA3530744 | ISU, D11 - toilet and basin faulty (suspect power pack & toilet solonoid constantly running) | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-21 12:05:00 | Fail | Replced faulty parts
MSA-DCS | WA3530748 | O D P - Control Room Plantroom door will not unlock | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-09-07 13:30:00 | Fail | Service lock, require parts.Replace latch, bolt throw, lever pack, hub and spindle.
MSA-DCS | WA3530751 | Damaged section of chain-link fencing to North-east perimeter | Bandyup Prison | GMP-BR- HO | Building | Steel Fencing & Gates (BU) | AFD Contracting | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-21 10:30:00 | Fail | 19/08/20Inspected damaged fence. Measured mesh size and width for repair.21/08/20Workshop hours - load all tools required for job. Pick up material from supplier.On site hours - cut out old mesh, straighten post, install new mesh and tie off.Workshop hours - dispose material off site.
MSA-DCS | WA3530823 | unit 4 PRU control room camera 60 has lines all through video feed | Bunbury Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-11-11 17:00:00 | Fail | Identify and document all cameras on PRU 17CH modem rack. Migrate all but 10 cameras over to bottom 17CH modem rack. Identify encoder cards required at MED prison and remove from MED encoder racks and into a new 10CH rack destined for PRU. Shuffle encoders around in MED to allow for 1 x 10CH chassis to be removed. Rename encoders new rack locations.Remove 17CH fibre rack from PPU and install the 10CH encoder rack. Terminate Coax and RS485 data to rack. Remove fibre patching as no longer required. Remove associated modems from MED rack.New design has resolved the issue and and will prevent further issues with aging OM1 fibre links in the future.
MSA-DCS | WA3530840 | Unit 4, PRU - perimeter zone 3,7 & 10 in contestant alarm | Bunbury Regional Prison | SPA-BR | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 10:57:19 | 2020-08-21 13:00:00 | Fail | Retied top wires on affected zones and retuned fence. Identified excessive noise on Zone 10, replaced suspect joint kits and confirmed noise level drop and fence operating correctly.
MSA-DCS | WA3530925 | Jeelia A,B,C wing cleaning stores Locks on these doors require urgent attention | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 14:00:00 | Pass | Attended site and determined that parts were required to complete. Upon trying to book a time to return to site, Maintenance Office advised that repairs were no longer necessary as they had decided to rearrange function of the area and the locks in question were no longer required.
MSA-DCS | WA3530932 | kitchen - combi oven probe not working | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-19 13:00:00 | Fail | 19/08/20Called as requested to replace the damaged core temp probe with new. Replaced tested all working ok.
MSA-DCS | WA3530939 | Unit 1 - D5 Window spirals are broken | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-13 14:00:00 | Pass | NEW SPIRAL BALANCES FITTED
MSA-DCS | WA3530949 | Industries Admin office - 2x cabinets lock barrels are broken and unable to lock cupboards all times | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-11-04 10:00:00 | Fail | Attempt repair on locks, require parts.Replace locks on 2 x cabinets.
MSA-DCS | WA3531021 | Laundry - Workshop Urinal is blocked in the laundry | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-14 11:30:00 | Pass | Used acid and plunger to clear blockage in urinal.
MSA-DCS | WA3531059 | Key control, broken sensory in door | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 13 Aug 2020 | 2020-08-13 17:14:18 | 2020-08-17 12:02:00 | Fail | Reported gatehouse door control faults, sourced parts, attended site, repaired cabling fault and replaced broken sensor.Tested doors and interlocks OK.Job completeParts (SEME Stock):Reed Switch4 Core Security Cable
MSA-DCS | WA3531060 | unit 1, control room - faulty light, tombstone have come away and wiringis loose | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-14 08:30:00 | Pass | Repaired faulty lights in unit 1 control room
MSA-DCS | WA3531061 | Unit 6 Cell D8 - Smoke alarm not working | Hakea Prison | GMP-BR- HO | Fire Protection Services | Smoke and Heat Detection (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 13:22:32 | 2020-08-13 14:49:00 | Pass | Attended site and found no one on site knew anything about the faultWing SO checked maintenance log and found no record of fault logged.Both Vesda units showing normal.Sample point possible cleared by wing officers before our arrival on site.
MSA-DCS | WA3531065 | Unit 10, A wing - Grille hard to double lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 13:22:16 | 2020-08-13 15:30:00 | Pass | 4L42 main throw bolt damaged. Repaired to restore proper function.
MSA-DCS | WA3531070 | Stores Main roof leaking badly | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 15:00:00 | Pass | REPAIRS TO SKYLIGHTS, MODIFY AIR VENTS ACROSS ROOF TOP. CLEAN RUBBISH OFF ROOF, GENERAL MAINTENANCE
MSA-DCS | WA3531071 | Assessments - Lock on door closest to basketball courts is sticking | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 13:28:08 | 2020-08-13 16:30:00 | Pass | Lock repaired and broken part replaced to restore proper function
MSA-DCS | WA3531072 | Unit 10 B wing 2 tiles missing in showers near the grille | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2021-03-29 22:42:00 | Fail | NEW TILES INSTALLED ACCORDINGLY
MSA-DCS | WA3531074 | Unit 10 Cell A16 Cell call button stuck inside | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 13:29:48 | 2020-08-13 15:00:00 | Pass | LED on the intercom on all the time. No active call message on the officer station display. PA also stopped working. Line busy message would show on the display when trying to make an announcement. Reset power to NODE. A16 intercom tested loud and clear. PA tested ok. Parts used:Consumables
MSA-DCS | WA3531095 | Stair well reception L1 large round light has been smashed-light out in ladies toilet | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 13:31:51 | 2020-08-14 11:00:00 | Pass | Replaced smashed light in stairwellFixed faulty light in ladies toilet lvl 2
MSA-DCS | WA3531097 | Unit 8 A/B Wing Wall behind boiler rusty & dangerous | Hakea Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-09-18 12:45:00 | Fail | ADVISED TO closing off cost to date, job to be re issued as a LVM in the future.
MSA-DCS | WA3531101 | Unit 9 A7 Cell call not working in cell | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 13:38:04 | 2020-08-13 17:00:00 | Pass | Poor audio in the cell and in the control room. Intercom filled with toothpaste. Removed and replaced with new intercom. Tested, audio is loud and clear in cell and in control. Stripped and cleaned the intercom at the gatehouse and kept as a site spare. Parts used:Cell Guard intercom CI-CCRJ45 wiring adapter Consumables
MSA-DCS | WA3531106 | Unit 1 Cell D09 Cell call not activating | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 13:38:51 | 2020-08-13 17:00:00 | Pass | No activation when call button pressed. Removed and replaced with new intercom. Tested, loud and clear audio in cell and in control. Parts used:Cell Guard intercom CI-CCconsumables
MSA-DCS | WA3531126 | Unit 7, H wing Cells 1-8 - Numerous blocked toilets in cells H1 – H8 | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 14:05:09 | 2020-08-14 08:47:00 | Pass | Drain machine used to unblock wing
MSA-DCS | WA3531130 | Pharmacy, Disabled toilet - Flush mechanism is faulty | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-14 09:40:00 | Pass | Replaced broken care flush button on disabled toilet
MSA-DCS | WA3531155 | Laundry room - Washing machine No 2 not operational. No water flowing into machine-see notes | Hakea Prison | WSM-MW-SITE | Electrical | General Electrical (EL) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 14:15:15 | 2020-08-14 12:45:00 | Pass | WM # 2 Water flowing into machine.Check Machine - Door lock faulty - requires replacement. Return to site with part, Supply & fit. Machine still faulting. Remove machine to workshop to diagnose.MACHINE NOT ECOMOMICAL TO REPAIR - QUOTE FOR SUPPLY & INSTALL OF NEW MACHINEBRAF approved - return to site - supply & fit new Washing Machine
MSA-DCS | WA3531162 | Unit 4 - D5 Sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-18 16:00:00 | Pass | Plunged basin to clear blockage
MSA-DCS | WA3531164 | WWTP 1000ltr IBC mixer faulty | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-09-11 09:00:00 | Fail | Service Report attached
MSA-DCS | WA3531166 | Unit 14 Control room door to B/D Wing is rubbing on the door frame, hinges require alignment. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 11:00:00 | Pass | Replaced hinges
MSA-DCS | WA3531168 | Unit 2 - C Wing Toilet system in Cell C4 continuously running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-17 16:00:00 | Pass | Installed new inlet valve in cistern
MSA-DCS | WA3531182 | Unit 2, D wing, cell 7 - water over flow in toilet system keeps running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 08:30:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3531184 | Unit 2 A Wing 2 x EMC lights not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-17 11:00:00 | Pass | Investigate lights not working.Source parts, repair 2 x lights in unit 2 A wing
MSA-DCS | WA3531189 | Unit 2 - C Wing Toilet system in Cell C10 continuously running | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 09:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3531196 | WWTP CSPL & MFC6 dosing pumps faulty | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | MAK Industrial Water Solutions Pty Ltd | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-09-11 09:00:00 | Fail | Completed during service visit. No charge. Notes included on Mak SR 14855.
MSA-DCS | WA3531197 | Unit 14 - Court Yard A/C gate lock to rear of units not working | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-14 12:00:00 | Pass | Service gate lock.
MSA-DCS | WA3531376 | Pod entry fire panel coming up with faults and continues to alarm | Bandyup Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 0 | CLOSE | 13 Aug 2020 | 2020-08-13 19:40:00 | 2020-08-13 18:40:00 | Pass | 13/8/20 JNL9 D8 showing multiple device and L9 D9 showing missing fault intermittently. Replaced L9 D9 and found address buttons were sticking ondetector. Also replaced L9 D8 as detector was visibly dirty and corroded.
MSA-DCS | WA3531404 | cam 53 - distorted poor quality image | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-11-02 11:30:00 | Fail | Replaced camera 53 for gatehouse vehicle gate - replaced with new BX420 Indigo camera, all cabled,installed and programmed ok. License file for NVR updated and all recording schedule setup and working ok. Job complete
MSA-DFES | WA3530918 | Station officers room issues with power points - see notes | CFRS Vincent | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 09:45:00 | Pass | Arrived at Vincent fire station at 0930. Spoke to Steve about power and data points playing up and he told us the phone line wasn’t working and neither was the internet on a computer. Upon diagnosis of fault we found that the data cable had been connected in the wrong port. Swapped the data to the correct terminal and phone line and computer were working as normal with internet. Discussed completed works with Steve and signed out for 0945.
MSA-DFES | WA3530990 | rear yard hydrent branch off point spraying water above ground copper pipper - see notes | CFRS Malaga | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 09:30:00 | Pass | Located to site to fix burst fire main
MSA-DFES | WA3531391 | Kitchen Area (15) Kitchen cabinet door hinges are loose-see notes | CFRS Perth | GMP-BR | Carpentry | Timber (all types) (CA) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 12:30:00 | Pass | Adjusted and tightened hinges to all kitchen cupboards as requested. Only needed to replace 1 set of hinges
MSA-DFES | WA3531406 | Claremont FS-Main Building - self closure on the duty door is broken. | CFRS Claremont-Main Building | GMP-BR | Building | Automatic Doors (BU) | AWB Co. | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-14 08:00:00 | Pass | Complete
MSA-DTAG | WA3530756 | L15 Plant room fire doors are not closing properly – panels are de-laminating | Central Law Courts | GMP-BR-HO | Building | Fire Door (BU) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-14 15:00:00 | Pass | Fire doors found to be damaged and delaminating, quote to be submitted for removal and replacement including all new hardware
MSA-DTAG | WA3530761 | Basement custody cell 3 Water fountain constantly running-see notes | Perth Children's Court | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-24 15:25:00 | Fail | attended 13.8.2020 system requires non standard insert valve for unbranded fountain ordered in and returned on 24.8.2020 to replace valve attended as per job sign slips
MSA-DTAG | WA3530789 | ground, Security Office - Low battery warning relating to duress alarm | Perth Children's Court | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-13 14:00:00 | Pass | Replaced Battery.
MSA-DTAG | WA3530906 | Fire Panel Isolation for 13/08/20 9.3pm-Confirm with Datatel which areas need to be isolated | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 09:00:00 | Pass | 13/8/20Isolated Z6-11 basement as requested by Datatel14/8/20Deisolated zones while on site conducting monthly testing
MSA-DTAG | WA3530922 | court room 1 - weighted door closer stopped working and door now slams shut | Joondalup Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-14 09:15:00 | Pass | adjustment made to door closer
MSA-DTWD | WA3530568 | V Block toilets - exhaust fans not working | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-19 12:00:00 | Fail | Repalced faulty rcd and contactor. Tested fans all working now. Job completedm
MSA-DTWD | WA3530713 | Mutiple faulty/flickeing fluro lights - tower ground floor men toilet & tower level 2 2x fluros | West One Services | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 13:00:00 | Pass | Job complete.
MSA-DTWD | WA3530796 | Near main conference room pond current water supply only a trickle | West One Services | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 13 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-13 16:00:00 | Pass | Complete
MSA-DTWD | WA3530941 | Pines Restaurant – Carpet tears – Trip Hazard | Bentley Campus | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-20 08:50:00 | Fail | Repair damaged carpet
MSA-DTWD | WA3530945 | B block Library – Light switch is faulty | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 11:45:00 | Pass | Attended site and signed in. Located B block library. Found faulty switch on bottom of plate. Replace switch mech and tested all okay. Job complete
MSA-DTWD | WA3530951 | Block 8 EBT kitchen Chilled water supply from chilled /boiling water unit not working properly | Thornlie Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 12:59:00 | Pass | Warranty issue site to contact BILLI direct
MSA-DTWD | WA3531011 | O block O004 faulty power point GPO | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-19 15:30:00 | Fail | Repalced faulty 15ampcpitlet amd rcd. Job completed,
MSA-DTWD | WA3531025 | F block FT10 Light switches arcing. Switch mechs probably need replacing-see notes | Carlisle Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 09:45:00 | Pass | Arrived on site , signed in , spoke to client about switch mechs arcing , got keys for access , located arcing switches , completed jsa , tested switches and deemed they needed replacing , isolated lighting circuit , removed old mechs from switch plates , fitted new mechs in switch plate and terminated cables , fixed plates back to wall flush , re-energised lighting circuit , tested switches worked correctly, both switches in working order and functioning as they are meant to be , completed signature slip , signed out , job completed
MSA-DTWD | WA3531157 | BLD 824 Gas Hot water system faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | Gas (PD) | Lane's Plumbing | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-20 18:00:00 | Fail | Supply and install new HWS
MSA-DTWD | WA3531160 | F block, FG32 - Leak in evap room, looks like its coming through evap exhaust vents (see notes) | Carlisle Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-09-14 12:30:00 | Fail | Water leaking around evap vent, roof access required but raining on first visit. Door has minor damage but still operates properly so Frank is happy to leave it as is.19/8/20 Reattended and sealed suspect areas. Will need to check during next rain to see if work has resolved the problem 14/9/20 - Have attended to repair roof leak. Confirmed with site the leak seems to be fixed. Works to address sagging door frame will need BRAF preparation
MSA-DTWD | WA3531163 | 1st floor A-Block lift - Small leaks either side of the lift | Carlisle Campus | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-09-14 15:30:00 | Fail | Attended site and inspected leak in the A Block lift. Will need to return in dry weather to inspect from the roof. 14/9/20 - Site advised leak was still an issue on one side of the lift. Re-attended site and installed compriban foam under suspect flashing Will need to confirm during next rain expected over the coming weekend Will need to repair ceiling water damage once resolved
MSA-DTWD | WA3531313 | Dempster Hall, Flat C Bathroom - Toilet light faulty | Muresk Institute | GMP-BR | Electrical | Lighting, Internal (EL) | Damian Rak Electrical Pty Ltd | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 16:00:00 | Pass | Replaced faulty lamp
MSA-DTWD | WA3531379 | F block FG31 Leak above Reem hot water system near wash bay next to cool room. | Carlisle Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-09-14 11:30:00 | Fail | Water running down cold storage wall. Roof access required. Raining on first visit not allowing roof access. Large pipe in picture is a downpipeRescheduled to attend 19/8/20 -Rusty box gutter needs replacing and 3 x rusty pops 100mm. BRAF will need to be prepared11/9/20 - Scheduled for Monday. Have been waiting on fine weather to begin works. Works completed 11/9/20
MSA-DTWD | WA3531383 | T block two security cameras above the Library court yard are not working | Murdoch Campus | GMP-BR | Security | CCTV Surveillance (SE) | Total Security Systems Pty Ltd | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 12:30:00 | Pass | 17/8/2020 - Ryan Jamieson - 10.45am to 12.30pmAttended site for 2x camera faults. I located the cameras and the Milestone nvr then attempted to search for the Hikvision cameras via the search tool on my laptop via the switch however I could not see any cameras. I spoke to their IT department who advised the cameras have never been online and they have scanned the network and couldn’t find them. To investigate further we would need to hire a boom lift and barricade off the area below to physically access the camera and cables.Sent BRAF to Programmed Andrew Crawford. Site have advised no further reattendance required with a lifter to investigate further. Job closed.
MSA-DTWD | WA3531384 | S block gas leak on #1 fume cupboard in Lab S1, when the fume cupboard is turned on | Murdoch Campus | GMP-BR | Plumbing & Drainage | Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 13 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 17:00:00 | Pass | Rectify gas issues on exhaust cupboards and bunsin burners
MSA-MRWA | WA3531347 | L2 male toilets Urinal leaking, please attend and remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 13 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 08:52:00 | Pass | Fixed leaking rhs urinal on l2.
MSA-DCS | WA3533658 | Medical Centre - Safe is faulty and wont unlock | Banksia Hill Detention Centre | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 14 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-24 12:30:00 | Fail | 14/08/2020 - Attended site. Gained entry to safe and removed to workshop for repair and extended testing of 7-10 days24/08/2020 - On site. Reinstalled the repaired and tested unit
MSA-DCS | WA3533662 | Jeelia, A5 - Drain blocked | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 14 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 08:30:00 | Pass | Clear blockage to basin waste
MSA-DCS | WA3533692 | Sterile zone concrete pit has collapsed | Wandoo Rehabilitation Facility | SPA-BR | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 14 Aug 2020 | 2020-08-20 17:00:00 | 2020-09-01 12:15:00 | Fail | OLD PIT REMOVED & NEW INSTALLED
MSA-DCS | WA3533699 | Gardens/Maintenance pit is sinking and unsecure | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 14 Aug 2020 | 2020-08-20 17:00:00 | 2020-09-01 11:00:00 | Fail | OLD PIT REMOVED - NEW ONE DUG IN - FORM WORK AND CONCRETED
MSA-DCS | WA3533736 | Gate house, control room door - door won't shut | Wooroloo Prison Farm | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Aug 2020 | 2020-08-14 12:07:38 | 2020-08-14 12:50:00 | Fail | Contacted K.Bennett as requested.Advised door is catching on reed switch.Hole that has been drilled for the reed switch is slightly to large.Secured reed switch in place with adhesive
MSA-DCS | WA3533794 | Unit 9 Cell B9 Water leaking into light fitting - possible pipe leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 14 Aug 2020 | 2020-08-15 08:48:55 | 2020-08-14 16:30:00 | Pass | Climbed into roof space located start off a water leak on hot line only aqua therm pipe will be back later today with gear to repair leak Return to repair section off burst pipe on aquatherm
MSA-DCS | WA3533804 | Visits - Loby Area Camera Monitors not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Aug 2020 | 2020-08-15 08:56:44 | 2020-08-14 11:06:00 | Pass | Powersupply showing 9vdc, should be 12 vdcReplaced powersupply with powerbox13.8vdc from van stock.All monitors are back online
MSA-DCS | WA3533888 | Unit 1, Outside End of Unit Yard gate - Lock intermittently Jamming and unable to unlock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 14 Aug 2020 | 2020-08-15 09:34:27 | 2020-08-14 13:00:00 | Pass | Serviced lock to restore normal function.
MSA-DCS | WA3533949 | Entrance driveway - Large pot holes causing damage to car rims | Hakea Prison | GMP-BR- HO | Paving & Roadworks | Concreting (PR) | AFD Contracting | 1 | CLOSE | 14 Aug 2020 | 2020-08-15 10:05:11 | 2020-08-14 14:30:00 | Pass | 14/08/20Fixed pot holes as best as could while in wet conditions
MSA-DCS | WA3533978 | Unit 8 - A/B & C/D unit doors not shutting corrctly | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Aug 2020 | 2020-08-15 10:09:52 | 2020-08-17 10:15:00 | Fail | Investigated fault, checked electric strikes, checked workstation, tested doors multiple times and monitored for correct operation. Found on occasions, doors don't close completely with enough force to latch into strike. Requires door/mechanical contractor to modify/adjust door closer mechanism.Advised prison staff.Electronic Strikes are working correctly.Job Complete
MSA-DCS | WA3534018 | Unit 13,D2 - top bunk reading light not working | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-17 08:30:00 | Pass | Investigate and repair unit 13 D2 bed light
MSA-DCS | WA3534054 | Passge door (between staff room & kitchen area)- swipe for door intermittently working - see notes | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 14 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-20 10:29:00 | Fail | Found lock screw lose, tightened and found wire lose, fixed to lockTested lock all tested ok
MSA-DCS | WA3534083 | WWTP damage power cable to clarifer pumps | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-28 15:00:00 | Fail | Replace cable and conduit to wwtp clarifier pump
MSA-DCS | WA3534125 | WWTP screening pit isolater broken | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-14 14:30:00 | Pass | Investigate and replace screening pit isolator
MSA-DCS | WA3534152 | Unit 14 - Control Room Unable to operate electronic doors | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 14 Aug 2020 | 2020-08-15 11:44:44 | 2020-08-14 16:00:00 | Pass | Attended site checked and found Init14 Control EBI workstation touch screen can’t open doors in Unit. Further check located the problem to be the stuck keyboard. Rectified the problem and tested it ok.
MSA-DCS | WA3534250 | Unit 3 - C10 Leaking toilet cistern | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-17 11:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3534261 | Gatehouse - visits side exit door not closing | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 1 | CLOSE | 14 Aug 2020 | 2020-08-15 13:12:38 | 2020-08-14 14:15:00 | Pass | Door closer adjusted
MSA-DCS | WA3534289 | Unit 3 - C4 Leaking toilet cistern | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-17 10:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3534293 | MPU - SPU kitchen oven hotplates. When rhs areas are switched on it trips the power in switch board | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-28 10:25:00 | Fail | Disconnect hotplate & leave for parts / replacement. Enable 3 other hotplates to work. Return 28/08/20 fit element & test all 4 ok.
MSA-DCS | WA3534296 | Canteen east Water from roof leak coming through extractor fan | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 14 Aug 2020 | 2020-08-19 17:00:00 | 2021-02-25 14:40:00 | Fail | REPAIRS MADE TO ROOF
MSA-DCS | WA3534340 | Unit 3 - A5 toilet leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-17 09:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3534345 | Unit 3, D1 - toilet leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-17 08:30:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3534346 | kitchen rear roller door (store) roller door is very hard to open | Banksia Hill Detention Centre | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-28 11:45:00 | Fail | 28/08/20Adjust tension on roller door so it is easier to open upwards.Load up all tools for possible height / access requirements.
MSA-DCS | WA3534347 | Unit 3, B4 - toilet leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-17 12:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3534352 | Yeeda Nicol air con unit is not working | Banksia Hill Detention Centre | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 14 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-17 09:00:00 | Pass | Condensate pump float stuck and making noise. Dislodged and cleaned float mechanism, flushed drain, confirmed no longer stuck and making noise.
MSA-DCS | WA3534424 | Unit 1 D12 camera can be seen unit 1 control cannot be seen by the pod CCU | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 14 Aug 2020 | 2020-08-14 20:53:59 | 2020-08-17 11:55:00 | Fail | Investigated fault, traced to comms issue in medical centre, repaired comms fault and confirmed safe cell is now viewable in unit 1, ccu and the main control room.Tested OKJob Complete
MSA-DCS | WA3534434 | Karnet Prison Farm - Unit 2 - Cell 84 - lock is broken | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 0 | CLOSE | 14 Aug 2020 | 2020-08-14 21:57:09 | 2020-08-14 20:45:00 | Pass | Afterhours urgent attend site, to gain entry to cell as lock wouldnt operate.fit replacement lockbody, replacing damaged cylinder, keyed to system, to operate the keys supplied onsite.
MSA-DFES | WA3534421 | Kitchen corner cupboard door broken from hinges - see notes | CFRS Maddington | GMP-BR | Furniture | Domestic Furniture (FU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 14 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-18 14:30:00 | Pass | Replaced cupboard hinges and bin draw as requested by site
MSA-DFES | WA3568374 | RETROSPECTIVE Work order-BYPASS: Z14 REED SWITCH ON DINING ROOM DOOR | VFRS Mandurah | GMP-BR | Security | Guards (SE) | Securex Security Systems & Services | 1 | CLOSE | 14 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-14 15:05:00 | Pass | Despatch Comments:BYPASS: Z14 REED SWITCH ON DINING ROOM DOORPatrol Resolution:NIL KEYS HELD EXTERNAL ONLYSTAFF CARS AND MEMBERS ONSITE ALL APPEARS IN ORDER
MSA-DTAG | WA3533881 | L4 Female staff toilet door not closing properly – digital code required for access | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-14 14:15:00 | Pass | new door closer fitted
MSA-DTAG | WA3534373 | ground Court 1 Various ceiling Lights not working-see notes | Mandurah Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-25 08:15:00 | Fail | Replaced faulty led globe
MSA-DTWD | WA3533667 | A block, auto door (near reception) - wont close | Munster Campus (ACEPT) | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 14 Aug 2020 | 2020-08-14 17:00:00 | 2020-08-14 10:35:00 | Pass | 1076491. Call to site. Attend to auto door. Locate to and replace corroded PE interface board. Check operational and safety features - all okay.
MSA-DTWD | WA3533684 | B block, leel 1, B107 - room is too dull, old tubes may need replacing | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 14 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-17 15:00:00 | Pass | Attended site and signed in. Located B107. Found room to have working lights in 840 colour. Spoke with site regarding the lighting options and did test runs of lights to see what they desire with replacing the tubes. Replaced 1 row of lights to 865 colour temp to change the light output over the work bench. Left the rest of the room standard as requested by site. Job complete
MSA-DTWD | WA3533815 | L1 laneway relay uneven paving - tripping hazards | Perth Campus B5 | GMP-BR | Paving & Roadworks | Paving (PR) | AWB Co. | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-17 13:00:00 | Pass | Works completed pending trade notes and documents.
MSA-DTWD | WA3533854 | Nth block L3 N321 Broken window blinds | Perth Campus B1 | GMP-BR | Building | Windows (BU) | NEYLOR | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-09-22 10:43:00 | Fail | Lift1 HMT-Geared :Found lift locked off on arrival. Could not contact passengers to gather more information. Ran lift to all floors and found no fault. Accessed top of car and adjusted door lockbridge. Checked all other floors and also adjusted ground floor lock due to lock bridge evident binding on contact block. Tested lift and left unit in service.
MSA-DTWD | WA3533896 | L1 student kitchen Tap is leaking | Perth Campus B1 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-19 17:00:00 | Pass | Fixed billi unit
MSA-DTWD | WA3534082 | Block 8, ground T floor, Koora-Mar centre - Internal door locks not working | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-19 11:00:00 | Pass | Block 8 - Koora-Mar - Locks faulty.Locks repaired.
MSA-DTWD | WA3534120 | A block, level 2, room 214 - the aircon wall button is broken | Joondalup Kendrew Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 14 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-14 13:54:00 | Pass | Diagnosed switch . Facilities asked me to get 4 . Picked up 4 replacements as they break all the time . Changed out broken one . Completed works by testing unit
MSA-DTWD | WA3534141 | D block ground gym area replace all blown lights and in toilets | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 14 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-17 14:30:00 | Pass | Changed 25x 26w 2pin globes, 9x 9w 2 pin globes and 5x 13w 2 pin globes, changed 3x ec13 ballest and 6x ec18/20 ballast.
MSA-DTWD | WA3534257 | E-Block, ground, restaurant Kitchen - Restaurant Kitchen the Flat Grill does not stay lit | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 14 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-17 15:30:00 | Pass | COMPLETED
MSA-DTWD | WA3534270 | E-Block, ground, restaurant Kitchen - the prover cabinet makes a rattling sound when turning on | Joondalup Kendrew Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 14 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-17 16:00:00 | Pass | COMPLETED 17/8/20
MSA-DTWD | WA3534277 | E-Block, ground, Training Bar behind E-19 - has blocked sinks | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 14 Aug 2020 | 2020-08-17 17:00:00 | 2020-08-17 08:45:00 | Pass | COMPLETED
MSA-MRWA | WA3533864 | Lift No 3 people stuck in lift | Don Aitken Centre MRWA Head Office | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 14 Aug 2020 | 2020-08-14 13:25:52 | 2020-08-14 12:45:00 | Pass | Lift3 DAC-Geared :SWP were already out on arrival. Recorded fault log; car was NAV, Front DTC, and 2701shutdown on drive.Found high resistance on relay contacts. Changed contacts; BSR13 & 14, ESR 13 & 14, LB 21 & 22. Did 150 runs of lift, no fault recorded. Put lift back on service.
MSA-MRWA | WA3533975 | mid vent building Camera 78 has lost PTZ function, please inspect and remediate/report | Traffic Operations Centre | GMP-BR | Security | CCTV Surveillance (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 14 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-18 00:00:00 | Pass | 18/8/20 - Dylan ParslowInvestigated issues with mid vent PTZ camera 78.Tested PTZ functions directly at camera with 2 seperate camera testers. Unable to use PTZ function, requires replacement.
MSA-DCS | WA3539323 | Unit 1 Cell B6 - Cell call is faulty | Albany Regional Prison-Prisoner Accommodation Unit 1 | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 15 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-19 08:29:00 | Pass | Cell call only working 1 way.Removed and replaced with CI-CC from van stock.Cell call fully operational
MSA-DCS | WA3539325 | Cell 513 cell call button not working | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 15 Aug 2020 | 2020-08-16 10:43:41 | 2020-08-17 14:45:00 | Fail | No activation when call button is pressed. Tested directly into CI8, still no activation. Traced fault to input on CI8 #2. No working spare inputs on other CI8 boards. Used site spare to repair fault. No more working CI8s on site. Intercom 5-13B and 5-13A both tested loud and clear in cell and in control. Parts used:Consumables
MSA-DCS | WA3539388 | Hakea Prison-Control room Unit 1 - VESDA fault in the fire alarm | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Automatic Fire Protection (ARA) | 1 | CLOSE | 15 Aug 2020 | 2020-08-16 14:56:54 | 2020-08-15 16:20:00 | Pass | 15/8/20 JN - Hakea PrisonFault on cell block 5 due to unit 5 being isolated. Deisolated and panel back to normal.
MSA-DCS | WA3539397 | Lost power in unit 14 - doors, computers etc not working | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 15 Aug 2020 | 2020-08-15 19:42:16 | 2020-08-15 21:00:00 | Fail | Control power isolation switch activated somehow and cut power to control desk. Gatehouse control desk unable to find reset in computer. Bypassed the isolation with the auto/ man switch in the unit 14 switchboard and site will get SEME to rectify the fault.
MSA-DCS | WA3568175 | Unit 3 Control Room key broken inside lock - Retrospective - do not re-atttend | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 15 Aug 2020 | 2020-08-16 01:49:00 | 2020-08-15 22:25:00 | Pass | Actually attended 15/08/2020 at 08:25am to 09:00am. PFM system down so Work Order not created until later.Removed broken key and repaired lock to restore normal function.
MSA-DCS | WA3540435 | Unit 4 - A wing Day room - Lock is broken- can't access day room. | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 16 Aug 2020 | 2020-08-16 11:21:44 | 2020-08-18 10:15:00 | Fail | 16/08/2020. Attended site after hours. Removed lock from door to allow access, handles had been snapped off. Parts required.18/08/2020. Replaced broken handles and re-fitted lock to restore normal function.
MSA-DCS | WA3540437 | West Kimberley Regional Prison- energised fence, Zone 2,3,6,12,16,17,18,21 | West Kimberley Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 16 Aug 2020 | 2020-08-16 15:35:42 | 2020-08-17 16:00:00 | Fail | Traveled to site.Attended site and investigated electric fence alarm faults. Reset several controllers and checked history log for any intermittent issues, no issues found. Found EC2 cardax controller had been offline. Tested voltage and all tested ok, found issue with GBUS ports, replaced EC2 controller with new 6000 Controller (site stock used)Programmed,powered up and tested ok. Found Network switch In EC cabinet offline. Programmed new network switch and installed into cabinet. All tested and working ok. 1 x Planet network switch used (Site stock)Walk tested all perimeter electric fence zones and tested for correct operation, all tested and working ok. Job complete
MSA-DCS | WA3540597 | Wooroloo Prison Farm - in visitor centre, CCTV camera unable to playback | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 16 Aug 2020 | 2020-08-17 12:20:19 | 2020-08-17 11:42:00 | Pass | Rectified and fixed the NVR recording issue. Job completed.
MSA-DCS | WA3556684 | Eyre B1 cell light switch faulty | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-19 12:00:00 | Pass | Replaced damaged switch
MSA-DCS | WA3556692 | gate front door front door latch fault….not closing | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 07:20:17 | 2020-08-20 10:30:00 | Fail | 17/08/2020 - Assessed issue - parts required. 20/08/2020 - Fitted new door closer to mitigate issue. Door may require adjustable seals in the future.
MSA-DCS | WA3556741 | gate house intercom system button has come out cannot use | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 17 Aug 2020 | 2020-08-17 15:43:54 | 2020-08-17 14:30:00 | Pass | Asked by office to contact site to determine fault and identify parts required. Button on Intercom broken, replacement Aiphone LEF-5 required. Attended suppliers location and picked up Intercom. Drove to site, removed faulty Intercom,installed new unit. Tested Intercom to allocated locations. Good communications.
MSA-DCS | WA3556746 | Unit 3 Cell C11 window spring broken needs repair | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 17 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-21 12:15:00 | Pass | SPIRAL BALANCES REPLACED
MSA-DCS | WA3556749 | Unit 3 Cell C02 requires new handle has fallen off | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 17 Aug 2020 | 2020-08-21 17:00:00 | 2020-09-21 14:00:00 | Fail | NEW CELL HANDLE INSTALLED
MSA-DCS | WA3556755 | Unit 3, Cell C01 window smashed needs replacing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 07:53:48 | 2020-08-17 15:00:00 | Pass | RE NEW SASH AND SPIRAL BALANCES - RE GLAZE WINDOW
MSA-DCS | WA3556765 | Unit 14 - B & D hot water not working kitchen area | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Aug 2020 | 2020-08-19 17:00:00 | 2020-10-14 09:30:00 | Fail | 20/8/20 - Inspected unit. Unit does not boil. Solenoid does not open to fill unit. Element does not heat water. Unable to recalibrate unit. Water leaked from inside unit when cover removed. Circuit boards covered in cockroach poo. Unit 5 years old. Braf required to replace.
MSA-DCS | WA3556774 | Unit 6 - B1 prisoner complaining that when he puts his bed light on his tv cuts out. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 09:30:00 | Pass | Repaired faulty lights in unit 6 b1
MSA-DCS | WA3556777 | Unit 3, D Wing landing cleaning cupboard drain in the floor is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-17 14:00:00 | Pass | Removed grate. Cleaned grate holes. Plunged drain and reinstalled drain grate.
MSA-DCS | WA3556783 | Unit 3 - B Wing Cell B 02 Window Spring not catching. Window does not stay open, | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 13:00:00 | Pass | SPIRAL BALANCES REPLACED
MSA-DCS | WA3556785 | Unit 1 - the B/D regi oven will not heat up, the main breaker was reset but still not working | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 08:12:30 | 2020-09-07 10:30:00 | Fail | Repair connection & test ok. Returned 7/09 to replace both glass seals & fitted ok.
MSA-DCS | WA3556791 | Hatch on A8 is not unlocking Unit 1 | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 08:17:00 | 2020-08-17 10:00:00 | Pass | Open jammed hatch and replace lock.
MSA-DCS | WA3556829 | Orientation, interview room 1 - door can not be locked | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 08:29:45 | 2020-08-17 11:15:00 | Pass | Repaired lock to restore normal function.
MSA-DCS | WA3556937 | Academy Accommodation Wing 3x showers in female bathroom blocked drains -see notes | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 09:36:02 | 2020-08-17 17:40:00 | Pass | X2 drain machines used to clean out inside and outside drains removing nearly 3 meters off tree roots
MSA-DCS | WA3556943 | Reconnent HWS - container freezer hire | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Main Kitchen | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 09:30:00 | Pass | Reconnected 3 phase HWS in kitchen
MSA-DCS | WA3556966 | Accomadation Laundry - Dryer No 2-clothes do not dry properly | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 09:50:51 | 2020-08-21 13:00:00 | Fail | AMS675877 WA3556966 - No 2 Dryer - Not drying properly. Check Dryer 1 & 3 .Dryer #2 - remove from site due to excessive lint build up and return to workshop - Carry out Necessary repairs to Dryer. Return to site and reinstall. *** Excessive lint build up in No 1 & 3 Dryers , which could be a fire risk!!*** .
MSA-DCS | WA3557012 | Zone 6, omitrax no activation | Greenough Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 10:28:38 | 2020-08-25 15:30:00 | Fail | Senstar module lost its configuration. Ran profile plots for zones 5 and 6 Omnitrax. Calibrated and tested ok to gatehouse.
MSA-DCS | WA3557034 | Old control Corridor numerous corridor lights damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-18 10:00:00 | Pass | Replaced faulty lamps and ballast
MSA-DCS | WA3557038 | kitchen cool room 2 coolroom 2 light damaged | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 12:00:00 | Pass | Replaced faulty lamps
MSA-DCS | WA3557042 | CCU (11), C5 - Blockage in sink and faulty tap. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 10:30:00 | Pass | Plunged basin to clear blockage. Cleaned blockage from tap outlet.
MSA-DCS | WA3557046 | Kitchen 1 x sink leaking frrom drain & 1 x sink tap spout leaking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 09:30:00 | Pass | Renew wall out let and plug and waste
MSA-DCS | WA3557069 | Stores - Roller door knocked out of track | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Roller Shutters (BU) | UNIVERSAL DOORS | 0 | CLOSE | 17 Aug 2020 | 2020-08-17 14:46:38 | 2020-08-17 14:15:00 | Pass | Replaced bottom rail
MSA-DCS | WA3557081 | Unit 3 Cell B03 personal lock needs repairing | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-17 14:00:00 | Pass | Replace door plate, lock and weld on strike.
MSA-DCS | WA3557084 | gate house - front door, faulty switch not working correclty - not opening front door | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 10:00:00 | Pass | Attended site and investigated programming of cardax system thoroughly between entry doors and reception push buttons. Checked all programming and tested all door functions and found to be working ok and as per site ASCON drawing notes from project handover. All tested and working correctly. Job complete
MSA-DCS | WA3557089 | Videolink 2x damaged smashed power points | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 10:57:53 | 2020-08-17 12:30:00 | Pass | Replaced broken gpos
MSA-DCS | WA3557105 | Unit 1, yard - There is a large hole in the wall in the A/C wing outdoor phone booth | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 11:00:00 | Pass | HOLE HAS BEEN FILLED
MSA-DCS | WA3557118 | MPU Office - powerpoint RHS as you entered Senior Officer office has nearly been knocked of the wall | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-20 10:30:00 | Pass | Repaired damaged gpo in mpu office
MSA-DCS | WA3557134 | POD - screens not showing camera 112, 114, 116 - | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 11:13:21 | 2020-08-17 16:30:00 | Pass | Rectified and fixed the camera connection issue with indigo, job completed.
MSA-DCS | WA3557140 | Unit 2, A wing yard - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-17 15:00:00 | Pass | Replaced broken light
MSA-DCS | WA3557147 | ERU hut leaking a couple of the ceiling sheets have fallen - see notes | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 11:25:51 | 2020-08-18 08:00:00 | Pass | REPAIRS TO CEILING PANELS
MSA-DCS | WA3557161 | Garments, toilets - water leaking in plumbing ducts behind toilets | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-19 08:30:00 | Pass | Investigated and tested all pipes and fixtures. No leaks detected.
MSA-DCS | WA3557162 | Unit 7 - C Wing Main power switches at back of oven in kitchen are disintegrating and are a hazard. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-20 13:30:00 | Pass | Checked damaged kitchen appliance gpos. Isolated and picked up replacement parts. Installed and tested
MSA-DCS | WA3557169 | Unit 3 - Office Grille lock damaged to SO office | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-10-09 15:30:00 | Fail | Open jammed lock and service, requires lock rebuild.Remove lock, install temp lock, rebuild lock in workshop, reinstall rebuilt lock.
MSA-DCS | WA3557182 | Education, Art room - 2 double GPO's broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 12:30:00 | Pass | Replaced gpos
MSA-DCS | WA3557186 | front gate, master control - camera screen not working | Melaleuca Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 11:57:52 | 2020-08-17 15:23:00 | Pass | Attended site, investigated and repaired CCTV faults in control room. Tested All OKJob Complete
MSA-DCS | WA3557210 | Outpatients Area, Lunch Room - Shut off valve faulty to the water fountain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-19 09:30:00 | Pass | Replaced faulty isolation valve that was seized open.
MSA-DCS | WA3557265 | U2 h2 Power supply failed | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-17 17:30:00 | Pass | Found issue with cardax power supply monitoring of mains fail. Replaced with new Gallagher power supply (site stock used)Installed and tested ok. Job completePart returned to site stock
MSA-DCS | WA3557270 | Bulk stores expander off line | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-18 09:30:00 | Pass | Bulk stores expander offline. Checked history log and found expander had lost its software and had cause expanders to go offline. Re installed with latest software and retested. All zones armed and tested ok. Job complete
MSA-DCS | WA3557275 | Key watcher faulty | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-17 19:00:00 | Pass | Reconnected door that had been removed on keywatcher panel. Tested lock functions and board voltage. Issues found between door lock and main board, both required for replacement. To be replaced under WA3514410. Job complete
MSA-DCS | WA3557332 | unit 9 A1 Viewing glass broken | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 13:15:04 | 2020-08-18 09:30:00 | Pass | RE FITTED NEW VEIWING GLASS
MSA-DCS | WA3557486 | Unit 4, C wing, C5 - toilet system leaking cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 11:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3557487 | Unit 4, C wing, C7 - toilet system leaking cell | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 13:00:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3557490 | Unit 4, A wing, A8 - toilet system leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 16:00:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3557493 | Unit 4 - D Wing Toilet system leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 14:00:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3557495 | Unit 4 - C Wing Toilet system leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 08:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3557497 | Unit 4, A wing, A9 - toilet system leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 09:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3557499 | Unit 4, D wing, D03 - toilet system leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 13:00:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3557501 | Unit 4 - A Wing Toilet system leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 10:30:00 | Pass | Replaced leaking inlet valve in cistern.
MSA-DCS | WA3557506 | Unit 4 - A Wing Door to plumbing duct between cells A03 and A04 won't open. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 11:00:00 | Pass | Open jammed lock, service, replace bolt throw, face plate and fixings.
MSA-DCS | WA3557512 | Unit 4, A wing, A05 & A06 - Door to plumbing duct betwwen cells A05 and A06 won't open | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 13:30:00 | Pass | Unable to open jammed lock, obtain speciality tools, open lock. Service and replace bolt throw.
MSA-DCS | WA3557513 | fron gate house Operation of the ram barrier is not functioning correctly. | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 17 Aug 2020 | 2020-08-17 18:59:56 | 2020-08-17 16:30:00 | Pass | 17/08/20Attend site.Barrier ok.Green traffic light stays on.Cover traffic light.
MSA-DCS | WA3557514 | Unit 4 - A Wing Door to plumbing duct between cells A11 and A12 hits floor when opened. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-09-04 14:00:00 | Fail | DOOR REMOVED/ PLANED DOWN & RE INSTALLED
MSA-DCS | WA3557555 | main gate front sally port doors not opening fully | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 15:42:34 | 2020-08-18 11:00:00 | Pass | 18/08/20Adjusted limits to ensure door opened fully.Workshop hours = load tools, source scissor lift, pick up & drop off scissor lift.
MSA-DFES | WA3556600 | engine room drying room 1 not working – mechanical issue | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 17 Aug 2020 | 2020-08-19 17:00:00 | 2020-10-23 15:00:00 | Fail | Job not completed yet further investigation required when conditions are dry for roof access
MSA-DFES | WA3556604 | Fluro light on left wall of Officers Room arcing when turned on-see notes | CFRS Maddington | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 17 Aug 2020 | 2020-08-19 17:00:00 | 2020-09-18 19:00:00 | Fail | ComepleteOn site and replaced fluros and broken light fitting in base all in working order. Notified staff and signed out
MSA-DFES | WA3556608 | kitchen fluro light faulty | CFRS Claremont | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 17 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-18 08:45:00 | Pass | Replaced faulty lights fluros and starters in kitchen x2 S10 starters and x2 36W fluros.
MSA-DFES | WA3556613 | Ground Various Lights not working-see notes | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 17 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-28 10:30:00 | Fail | Replaced x2 fluros in the fitting in front of the disabled toilet entry and replaced the faulty fluro globe to an LED globe and the light still wouldn’tcome on. Inspected PE cell and the insides of it had rusted and shorted out. Replaced the PE cell, siliconed it up and checked that everythingwas functional. Attended site and investigated faulty light fittings. The light in applied training is un repairable as it is missing its diffuser and has led tubes willreplace with led panel. Ballast in operations delivery is faulty will replace with like fitting
MSA-DFES | WA3557189 | Engine room door 3 has snapped off wires from door sto controller- See notes | CFRS Duncraig | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 10:45:00 | Pass | Engine room door 3 roller door cable has snapped and there is wires exposed. This sort of cable and fault is not something serviced by us, we have inspected it and made it safe and have referred to them the company that services roller door controls and cabling.
MSA-DFES | WA3557391 | Hazmet/rescue storeroom - lights not turning on when entering room-see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 10:45:00 | Pass | COMPLETED
MSA-DFES | WA3557405 | L1 ladies toilets over flowing | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 17:04:00 | Pass | Unblocking the toilet
MSA-DTAG | WA3556874 | 1987 L2 FIP ARA tech to isolate FIP from 16.30pm Monday 17 August - see notes | Supreme Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-18 01:30:00 | Pass | Isolated 1987 building for datatel works. Deisolated when works completed.
MSA-DTAG | WA3556896 | Lift 1 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 20:15:00 | Pass | Found door drive belt had come off, need to put back on, further repair required to be closed out at $0
MSA-DTAG | WA3557465 | Located in magistrates garage - Fluro light unit needs replacing as per direction of the electrician | Rockingham Justice Complex | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 12:15:00 | Pass | Inspected fault and replaced faulty fitting
MSA-DTAG | WA3557470 | level 6, Prisoners Review Board - Water leaking from pipe flange connection | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 15:30:00 | Pass | Quote to be sent to client
MSA-DTWD | WA3556799 | Admin ground Toilets, investigate bad small from toilets | Clarkson Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 10:10:00 | Pass | COMPLETED
MSA-DTWD | WA3556837 | P block ground male toilets the 1st urinal leaking from behind when flushed | Joondalup McLarty Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 14:18:00 | Pass | COMPLETED
MSA-DTWD | WA3556970 | G block/wing L1 G102 staffroom electric tingles/shock being reported- see notes | Leederville Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 15:45:00 | Pass | Arrived at site, signed in ,completed jsa, located sink in g block , spoke to person that received shock about the incident, carried out testing , reported shock to western power to investigate, waited on site for western power electrician to arrive , shock deemed to be from static build up , site deemed safe by western power , cleaned up work area, completed paperwork , signed out ***job completed ***
MSA-DTWD | WA3557005 | Q block, level G, lift Lobby - loud clunking noise when operating | Joondalup McLarty Campus | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 11:55:00 | Pass | CHECKED OPERATIONS FOUND CABLE NEAR GSM UNIT IN THE TOP OF THE SHAFT HANGING ACROSS THE GOVORNER RECTIFIED RAN TEST OK PLACED BACK TO NORMAL SERVICE MONITOR WHILE ON SITE OK ON DEPARTURE.EQUIPMENT RUNNING, BACK TO NORMAL OPERATION
MSA-DTWD | WA3557199 | A block, disabled toilet - toilet blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-21 09:15:00 | Fail | Jet lines and pits
MSA-DTWD | WA3557238 | level 3, Plumbing duct, West - Repair leaking connection | Perth Campus B6 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 12:45:00 | Pass | Fixed leak
MSA-DTWD | WA3557240 | L3 Student male toilet Loose gpo | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 08:00:00 | Pass | Attended site, resecured loose gpo in toilets lvl 3. Job complete
MSA-DTWD | WA3557287 | L1 Student female toilet (W) Damaged gpo | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 07:46:00 | Pass | Attended site, replaced gpo lvl1 female toilets. Tested job complete.
MSA-DTWD | WA3557300 | E block E74 Kitchen – Combi Oven Fan Malfunction – Error Code E 03 | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-18 10:15:00 | Pass | COMPLETED
MSA-DTWD | WA3557469 | Block or Unit: A Block Rear Courtyard Repair umbrella broken | East Perth Campus | GMP-BR | Building | Sunscreens (BU) | AWB Co. | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 09:15:00 | Pass | Attend siteLocate umbrellasInspect and assess damageContact manufacturer and request service quote and etasupply 1of replacement arm bung (to suit CTS43 umbrella) supply 1of corner repair plate (to suit CTS43 umbrella) Labour (inc. call out)
MSA-DTWD | WA3557471 | P block main entrance Damaged glass 1st panel RH side entry. | Midland Campus | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-20 09:59:00 | Pass | ATTENDED SITEREGLAZED BROKEN WINDOW6.38 CLEAR LAMINATED SAFETY GLASS1-1053 X 770PLUS SILICONE
MSA-DTWD | WA3557476 | Admin building fire panel needs to be reset after alarm activation | West One Services | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 16:00:00 | Pass | Device had been trigered last week by toast. Reset sustme and returned to full function
MSA-DTWD | WA3557482 | D block, plant room - Chilled water pump and motor noisy | Midland Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-18 16:00:00 | Pass | Attended call checked chiller pump in d block , found pump Check's ok but motor is noisy & requires replacement. Further works submitted on DAS.
MSA-DTWD | WA3557515 | Campus Ringroad - There is pothole developing in the ringroad NW corner near Automotive carpark. | Midland Campus | GMP-BR | Paving & Roadworks | Asphalt (PR) | MR POTHOLE | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 10:55:00 | Pass | job completed - repaired asphalt in 2 locations
MSA-DTWD | WA3557559 | B Block, level 2, B225 - projector has fallen down, repair to broken classroom projector screen | Leederville Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 2 | CLOSE | 17 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-19 14:30:00 | Pass | Attend siteFacilities on leaveGot keys from student adminLocate room and projectorBracket come away and fixings has failedGot ladder and tools neededRe drill holes fit new plugs and secure bracket to wallHang projector screen and testPack up clean up
MSA-DTWD | WA3557562 | Level 6, Boiler room L6 - gas boilers not heating properly | Perth Campus B1 | GMP-BR | Mechanical Services | Boilers (MS) | Equans Mechanical Services Australia | 3 | CLOSE | 17 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 16:36:00 | Pass | Boiler tech attended site. Help with access to equipment and inspection. On investigation boiler low flame hold relay was found active. Moved back to high flame control and equipment was monitored. All control relays were checked and confirm as operating properly. As switch is external to unit is may have been unknownly bumped by a contractor or someone working in the area causing low flame hold to engage leading onto low hot water temps. Boiler tech has confirmed equipment is operating correctly and no further faults present. Work area left tidy. Temps maintaining 62deg
MSA-MRWA | WA3556949 | L2 Female toilet Full Flush in cubicle not working, please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 17 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-17 15:10:00 | Pass | Replaced faulty wahsers in the cistern
MSA-DCA | WA3564426 | State Theatre Centre-Air quality testing due to mould-main practise Area-Rehersal Studio | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 1 | GMP-BR | Cleaning | Cleaning (CL) | Site Environmental & Remediation Services Pty Ltd | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 17:00:00 | 2020-09-18 14:57:00 | Fail | Works completed 19/08/2020 emailed works to Reese Withey 31/08/2020
MSA-DCS | WA3557662 | L3 large kitchen area near lift Strong odour coming from sink | East Perth | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-18 12:30:00 | Pass | Complete
MSA-DCS | WA3557699 | Jeelia office front office door has dropped on hinge affecting closing | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 2 | CLOSE | 18 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-31 08:00:00 | Fail | DOOR HINGES RE SECURED
MSA-DCS | WA3557850 | Unit 7 - A Wing Glass Skylight has smashed | Casuarina Prison | SPA-BR | Building | Windows (BU) | Midolo Building Services | 0 | CLOSE | 18 Aug 2020 | 2020-08-18 12:14:21 | 2020-08-25 15:00:00 | Fail | REPAIRS TO ROOF/SKYLIGHTS
MSA-DCS | WA3557954 | Serpentine cell 06 light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-20 09:00:00 | Pass | Repaired light
MSA-DCS | WA3558041 | Social visits - Roof leaking down the center in various places | Hakea Prison | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 09:02:00 | 2020-08-18 14:30:00 | Pass | VARIOUS ROOF LEAKS REPAIRED
MSA-DCS | WA3558062 | Perimeter - microwave tamper is faulty | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-18 19:00:00 | Pass | Attended site and realigned and reset microwave set and replaced with new End of Line resistor. All replaced and tested working ok. Job complete Travel home
MSA-DCS | WA3558082 | Unit 5, Cell A6 - broken window slider frame. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 14:15:00 | Pass | SPIRAL BALANCES RENEWED
MSA-DCS | WA3558191 | Unit 5, B wing - shower window ribbit snapped | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 15:00:00 | Pass | NEW SPIRAL BALANCES INSTALLED
MSA-DCS | WA3558193 | Unit 1 - D Wing shower window has dropped | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-09-02 10:00:00 | Fail | RE FIX WINDOW FRAME AND RE SEAL
MSA-DCS | WA3558199 | unit 1 ablutions exhaust fan not workig over shower | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-20 13:30:00 | Pass | Investigate and Replace Unit 1 Toilet Exhaust Fan
MSA-DCS | WA3558201 | amenities, whole unit - no heating | Casuarina Prison | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-19 15:30:00 | Pass | Replaced defrost thermostat all ok
MSA-DCS | WA3558206 | WWTP mixer pump conduit broken | Karnet Prison Farm | GMP-BR- HO | Mechanical Services | Pumps (MS) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-20 15:00:00 | Pass | Investigate and repair WWTP mixer conduit
MSA-DCS | WA3558210 | Unit 13, C4 - shower screen leaking | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-31 13:00:00 | Fail | SHOWER SCREEN RE SEALED
MSA-DCS | WA3558216 | Unit 13 - B7 shower silicon leaking | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-31 12:00:00 | Fail | DOUBLE UP - WORK COMPLETED ON WA3580830
MSA-DCS | WA3558227 | gatehouse, POD - Camera 86 - looks like its in night vison mode, | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Aug 2020 | 2020-08-18 13:47:51 | 2020-08-18 12:45:00 | Pass | Camera 86 is PTZ 1 which is due for replacement and to be completed through WA35027341.
MSA-DCS | WA3558246 | Unit 1, cell B24 - Desk light broken | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-20 12:00:00 | Pass | Investigate and repair Unit 1 Cell 24 Light
MSA-DCS | WA3558256 | Kitchen - light fitting not working over salad prep area | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-20 10:30:00 | Pass | Investigate and repair kitchen light
MSA-DCS | WA3558369 | Sentence planning kitchen - sink taps broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-25 11:00:00 | Pass | COMPLETED
MSA-DCS | WA3558786 | Level 1 – lights are out in the main reception area | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 15:00:00 | Pass | Repaired lighting on level one reception area.
MSA-DCS | WA3558872 | Level 3 – the light globe has gone in the hanging light in the kitchen area | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 12:00:00 | Pass | Repaired lighting on level three.
MSA-DCS | WA3559056 | Level 4 – a light is out in the main floor area; a light is out in the shower in the ladies toilet | East Perth | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 11:00:00 | Pass | Repaired lighting on level four.
MSA-DCS | WA3561385 | unit 4 office door lock faulty | Karnet Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 11:05:00 | Pass | Attended site, replaced wornout lockbody and adjusted strike plate.Date on site: 24/08/2020Time on site: 10:05am - 11:05am
MSA-DCS | WA3562358 | recreation main gym storm damage to verandah roof | Wooroloo Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 10:39:34 | 2020-10-08 13:31:00 | Fail | REPAIRS TO FLASHINGS, GUTTER AND ROOF SHEETING
MSA-DCS | WA3562474 | Storage dam clorine alarm faulty | Wooroloo Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-21 12:41:00 | Pass | First visit 19/08/2020. Fault identified, return visit required to remedy fault.Returned 21/08/2020. Installed receiver module, transmitter and gas generator
MSA-DCS | WA3563327 | Cyrenian demountable water pump not working under sink | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-25 14:30:00 | Pass | Renew sani lifting station
MSA-DCS | WA3563934 | SOG Base, male toilets, conference room 2 - toilet faulty | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 11:18:35 | 2020-08-18 19:30:00 | Pass | Unblocked sewer line full of roots.
MSA-DCS | WA3564007 | video links - access doors lock faulty allowing prisoners to enter | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-19 09:50:00 | Pass | Reconfigured lock on door to Video Link Door to be key entry only and free to egress internal
MSA-DCS | WA3564044 | Unit 9, B16 - Sink is cracked in two and coming away from the wall and needs replacing | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 12:22:32 | 2020-08-18 18:30:00 | Pass | Removed Broken basin replaced with new wall hung and repaired and adjusted pipework and copper set
MSA-DCS | WA3564054 | Unit 7, S3 - faulty light switch | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-19 10:00:00 | Pass | Replaced light switch
MSA-DCS | WA3564057 | Reception - Downlight faulty above senior officers office is faulty Scissor lift required | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-28 12:00:00 | Fail | Repaired lights
MSA-DCS | WA3564065 | Kitchen - Day Room HW urn tripping power | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-25 13:04:00 | Fail | NICOLAS DEGRYS WAS WORKING ON THE WRONG WORK ORDER NUMBER SO THESE COMMENTS ARE NOT ABOUT THIS SYSTEM THIS WO SHOULD HAVE BEEN LEFT OPEN Restarted at 9.50am 25/08/2020Replaced corroded tap on unit causing boiling water to go everywhere when dispensing. Work completed at 10.35am 25/08/2020ATTENDED 20.8.2002 DIAGNOSED ORDERED SPECIAL PARTS IN ELEMENT AND PCB HAD NOT BEEN TO THIS UNIT PREVIOUSLY PARTS HAD TO BE ORDERED IN RETURNED ON 9.9.2020 AND REPLACED ELEMENT AND PCB CONTROLLER BILLI ULTRA
MSA-DCS | WA3564067 | Unit 9, A3 -cell call faulty | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 12:40:35 | 2020-08-18 15:30:00 | Pass | Replaced damaged cell call and rectified the faulty cable. Job completed
MSA-DCS | WA3564068 | Dairy HW controller not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 12:40:30 | 2020-08-25 12:00:00 | Fail | No controllers In Perth have order one from melboure getting it air bagged over.17,8,20 completed.
MSA-DCS | WA3564078 | kitchen Hot box thermostat faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 12:45:17 | 2020-08-19 10:30:00 | Pass | Replaced Digitemp thermostat and set new temp, test ok.
MSA-DCS | WA3564133 | Unit 1 A12 Keys getting stuck in the prisoner door lock | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 13:11:57 | 2020-08-19 16:00:00 | Fail | 18/08/2020. Assessed issue and determined repair not possible, needs replacement.19/08/2020. Replacement lock fitted.
MSA-DCS | WA3564205 | Unit 1 D wing day room lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 13:44:22 | 2020-08-18 16:45:00 | Pass | Repaired and serviced lock. Replaced broken component to restore normal function.
MSA-DCS | WA3564240 | Lenard, B05 - light switch broken | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-20 11:30:00 | Pass | Replaced light switch
MSA-DCS | WA3564318 | Unit 2, A/C - eletrical On/off switch for the urn plug on A/C side has been pushed into the unit | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-19 15:00:00 | Pass | Replaced faulty gpo in unit 2
MSA-DCS | WA3564370 | perimeter cameras - not responding to alarm | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 18 Aug 2020 | 2020-08-19 00:08:57 | 2020-08-19 19:47:00 | Fail | Issues with alarms not displaying, checked gallagher and confirmed alarms, confirmed HLI working as alarms active in Indigo.Issue with site DB, merged both Site DBS and reprogrammed users
MSA-DCS | WA3564404 | Unit 2, B/D dayroom - hot water will not turn off | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 18 Aug 2020 | 2020-08-18 20:44:52 | 2020-08-18 19:30:00 | Pass | Attended job. Replaced broken hot spindle that would not turn off.
MSA-DFES | WA3557943 | security alarm activated late last night all zones are flashing - see notes | DFES Baldivis | GMP-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-18 10:30:00 | Pass | Replaced 2 x 12v 7ah battery
MSA-DFES | WA3563917 | Engine room water leaking through ceiling through the cornise and ceiling space | CFRS Maddington | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-21 13:15:00 | Fail | Carried out roof repairs and applied stain block to ceiling
MSA-DFES | WA3564022 | Engine room and awning, yard ground -Fix broken lights in engine bay and replace with LED, only the | CFRS Daglish | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-09-17 14:45:00 | Fail | Arrived on site at 13:10 to inspect FS garage lights. Job needs 12ft ladder access. There are 3x 4ft Fluros fittings getting replaced for LED, 4x 5ft fittings to LED and 1x wall mounted walk way light. Signed out at 14:15
MSA-DFES | WA3564130 | Engine room Bay - engine room door will not close properly, electrical fault | CFRS Perth | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 18 Aug 2020 | 2020-08-18 17:08:52 | 2020-09-08 14:00:00 | Fail | Removed damaged curly cable , replaced with new. Complete as per quoted works.
MSA-DFES | WA3564286 | 27 engine room yellow steel post at each end of engine room rusting- see notes | CFRS Midland | GMP-BR | Building | Steel Work (BU) | AWB Co. | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-19 13:15:00 | Pass | Inspect and measure to submit braf. Declined.
MSA-DTAG | WA3560971 | L4 public waiting area Fixings are loose on numerous amount of chairs-see notes | Central Law Courts | GMP-BR-HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 08:00:00 | Pass | ALL SEATING SECURED
MSA-DTAG | WA3561695 | L5 judicial door duress alarm room 5.06 activates by itself and then stops beeping by itself | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 17:00:00 | 2020-09-02 13:00:00 | Fail | Repaired in-session button, by replacing with part from van stock.Tested, all OK.
MSA-DTAG | WA3563971 | Level 8 - Public entry door to Court 81, inner vinyl door panel is separating, needs to be re-attach | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 09:30:00 | Pass | DOOR PANEL RE ATTACHED
MSA-DTWD | WA3557675 | B and C block alarms going off about 4 times a week could be faulty sensors | Munster Campus (ACEPT) | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 18 Aug 2020 | 2020-08-18 17:00:00 | 2020-08-19 09:50:00 | Fail | 18/08/2020, 940-1030According to monitoring zones 7, 115, 147 are going into alarm.Replaced zone 7need a 360 to replace 115and 147 doesn’t exist and was a type 00 I changed it to a 10 spare.19/08/2020, 915-950Replaced zone 115 360 pir.
MSA-DTWD | WA3557949 | Bowling Green spot light the RCD Blue 2 is dripping out. | Murdoch Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-31 15:00:00 | Fail | Attended site and signed in. Located greens lighting control and found B2 tripping when turned on. Investigated to find furthest pole on circuit to have fault in head. Lights are in the bushes and not on the greens. Isolated fault and found lights on poles to be out. Middle pole has 1 light out. End pole has 1 out on other side. Will need ballasts ignitors and globes for 400w sodium lamps. Or replace to 200w led flood lights. Mike said leave them. Upon leaving site found that the reported circuit tripping was not the one mike wanted fixed. Went back with mike and found that 2 other circuits after being on won’t reset. Need more time to return and identify fault. Lights he wants to work are the poles in the middle of the back section facing east. Job not complete 31/8 repalced 2x faulty lights with led fittings .job completed
MSA-DTWD | WA3557959 | Childcare carpark No power to main bore pump | Rockingham Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | LD TOTAL | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-19 10:30:00 | Pass | ATTENDED SITE NO POWER TO IRRIGATION. RESET CIRCUIT BREAKER IN SWITCH ROOM RAN PUMP FOR 10 MINUTES DIDN'T TRIP OUT AGAIN
MSA-DTWD | WA3557968 | F block security light that will not go out in the main walkway | Murdoch Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-21 14:30:00 | Pass | Attended site and signed in. Located F block and light staying on. Tested all lighting control and found in switchboard overtire for f block to be on. Labelled and turned off for auto mode. Tested auto mode and all works properly. Job complete
MSA-DTWD | WA3558020 | K block yard Bore pump has low pressure | Rockingham Campus | GMP-BR | Landscaping & Gardening | Grounds Maintenance (LG) | LD TOTAL | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-19 12:15:00 | Pass | TEST SYSTEM LOCATE MAINLINE LEAKS REPAIR DAMAGED MAINLINE, TEST OK OK
MSA-DTWD | WA3558066 | UO24 banks of fluro light constantly tripping | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-19 10:00:00 | Pass | Replaced faulty light fitting. Job completed
MSA-DTWD | WA3558075 | U008 2x roof leaks - 1 over bench 2 - and 1 over bench 37 | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-18 15:00:00 | Pass | found flashing around support with split silicone, carried out repair . Bench 37 - found 2 dektites with split silicone and repaired
MSA-DTWD | WA3558089 | U024.8 roof leak at the doorway entrance | Balga Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-18 13:00:00 | Pass | Investigated area above suspected leak, found large steel support rod flashing with split silicone/ carried out repair - also found A/C flexiduct is perished and needs replacing
MSA-DTWD | WA3558305 | D block L1 entry Remove broken concrete bench and dispose of | Leederville Campus | GMP-BR | Furniture | Outdoor Furniture (FU) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-20 07:45:00 | Pass | Locate d blockLook for bench seatConfirm removing and not repairingWill need to break seating upWhen not busy around entranceReturn 1st thing Thursday 20/8With empty van and before classes commenceAttend site unbolt timber seatingRemove concrete seatClean up and take back to the yard to dispose of
MSA-DTWD | WA3563549 | block 3 Water leak in passageway outside 3D | Thornlie Campus | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-21 13:30:00 | Pass | Leak resolved and confirmed by site
MSA-DTWD | WA3563899 | block 3B Hot water unit not working in automotive washroom | Thornlie Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AWB Co. | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 11:30:00 | Pass | Arrived on site, signed in , located hws , completed jsa, isolated power, isolated water , drained tank , disconnected thermostat, removed element, fitted new element, fitted new thermostat, filled up tank , replaced fuse in db, reenergised circuit , rested water , it is hot , cleaned up work area , ***job complete***
MSA-DTWD | WA3563904 | Level 1, main roller door locked open - This is a brand new system & has done this twice | Perth Campus B1 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-18 15:19:00 | Pass | 1078023, arrived onsite and inspected unit and found controller in error code 7, stating maximum run time had been achieved, inspected safety beams and found the TX had a internal bracket broken causing the beams out of alignment, removed beam and repaired it. Reinstalled beam, reset controller and tested operation numerous times and could not fault. Would suggest to replace the repaired beam in the near future, the beams are a Grifco 772 two wire type.
MSA-DTWD | WA3563913 | A block, level 3, A338 - door lock isnt working to inner store | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 11:45:00 | Pass | service lock and adjust strike plate to A338 storeroom
MSA-DTWD | WA3563959 | Room D17 Faulty lighting motion sensor | Rockingham Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-20 14:15:00 | Pass | Attended site and signed in. Located D block and room 17. Found lights to not turn on. Tested sensor to be cactus. Replaced with new infrascan sensor. Rewired to suit. Tested all okay. Job complete Start actual time is incorrect. Promap app lagged out and selected time. Actual start 1.15pm
MSA-DTWD | WA3564008 | Jandakot annexe staff entry Staff electronic door will not lock. | Jandakot Campus - Annex | GMP-BR | Security | Access Control (SE) | Securex Security Systems & Services | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-18 14:00:00 | Pass | 18/08/2020, 1340-1400Locksmith required. Strike ok. Handles tongue wont go in without the door sensor open and it’s sticky and staying closed, I’ve wedged paper into the mechanism so it thinks the door is open so the tongue becomes loose and the door can close.
MSA-DTWD | WA3564110 | K block K05 Walk-in freezer is not working correctly | Midland Campus | GMP-BR | Refrigeration | Freezers (RE) | Precise Air Group | 1 | CLOSE | 18 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-28 15:00:00 | Fail | Re-attended site after evacuation was completed, gased system accordingly,tested operation and left all operational
MSA-DTWD | WA3564142 | BLD 834, Computer room - Leaking roof | Muresk Institute | GMP-BR | Building | Ceiling (BU) | Lee Carpentry | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-19 10:00:00 | Pass | Repairs to roof leak
MSA-DTWD | WA3564230 | A block, Level 2, A239 - faulty lights, replace light tubes | Leederville Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-21 09:15:00 | Pass | Arrived on site, signed in, located light, completed jsa, setup work area, isolated lighting, removed old tubes and starters, replaced with new ,tested light and now fully operational , cleaned up work area, completed paperwork , signed out ***job complete***
MSA-DTWD | WA3564236 | Customer service - collapsed hinges on salon door, door is difficult to open | Armadale Campus - 40 Commerce Ave | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-09-11 16:00:00 | Fail | Have removed saloon door and carry out repairs to the wall and carpet
MSA-DTWD | WA3564250 | carpark - sinking paving | Perth Campus B6 | GMP-BR | Paving & Roadworks | Concreting (PR) | AWB Co. | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-20 12:00:00 | Pass | Relayed sunken pavers.
MSA-DTWD | WA3564317 | building 2 - Water leaking down external wall outside disable toilet | Thornlie Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-09-01 12:00:00 | Fail | reseal flashing and replace fixings. Leak has been checked after rain on the 1/10 and leak has stopped.
MSA-DTWD | WA3564327 | A Block, level 3, A354 passageway entry/ramp - roof leak in passageway to Corp Services Office | Leederville Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 3 | CLOSE | 18 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 15:15:00 | Pass | Sourced leak and replaced roof tiles.
MSA-DTWD | WA3564333 | K block, K02 - Repair/replace 2x fly zappers in the Canteen kitchen | Midland Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 18 Aug 2020 | 2020-08-21 17:00:00 | 2020-09-09 12:30:00 | Fail | Attended site, located zappers ,completed jsa, set up work area , removed old fly zappers , moved fixings to suit new zappers , installed new zappers , tested zappers , all working , cleaned up work area , completed paperwork **job complete***
MSA-DCS | WA3566450 | Jeelia A3 sink tap linking | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-20 16:05:00 | Pass | Replaced leaking spindle in the basin
MSA-DCS | WA3566482 | unit 3 D wing burner on gas cook top broken | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 19 Aug 2020 | 2020-08-25 17:00:00 | 2020-09-10 09:30:00 | Fail | Unit 3D Wing burner on gas cook top broken. Remove broken parts. Order & pick up new burner. Return & install. All working.
MSA-DCS | WA3566532 | Education front door will not lock | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 07:49:54 | 2020-08-20 11:15:00 | Fail | 19/08/2020 - Attended site. Performed repairs to restore some function, but replacement lock needed.20/08/2020 - On site. Replaced lock to restore normal function. Door itself may need repairs. Site advised.
MSA-DCS | WA3566584 | Unit 1 D9 prisoner lock jammng | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 08:13:03 | 2020-08-19 16:15:00 | Pass | Supplied and fitted new lock to replace faulty unit.
MSA-DCS | WA3566589 | Unit 1 D11 door jamming on frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 08:16:46 | 2020-08-19 15:30:00 | Pass | Adjusted hinges to restore normal function.
MSA-DCS | WA3566594 | Manitenance Lunch Room Boiling water unit requires service as water tastes fowl. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 13:13:00 | Pass | Restarted work at 10.35am 25/08/2020As per request. Installled filtration system to the boiling water pou unit. Completed work at 10.55am 25/08/2020INSTALLED NEW CAPEX ASSET MAXIFLOW SCALE FILTER SYSTEM CONNECTED TO EXISTING BWU A40191318G
MSA-DCS | WA3566608 | Unit 2 - A & C toaster faulty tripping power. | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 13:30:00 | Pass | Replaced damaged gpo and toaster lead in unit 2
MSA-DCS | WA3566670 | Unit 1 C-D Wing Programmes room – Store Room Broken GPO ,Light Switch & Data Point | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 10:00:00 | Pass | Investigate and repair unit 1 c & d programs room gpo, data point and light switch
MSA-DCS | WA3566704 | Unit 2,A-B wing airlock & end of B wing - lights not working x3 | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 15:00:00 | Pass | Investigate and repair unit 2 b wing airlock and wing lights
MSA-DCS | WA3566707 | Unit 2, C-D wing airlock & end of wings - lights not working x4 | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 13:00:00 | Pass | Investigate and repair unit 2 c&d airlock and wing lights
MSA-DCS | WA3566710 | Unit 1, C-D wing airlock & end of D wing - lights not working x3 | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 11:30:00 | Pass | Investigate and repair unit 1 c & d airlock and d wing lights
MSA-DCS | WA3566739 | education verandah lights not working in one section | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 14:30:00 | Pass | Replaced faulty timer
MSA-DCS | WA3566774 | Unit 4, Court yard - Turnstile buzzer is playing up - stays on and having to constanlty reset it | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 15:30:00 | Pass | Attended unit, found Turnstile not returning to “Home” position when switched off “Free wheel”. I found the Turnstile stiff to rotate and the base ball race dry. Regressed the roller baring using grease gun via grease nipple at baring location. Worked grease thru baring and noted an improvement on rotary motion. Turnstile now returning to home correctly.
MSA-DCS | WA3566852 | Termites active in bathroom vanity. Require treatment to slab under vanity and perimeter treatment | Boronia Pre-release-AP08 - Prisoner Accommodation House 16-Ground Floor-Bedroom 4 | GMP-BR- HO | Pest Control | General Pest (PC) | High Tech Pest Control | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 12:00:00 | Pass | Termite treatment installed as per report
MSA-DCS | WA3566859 | Karakin A wing, common area - 2x broken ceiling fan switches | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 10:30:00 | Pass | Replaced fan controllers
MSA-DCS | WA3566876 | MPU (8), control room - CCTV monitor and recording device for M17 has damaged cables | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 09:30:00 | Pass | BNC cable connection damaged due to location of DVR on Desk. Repaired BNC plug. Returned next day with angle brackets to relocate DVR to side of Desk to prevent further damage. Installed Rawl plugs into holes drilled into concrete, screwed in brackets and mounted DVR, install additional bracket at top of DVR to prevent movement. Reconnected cables and confirmed operation.
MSA-DCS | WA3566887 | front of of property 2x wooden fence post damaged | Warminda Hostel | GMP-BR- HO | Carpentry | Timber Fencing & Gates (CA) | Schlager Construction Group | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 14:30:00 | Pass | Attended site and carried out repairs to the damaged timber fence posts located at the front of the property.
MSA-DCS | WA3566889 | Unit 7, C wing, Kitchen round sink spout leaking, needs new seal | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-20 15:00:00 | Pass | Replaced leaking oring in kitchen tap.
MSA-DCS | WA3566899 | Unit 13 - C13 Personal lock broken | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 12:00:00 | Pass | Replace mortise lock and install offset strike plate.
MSA-DCS | WA3566901 | unit 1, B wing, courtyard - camera not working camera 33 | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 10:54:12 | 2020-10-13 15:42:00 | Fail | Installed and programmed replacement Indigo BX Dome Camera.Tested OKParts (SEME Stock):1 x Indigo fixed dome.Consumables
MSA-DCS | WA3566903 | Security Area - Office Footage required for download. Gatehouse 13.08.2020 | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-19 13:00:00 | Pass | Downloaded required video and provided to Security staff
MSA-DCS | WA3566922 | control camera 28 poor image - SEME on site | Albany Regional Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-11-20 16:30:00 | Fail | Installed IndigoVision Encoder (PFM Stock) in Camera EC, installed N/W switch and patch cables and SFPs to connect signally digitally back to Gatehouse. Improved picture.
MSA-DCS | WA3566925 | control gallagher network swtich fail- SEME on site | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-10-23 14:30:00 | Fail | Installed replacement Network switch
MSA-DCS | WA3566965 | Unit D6 water leak from ceiling | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-11-25 09:00:00 | Fail | SOURCE OF LEAK LOCATED & REPAIRS CARRIED OUT
MSA-DCS | WA3567020 | Education Library power issue - contractor on site | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-19 13:30:00 | Pass | Remove damaged GPO and Make safe
MSA-DCS | WA3567021 | Ground floor, Male toilet - urinal continuously running | Warminda Hostel | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 11:51:13 | 2020-08-20 10:15:00 | Pass | Complete
MSA-DCS | WA3567111 | Unit 4, B/D - door handle is missing on wing door. | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 13:00:00 | Pass | JOB DOUBLE UP OF WA3500114- COMPLETED ON 24/08/2020
MSA-DCS | WA3567238 | Unit 1, D7 - The striker plate is coming away from the door frame and needs to be secured (welded) | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 10:30:00 | Pass | Unable to complete due to no available officer - arranged for 21/08/2020.Cut off broken strike plate and weld on new plate.
MSA-DCS | WA3567254 | Unit 4, K block - kitchen tap is leaking heavily - turn off its fully running | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 12:21:36 | 2020-08-19 16:15:00 | Pass | COMPLETED
MSA-DCS | WA3567257 | Main kitchen - HOT Box - temposat not working and seals damaged, not closing properly | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 12:23:17 | 2020-08-27 14:10:00 | Fail | Returned 27/08 & replace section of doorseal ok
MSA-DCS | WA3567280 | Entry building - 4 blown lights | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 14:30:00 | Pass | Replaced led oysters
MSA-DCS | WA3567357 | Laundry, NO 4 washing machine - leaking water | Hakea Prison | GMP-BR- HO | Equipment | Cleaning Equipment (EQ) | COMMERCIAL LAUNDRY SOLUTIONS | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 12:55:05 | 2020-09-04 14:28:00 | Fail | No 4 WM Leak - Attend site and determine soap flush water baffle broken. Return to workshop.Collect new baffle, return to site , fit new baffle and test O.K
MSA-DCS | WA3567454 | Unit 15 Fire system Please check sampling points | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 13:53:56 | 2020-08-20 11:58:00 | Pass | Attended site and found the following.1: only able to check one cell but found grill already badly blocked with lint will require cleaning on a weekly basis otherwise flow problems will occur.2: Found very easy to block sample point with a sheet of paper easier than units 13,14.3: Found on main panel in Cript that description doesn’t include unit number, just cell number wing and zone. Also no block plan showing where zones are.4: Found the following devices Disabled for unknown reason.Devices 2103,2095,2090,6105 and 8102 (all MASD) re enabled and left normal.Staff mentioned that they had no training on the panels and didn’t really understand them at all as different to other systems on site.5: Found the following devices is missing fault.12050,12049,12046,12045,12051,12048,12047 and 12044 ( all MASD )As no information as to what units the faults are in possible in units 17 & 18 and no access as still under builders control.Left these devices disabled.6: Also noticed t
MSA-DCS | WA3567458 | reset centre, Creche - toilet blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 13:51:33 | 2020-08-20 08:48:00 | Pass | Drain line blocked drain machine used to clear 20 meters off blockage
MSA-DCS | WA3567463 | Unit 5, C wing, Dayroom - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 10:30:00 | Pass | Repaired light
MSA-DCS | WA3567473 | Social Club Forecourt, walking path to carpark - Lid to Pit damaged (Demarcated by cones at Present) | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 13:30:00 | Pass | INSPECTED AND ASBESTOS TESTED - ADVISED ITS A TELSTRA PIT SO WE CAN NOT REMOVE/FIX/REPLACE
MSA-DCS | WA3567477 | Back Hallway Staff Entry Faulty door in hallway not closing properly. | Walcott Centre (Central West Metro ) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 10:30:00 | Pass | Attended site and replaced damaged hydraulic closer on hallway door.
MSA-DCS | WA3567486 | Disable toilet faulty vent on door | Walcott Centre (Central West Metro ) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 11:30:00 | Pass | Attended site and carried out repairs to the damaged vent on disabled toilet door
MSA-DCS | WA3567499 | Unit 3 - C4 toilet not flushing properly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 08:30:00 | Pass | Remounted cistern to wall and tested flushing mechanism.
MSA-DCS | WA3567515 | Education, lunch room - faulty door handle/ locking mechanism requires attention | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 14:30:00 | Pass | Repair and lubricate lock.
MSA-DCS | WA3567517 | Unit 16 Airlock entering B/D wing from outside, part of steel frame near inner door is coming apart | Casuarina Prison | GMP-BR- HO | Building | Security Doors (BU) | Midolo Building Services | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-10-06 14:00:00 | Fail | NEW DOOR SEAL FITTED - COMPLETE
MSA-DCS | WA3567565 | Gatehouse, perimeter Zone 8 & 9 - problem with the internal microphonics | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 15:14:02 | 2020-10-01 11:24:00 | Fail | Opened Inteliflex cabinet, small water residue at base of cabinet, cleaned and sealed.No water damage to controller as controller mounted high.Tested fence zones and confirmed correct operation
MSA-DCS | WA3567592 | Reception, main entry doors - is permanently locked unable to be unlocked | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 19 Aug 2020 | 2020-08-19 20:03:55 | 2020-08-19 17:30:00 | Pass | Attended site. Forcibly gained entry and replaced broken lock. Normal function restored.
MSA-DFES | WA3566761 | dorm 6 - air con not working correclty and motor making nosies | CFRS Perth | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-19 14:00:00 | Pass | Fixed vibration noise issue with ac dorm 6
MSA-DFES | WA3566827 | Boiler Start Failure HVAC to attend | DFES Cockburn Emergency Services Complex | GMP-BR | Mechanical Services | Boilers (MS) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-09-09 12:00:00 | Fail | Completed boiler service repairs as per service report.All appears to be functioning satisfactory.
MSA-DFES | WA3567605 | front transportable toilets - the balustrade on the right hand side of stairs, has loose riverts | FESA RHQ - Forrestfield | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 12:00:00 | Pass | Installed new fixings to re-secure balustrade
MSA-DFES | WA3567606 | Main admin building, the superintendents office is getting hot compared to the rest of the office ar | FESA RHQ - Forrestfield | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-10-01 12:00:00 | Fail | Pick up equipment for required works. Attend site. Sign in. Access area and remove ceiling tiles. Locate duct and cut in half. Install new inline damper and reconnected duct. Relocate temperature sensor to a better location. Carry out air balance of system. Found out that this area was originally an open plan. Now added to this area is two perimeter offices, meeting room and interior/ perimeter open area. Also a wall between twi open plan areas has been taken out. There a 3 different heat loads that are going to be affected differently. We have carry out the best adjustments to the system as possible. Temps accross the floor are even at present. Slight adjustments of temperature setpoint might be required into summer months.
MSA-DTAG | WA3566664 | ground security office Fault in fire panel for Basement Carpark-see notes | Perth Children's Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 19 Aug 2020 | 2020-08-19 12:57:29 | 2020-08-19 11:00:00 | Pass | COMPLETED
MSA-DTAG | WA3566797 | Juryroom exit door - faulty hinges, need repairing/replacing | Rockingham Justice Complex | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-19 13:00:00 | Pass | FITTED NEW BOTTOM HINGE
MSA-DTAG | WA3566894 | Elec burning smell coming from power points at work station | Rockingham Justice Complex | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 0 | CLOSE | 19 Aug 2020 | 2020-08-19 14:44:49 | 2020-08-19 12:45:00 | Pass | Inspected burning smell to office and found fault to be powerboard hotpoint - removed and tested all working
MSA-DTAG | WA3567393 | Level 7 office space temp high worst spaces are rooms 7.1 and 7.2. | Central Law Courts | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 16:00:00 | Pass | Attend site. Check level 7, rooms 7.1 and 7.2 too hot. Check temps accross floor and found to be 24 degrees. Check vav box setpoints and found to be 23.5. Adjust setpoints to 22.5, found heating damper to close and cooling damper to open. Check vav box operation across floor and found to work as normal. Access lev 7 and check temps. Found area to now be 23 degees. Ac working as normal.
MSA-DTAG | WA3567427 | Judge Quail’s bathroom Toilet always running | Perth Children's Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 14:50:00 | Pass | replaced with new dual flush inlet valve and foam seal
MSA-DTWD | WA3566516 | Staff area faulty lock on security door | Jandakot Campus - Annex | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 19 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-20 15:25:00 | Pass | Replaced door lock
MSA-DTWD | WA3566527 | A block ground West End Diabled toilet water coming up through floor vent when flushing | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 19 Aug 2020 | 2020-08-19 17:00:00 | 2020-08-19 09:30:00 | Pass | unblocked toilet through dg
MSA-DTWD | WA3566602 | G block male toilets Toilet doesn’t flush properly and therefore gets blocked | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 12:59:00 | Pass | Fix toilet issues
MSA-DTWD | WA3566614 | D-Block G/Floor Canteen area, replace all blown ceiling lights | Joondalup Kendrew Campus | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 14:30:00 | Pass | Pickup new globes on the way to site, then start replacing globes. Had issues with some light with no power but after tracing back i found it going back to a hidden switch in a seperate room which was off. One light kept falling down after i change the globes due to the clips holding it up to be broken. Sourced replacement light to fit in cut out and return to replace.
MSA-DTWD | WA3566653 | A block A19 student services office heating not working correctly | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 14:45:00 | Pass | Found heater bank 3 tripped safety due to power failure. Reset and checked operation. All ok.
MSA-DTWD | WA3566655 | Block 8 First floor 8F55 door lock damaged & wont accept key | Thornlie Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 1 | CLOSE | 19 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-19 11:00:00 | Pass | Block 8 -8F55 - lock damaged.Lock repaired/replaced.
MSA-DTWD | WA3566711 | U018 emergency exit light not working-AWB on site | Balga Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 13:00:00 | Pass | Check exit signs to U0018. All woekimg fine.no action taken
MSA-DTWD | WA3566713 | U017.2 flickering fluro - AWB on site | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 12:30:00 | Pass | Replaced fluros in room.job completed,
MSA-DTWD | WA3566731 | BLD 823 and BLD 817 Seals faulty on toilets | Muresk Institute | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Lane's Plumbing | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-19 12:30:00 | Pass | Job completed - replace faulty seals to toilets
MSA-DTWD | WA3566741 | T block fans in Hairdressing rooms T038, T040 & T042 be checked as they are not working correctly. | Murdoch Campus | GMP-BR | Electrical | General Electrical (EL) | Equans Mechanical Services Australia | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-10-28 08:54:00 | Fail | Found exhaust systems not turned on at switch in rooms and run times very short. Air quality being tested and further works required to adjust run times. Work request to be submitted.attended site Friday 28.8.20 to complete air quality test.We attended site Friday 28.8.20 to complete air quality test. Test results sent to site Fm and andrew crawford.Braf Submitted and completed works by relay controls
MSA-DTWD | WA3566912 | Students male toilet Toilet pan inlet leaking when flushed | Kwinana Automotive Centre | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-20 14:00:00 | Pass | Fixed leaking flush pipe
MSA-DTWD | WA3567370 | B block BG25-Small capillary airline that operates locking system - see notes | Carlisle Campus | GMP-BR | Electrical | General Electrical (EL) | Precision Automotive Equipment/Bapcor | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-26 08:30:00 | Fail | Repairs to airline
MSA-DTWD | WA3567595 | block 10, 1st male toilet - leaking toilet, last cubicle | Thornlie Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 11:36:00 | Pass | Fix leaking toilet
MSA-DTWD | WA3567598 | Raised pavers on pathway between block 8 & 10 | Thornlie Campus | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 15:00:00 | Pass | 25/08/2020 - paving relevelled as requested by site.
MSA-DTWD | WA3567599 | Raised pavers on pathway of courtyard | Thornlie Campus | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 15:30:00 | Pass | 25/8/20 - Completed reveling of pavers as requested by site
MSA-DTWD | WA3567603 | Koora Marr centre - Double GPO loose on wall near entry | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 19 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 09:00:00 | Pass | Arrived on site, signed in , located PowerPoint , completed jsa , removed old fixings , replaced holes in wall with wall mates , replace screws and fixed mounting block back to gyprock , re fitted PowerPoint , all now good ***job complete ***
MSA-MRWA | WA3566634 | ground archives room Repair and/or replace lock on small roller door. | Heavy Vehicle Services | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 19 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 13:55:00 | Pass | Secured small roller door to archive room. Lock mechanism is missing the locking bars and strikes. Staff have not used the door in 5 years and only needed it to be secured so the door has been secured to the frame
MSA-DCS | WA3567986 | Cell A2 broken window glass. Unit 2 | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 20 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 11:15:00 | Pass | WINDOW REGLAZED
MSA-DCS | WA3567990 | Bakery - Workshop freezer sea container has stopped working | Casuarina Prison | WSM-BR-SITE | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 07:50:37 | 2020-08-20 10:00:00 | Pass | Turned freezer on and found to be fully operational.
MSA-DCS | WA3567995 | Unit 6 - C7 Drain in floor under sink blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 08:30:00 | Pass | Removed paint from fwg. Cleared blockage with plunger.
MSA-DCS | WA3567999 | Visits Area CCTV footage of Prisoner corridor in Visits is not recording | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 07:57:33 | 2020-08-20 11:00:00 | Pass | Checked programming onIndigo. Found mismatch in software regarding the recording NVR. Corrected the data mismatch and confirmed recorded video available for viewing.
MSA-DCS | WA3568037 | Unit 2, C & D office - plumbing leak in roof | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 08:25:52 | 2020-08-20 15:51:00 | Pass | Unit 2 second story plant room, supplied and installed a new section of 20mm hot water service as it had burst. Tested works on completion
MSA-DCS | WA3568060 | Crises care cell 4 Faulty power point | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 08:38:47 | 2020-08-20 13:00:00 | Pass | Replaced gpo
MSA-DCS | WA3568118 | whole of office 3x down lights, 19x fluro's and 3x regular | Maddington (South East Metro) | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 12:30:00 | Pass | Repaired numerous faulty lights around site
MSA-DCS | WA3568126 | Unit 2 B5 Medical hatch Lock key won’t go in Barrel | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 09:11:30 | 2020-08-24 11:15:00 | Fail | 20/08/2020 - Attended site. Temporary repairs performed to make safe. Parts needed.24/08/2020 - On site. Supplied and fitted replacement parts to restore normal function.
MSA-DCS | WA3568129 | Unit 6, Regi Kitchen - Regi oven not heating, worker claims to have received a electric shock | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 09:06:15 | 2020-08-21 08:30:00 | Pass | Regi oven shock
MSA-DCS | WA3568142 | kitchen Receiver goods Room Lights Not Working - ladder required | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 08:00:00 | Pass | Investigate and repair kitchen goods receivals room lights
MSA-DCS | WA3568145 | Unit 4, C wing - light in C wing landing not working, bulbs have been replaced and still not working | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-24 15:00:00 | Pass | Repaired multiple faulty lights in unit 4 C wing landing and showers
MSA-DCS | WA3568151 | Education - Locks on room 10B and toilet door in demountable are sticking & unable to open smoothly | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-10 10:15:00 | Fail | Replace bolt throw and service lock on 10B.Replace strike on Toilet door.
MSA-DCS | WA3568153 | CCU (11) - leaking faucet,CCU Sliuice Room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 16:00:00 | Pass | 24/8/20 - investigate fault. Cistern has leaking side entry inlet valve. Part ordered. 25/8/20 - collected parts offsite. Replaced jumper valve in isolation valve. Replaced leaking inlet valve
MSA-DCS | WA3568157 | Medical Centre - toilet blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 09:41:01 | 2020-08-20 14:00:00 | Pass | Plunger used to unblock toilet
MSA-DCS | WA3568163 | Bakery oven burner fault | Casuarina Prison | WSM-BR-SITE | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 09:44:58 | 2020-08-21 15:30:00 | Fail | Job complete
MSA-DCS | WA3568189 | INF (10)- New dryer keeps tripping the power socket | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-02 17:00:00 | Fail | Installed 20amp circuit for dryer in laundry of infirmary
MSA-DCS | WA3568217 | unit 4 PAU perimeter controller 28 EC2 and 3 off line | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 10:24:18 | 2020-11-18 12:11:00 | Fail | Upgrade being assessed under other works.
MSA-DCS | WA3568218 | control room main prison gate control PAU monitor constant buzzing | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 10:26:52 | 2020-11-18 16:22:00 | Fail | Replaced monitor with brand new onsite spare from stock. Stock has been replenished.
MSA-DCS | WA3568224 | PAU zones 2,4,5,7,9 and 11 fail to activate on testing | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 10:29:23 | 2020-08-21 18:00:00 | Fail | Tested all fence zones in PRU. Gate Control advised all zones activated with audible alarm, camera switched to alarmed zone on activation.
MSA-DCS | WA3568240 | MPU (8) - Day Room tap on the urn sprays out at all angels when dispensing. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 10:35:00 | Pass | Replaced corroded tap. All working okay
MSA-DCS | WA3568248 | Unit 5, Cell D3- Light still not working, possible bulbs & fuse | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-24 11:00:00 | Pass | Repaired faulty lights in unit 5 D3
MSA-DCS | WA3568277 | Unit 1, C9 - toilet blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 16:00:00 | Pass | Plunged toilet to clear blockage. (Toilet roll)
MSA-DCS | WA3568293 | Education front door front door frame and hinges are out of level | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2021-02-15 10:58:00 | Fail | DOOR PARTS RE FIXED & ADJUSTED DOOR - BRAF SENT TO REPLACE DOOR FRAME AND HINGES - MARIO PUT JOB ON HOLD - CLOSING OFF COST TO DATE AND WITH TEMP FIX.
MSA-DCS | WA3568343 | Unit 4, B7 - smashed cell door veiwing window | Casuarina Prison | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 13:15:00 | Pass | OBS PANEL RE GLAZED
MSA-DCS | WA3568383 | unit 2 lower landing ceiling unable to hold exhaust fan requires replacing | Karnet Prison Farm | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-11-12 18:00:00 | Fail | DAMAGED CEILING REPLACED
MSA-DCS | WA3568401 | SITE COST Main Entry to visits area - sliding doors are not opening | Bunbury Regional Prison | WSM-BR-SITE | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 20 Aug 2020 | 2020-08-20 20:08:53 | 2020-08-20 13:15:00 | Pass | Contacted site and was advised that PRU sliding door was having issues. Had site reset power to readers and readers confirmed to be working ok. Issue related to sliding door mechanical side. Requires door mechanic attendance
MSA-DCS | WA3568403 | SITE COST Unit 6, cell 15 & 16 - keys wil not go into lock. unable to be opened | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 20 Aug 2020 | 2020-08-20 16:11:15 | 2020-08-20 15:00:00 | Pass | Repaired / adjusted 2 x cell locks in Unit 6 Cells 3 & 15Reported as 15 & 16 Senior Officer Dean - confirmed 3 & 15
MSA-DCS | WA3568481 | unit 3, C wing, External Breezeway doors - lock has been broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 13:26:46 | 2020-08-20 15:30:00 | Pass | Forcibly opened lock
MSA-DCS | WA3568486 | Unit 4 C9 GPO broken | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 09:30:00 | Pass | Replaced gpo
MSA-DCS | WA3568487 | Gatehouse - metal detector, constant alert noise | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 13:31:40 | 2020-08-21 15:54:00 | Fail | Investigated fault, Modified configuration and monitored for correct operation.Tested OKJob caomplete
MSA-DCS | WA3568494 | Unit 2, D13 - Cistern Broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-25 13:58:00 | Pass | Removed old cistern replacing with new and adjusted pipe work to suit
MSA-DCS | WA3568516 | Unit 6, A16 - toilet will not flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 13:54:15 | 2020-08-21 14:25:00 | Fail | Repaired faulty cistern
MSA-DCS | WA3568553 | Lvl 3, Ladies toilet- hand basin is leaking | East Perth | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 11:30:00 | Pass | Complete
MSA-DCS | WA3568619 | Social Visits - door lock jamming | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 15:27:49 | 2020-08-21 14:00:00 | Pass | Attended site and surveyed/tested door. No fault could be identified.
MSA-DFES | WA3568120 | station building - window treatments (curtains/blinds) throughout building are in various states | CFRS Welshpool | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-10-13 10:54:00 | Fail | Did not get BRAF Approved
MSA-DFES | WA3568257 | Level 1 room 17 and ground level room 21 - the speakers can barely be heard | CFRS Fremantle | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-24 12:45:00 | Pass | COMPLETED
MSA-DFES | WA3568263 | Level 2 Lobby Door and Stairwell door-Egress Button not working -see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-20 16:30:00 | Pass | 20/8/20 - Dylan ParslowInputs on door controller side B for level 2 lobby east door, not functioning correctly. Rewired egress to spare input on side A and programmed macro for exit operation.Tested all working ok
MSA-DFES | WA3568353 | Retrospective WO - Z1 REED SWITCH ON FIRE ENTRY DOOR - Do not attend | DFES Fleet & Equip Serv Fleet Appliances Prog Bran | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 20 Aug 2020 | 2020-08-20 17:00:00 | 2020-08-20 08:38:00 | Pass | Patrol Resolution:EXTERNAL CHECK ALL APPEARS SECURE, STAFF ON SITE JOHN KIRK, LICENCE NUMBER 5007435.
MSA-DFES | WA3568477 | ground server room, security tag sensor not working-see notes | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 09:40:00 | Pass | 25/8/20 - Dylan ParslowFound card reader frozen.Power cycled and tested all ok.
MSA-DFES | WA3568565 | engine room door No2 will not go up suspect electrical fault | CFRS Murdoch | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 17:00:00 | 2020-09-30 09:30:00 | Fail | Technician attended the site of Murdoch Fire Station to the Engine room #2 Bi-fold door no. W22122 on 20/08/2020. Following a full test and inspection of door components found fault to be electrical burn after the tech has isolated the door and opened up control boxes. Upon opening the gfa controller he could immediately smell an electrical burn so he tested all other components to top control box and everything seems ok. He concluded that the gfa controller has blown up and will required a replacement to get the door back into operation.Technician retuned on site on 30/09/2020 to replace the faulty controller with a new gfa 971 controller and completed quoted works. Full test and inspection of door function completed prior to leaving site. This quote includes:"Supply and installation of 1 x new replacement GFA 971 Controller "Test and check door operation."The above work is to be carried out during normal business hoursBreakdown of cost: First callout and l
MSA-DFES | WA3568635 | Overflow shrouds & drain caps in sinks & on bathroom floors are corroded | DFES Cockburn Emergency Services Complex | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-10-02 10:56:00 | Fail | Replacing the basin fittings
MSA-DTAG | WA3568149 | L14 Chambers 14.05 Chamber door is not closing fully | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-21 08:45:00 | Pass | DOOR CLOSER ADJUSTMENT MADE
MSA-DTAG | WA3568376 | Level 9, staff toilets - Toilet seat is cracked, unisex toilet next to Court 91 | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-20 11:52:00 | Pass | Complete
MSA-DTAG | WA3568384 | Crown Robing Room - 106 door is binding in door frame | Supreme Court | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-21 11:00:00 | Pass | ADJUSTMENT TO DOOR MADE
MSA-DTAG | WA3568437 | Magistrates Court entry- Damaged carpet tiles due to termite invasion | Perth Children's Court | GMP-BR-HO | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 11:15:00 | Pass | Magistrates Court Entry damaged carpet tiles due to termite invasion.Replaced damaged carpet tiles and stairnosing
MSA-DTWD | WA3567954 | Lift 1 has stopped working | Mount Lawley Campus | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 20 Aug 2020 | 2020-08-20 11:29:27 | 2020-08-20 08:45:00 | Pass | Lift1 MLT-Hydraulic :Lift stopped on H2 error, Lost speed up, checked Emerson drive for faults, all ok, checked known fault with K 29 relay, all ok, reset processor and ran lift for sometime,could not reproduce fault, also checked pressure was holding on digital gauge passing valve body, left lift in service.
MSA-DTWD | WA3568072 | child care laundry ceiling damgaed | Rockingham Campus | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-20 15:30:00 | Pass | Have attended site and measured up to replace ceiling. BRAF will need to be prepared 7/9/20 - Original BRAF revised and submitted to allow for Saturday Labour rate 22/9 - BRAF declined. Andrew Crawford requested to close off and claim costs to date
MSA-DTWD | WA3568158 | Student Male toilet - Remove Racial graffiti | Kwinana Automotive Centre | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 0 | CLOSE | 20 Aug 2020 | 2020-08-20 13:14:29 | 2020-08-21 10:50:00 | Fail | Removal of Graffiti from male toilets
MSA-DTWD | WA3568213 | sewer pump - plump in alarm | Mandurah Campus (formerly Peel) | GMP-BR | Waste Management | Plant & Pumps (WM) | Ballantyne Plumbing Gas & Electrical | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 17:00:00 | 2020-08-20 13:30:00 | Pass | Made repairs to electrical system and tested
MSA-DTWD | WA3568256 | B2122 Staff Kitchen Sink Blocked | Bentley Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-28 11:10:00 | Fail | Rectify major blockage
MSA-DTWD | WA3568336 | V block Passageway water fountain has come loose | Rockingham Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 14:32:00 | Pass | Re fixed fountain arm to bracket. All ok
MSA-DTWD | WA3568348 | N Block, Room N119- Repair power GPO near massage table broken on wall | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 12:45:00 | Pass | Arrived on site, signed in, spoke to client about job, located gpo, completed jsa, removed blank plate on the wall to test cables, cables tested out good, replaced blank plate , found distribution board, isolated circuit, removed blank plate , fitted dgpo and fixed it back to the wall , re energised circuit , tested dgpo, test passed , cleaned up work area , locked room , completed paperwork ***job complete***
MSA-DTWD | WA3568409 | A Block, Room AT4A male toilets- 1st Cubicle, Cistern Leaking, Water continuously running | Carlisle Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-21 13:45:00 | Pass | Replace toilet and leaking tap
MSA-DTWD | WA3568500 | S block, level 1, S108 and Passage near E 100 - faulty lighting, replace tubes | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 14:15:00 | Pass | Arrived on site, signed in, spoke to client about job, located lights in room and passages , completed jsa, set up work area , changed tubes and starters , cleaned up work area , locked room , completed paperwork ***job complete***
MSA-DTWD | WA3568562 | E Block - E58 Large Scale Kitchen – Faulty function dial on Pizza Oven | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 1 | CLOSE | 20 Aug 2020 | 2020-08-21 17:00:00 | 2020-10-07 13:30:00 | Fail | completed 7/10/20 - no contact from suppliers or call back so complete job.
MSA-DTWD | WA3568621 | Small garden at back of 12Ab - Lighting not working, replace as requested | Perth Campus B5 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 20 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-04 09:19:00 | Fail | Repalced faulty lamps to pole lights. Tested all working .job completed
MSA-DTWD | WA3568631 | J003, J004 & J005- Fragile wooden steps | Balga Campus | GMP-BR | Carpentry | Staircases, Balustrades and Handrails (CA) | AWB Co. | 2 | CLOSE | 20 Aug 2020 | 2020-08-25 17:00:00 | 2020-09-08 15:00:00 | Fail | As per attached signature slips
MSA-DCS | WA3568707 | WWTP air operated valves to claifier tank faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 3 | CLOSE | 21 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-10 13:30:00 | Fail | WWTP Air operated Valves to clarifier tank faulty. 5 x Air valves & actuator drives faulty. Check valves, order new parts. Pick up & return to Treatment Plant.
MSA-DCS | WA3568711 | Unit 6 - B Wing cleaners store water leaking from the pipe on the right side of the sink, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 21 Aug 2020 | 2020-08-22 07:32:13 | 2020-08-21 15:00:00 | Pass | Collected parts offsite. Repaired leaking pipes in cleaners store. Tested
MSA-DCS | WA3568716 | monitor room, 5 zones not showing camera loop feeds when alarm is activated | Boronia Pre-release-AS14 - Administration and Visitors Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Aug 2020 | 2020-08-21 11:36:30 | 2020-08-21 09:00:00 | Pass | Attended site and found NVR2 offline which was causing zones to not activate on alarm. Rebooted NVR and checked for correct disks and raids being built. Retested all perimeter alarms and checked for correct recordings. All tested and working ok. Job complete
MSA-DCS | WA3568720 | INF (10) - Cleaning Store tap leaking in laundry | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 08:30:00 | Pass | Nill
MSA-DCS | WA3568722 | SOP kitchen tap leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 15:30:00 | Pass | Nikl
MSA-DCS | WA3568761 | Kitchen - BRAT pan is failing work hydraulic lifter | Karnet Prison Farm | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 21 Aug 2020 | 2020-08-22 08:20:54 | 2020-08-21 18:30:00 | Pass | 21/08/2020Called as requested to the bratt tilt not working. Found an air pocket in hydraulic line cleared tested ok. Also replaced tilt switch and stat knob as required. Also replaced the glass lenses on the combi oven.
MSA-DCS | WA3568774 | SOG POD - Perimeter Alarm not activating FO2 | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 21 Aug 2020 | 2020-08-22 08:30:08 | 2020-08-21 12:45:00 | Pass | Travelled to site.Attended site and checked fence alarms from control room. Found EC12 Fence alarm was in constant alarm, gained access to sterile zone and checked EC12. All EC equipment working ok however electric fence zone F2 had been short circuiting. Isolated zone and drove around to external fence area and checked the whole of F2 fencing, found cables latched together by electric fence sign causing a short circuit. Disconnected sign and re-mounted sign to avoid future issues and crossing of electric fence cabling. De-isolated zone at EC isolator switch and retested fence. All alrams cleared and working ok. Job complete
MSA-DCS | WA3568876 | Unit 1, ground reception - Front door lock is hard to operate. Suspect door has dropped and is touch | Midland (North East Metro) | GMP-BR- HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 15:20:00 | Pass | Attended site, serviced lock, rehung door.Date on site: 24/08/2020Time on site: 02:05pm - 03:20pm
MSA-DCS | WA3568886 | Bromic Pizza Fridge temp is high - see notes | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Cleaners Room - Next to Main Kitchen | GMP-BR- HO | Refrigeration | Refrigerators (RE) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-09-10 15:16:00 | Fail | Replaced the evaporator coil and drier, checked the leak found OK. Charged the refrigerant and checked foundvok.
MSA-DCS | WA3568907 | Main Prison, Industries, vegie prep- Roller door in constant alarm | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 16:30:00 | Pass | Three doors in same building showing permanent alarm. Vege Prep inwards Goods Roller, veg prep outwards Goods Roller & Maintenance Entry Door. Replaced damaged heavy duty Roller Door Reed switches on Vege Prep doors and replaced missing concealed Reed switch magnet in maintenance door. All alarms clear.
MSA-DCS | WA3568940 | Unit 9, Cell A4- officer received electrical shock from switch | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 0 | CLOSE | 21 Aug 2020 | 2020-08-21 14:15:46 | 2020-08-24 13:00:00 | Fail | Investigate electric shock and attached report to Pro Map
MSA-DCS | WA3569014 | Unit 3, Cell 28- Door lock is broken | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 16:30:00 | Pass | New cell lock fitted to replacement door fitted by Wooroloo maintenance.
MSA-DCS | WA3569017 | Unit 4A, Cell 38- Door lock is broken | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 14:30:00 | Pass | replaced cell lock on Cell 38 Unit 4A
MSA-DCS | WA3569046 | Unit 4, Cell B7- Sink is leaking at U bend | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 15:30:00 | Pass | Nill
MSA-DCS | WA3569049 | Health centre - blocked toilet, has been an on going issue. | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Aug 2020 | 2020-08-22 11:30:01 | 2020-08-21 16:32:00 | Pass | Inspect and flush all drains and waste No sign of any blockage all drains are running free
MSA-DCS | WA3569053 | Unit 4, Cell B11- Window wont stay open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 14:45:00 | Pass | SPIRAL BALANCES REPLACED
MSA-DCS | WA3569064 | office in admin area - door lock requires a key to exit. please blank lock from inside 2 outside | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 21 Aug 2020 | 2020-08-22 11:43:26 | 2020-08-31 10:15:00 | Fail | 24/08/2020. On site. Assessed door. Parts needed to achieve desired result. DOJ consultation required.31/08/2020. Attended site. Supplied and installed mortice lock. Installed site supplied door furniture. Set lock to Free to Exit as instructed by DOJ.
MSA-DCS | WA3569180 | Main Kitchen- back door lock is faulty | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 13:45:00 | Pass | Replaced lock and cylinder on Main Kitchen Rear Door also replaced broken handle spring on external handle
MSA-DCS | WA3569182 | Main Kitchen- switchboard door lock is faulty | Bandyup Prison | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 14:30:00 | Pass | Whilst at bandyup Womens Prison - Repaired Lock on Kitchen Main Switchboard
MSA-DCS | WA3569284 | Administraation - climate control is broken there is no heating | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 08:30:00 | Pass | found fire alarm relay activated on arrival. Reset relay and test ran units successfully in all modes. All operational at time of departure.
MSA-DCS | WA3569296 | unit 2, A wing - PA system is very loud, | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-11-20 14:49:00 | Fail | Replaced PA speaker with new one with adjustable potentiometer. Set to 5 watts and prison staff and inmates are happy.
MSA-DCS | WA3569386 | Wooroloo Prison Farm - Gatehouse - Perimeter fence camera is not live recording. | Wooroloo Prison Farm | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 21 Aug 2020 | 2020-08-21 21:48:17 | 2020-08-21 23:00:00 | Fail | Attended site and investigated the fault.Checked and tested Senstar module in zone 3.Restarted IndigoVision computers.Logged in with operator password and conducted test.All back to normal and operational.
MSA-DFES | WA3568688 | ground outside carpark-refix Purlin Support above vehicles between bays 130-140-see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Steel Work (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 21 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 14:30:00 | Pass | Purlin spreader rescrewed back in place
MSA-DFES | WA3569002 | G Floor, Ladies toilet - light not working | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 11:45:00 | Pass | COMPLETED
MSA-DFES | WA3569010 | Lvl 2, Media Section- Ceiling light cover fallen off & is hanging by cables | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 10:15:00 | Pass | COMPLETED
MSA-DFES | WA3569018 | Kitchen - fan unit above the stove the ducting has broken away from the ceiling space | CFRS Wangara | GMP-BR | Building | Materials (BU) | AWB Co. | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 08:31:00 | Pass | Attended site, inspected broken ducting above rangehood, left site to pick up parts returned and replaced ducting with new, tested, job complete.
MSA-DFES | WA3569030 | damage to bitumen traning area - requires repairing to eliminate any trip hazards and further damage | CFRS Rockingham | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-09-16 14:56:00 | Fail | 24/8/20 - Have attended site and assessed works required. Have issued a request to Asphalt Repair Contractor. Will prepare BRAF once we receive the quote Purchase order issued to subcontractor on approval of BRAF 3/9/20Works now completed
MSA-DFES | WA3569220 | Retrospective WO - ZONE 22 IN ALARM REED SWITCH APP BAY 1 REAR DOOR | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 10:09:00 | Pass | Guard AttendanceDespatch Comments:ZONE 22 IN ALARM REED SWITCH APP BAY 1 REAR DOORPatrol Resolution:TRUCK WENT ON A JOB . NO SIGN OF FORCED ENTRY . TRUCK ARRIVING BACK WHILE ONSITE
MSA-DFES | WA3569274 | 1 floor, passage way, operations and Marine services - light fitting half hanging out of ceiling | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 14:45:00 | Pass | Repaired light that has fallen down on level 1 and everything is safe and fine.
MSA-DFES | WA3569362 | Cracking in the ceiling appearing from the corners of the air condition | DFES Education and Heritage Centre | GMP-BR | Building | Ceiling (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2021-01-12 11:14:00 | Fail | Patch cracks in ceiling and sand and seal and then paint ceiling and Cornice
MSA-DFES | WA3569364 | Red Pod Area- Ceiling requires painting | DFES Education and Heritage Centre | GMP-BR | Painting | Internal (PA) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-12-16 14:30:00 | Fail | 16/09/2020 02:50 PM (UTC+08:00) - crispin@protek247.com.au Have been negotiating with site to resolve a time to get our ceiling subcontractor to site to quote works Have been in discussions with Heather McNamara, Site Facilities to resolve a time to carry out the works. At this stage it seems likely the work will need to be done once the centre closes for the year in early December Works will require the area be closed off for at least 2 daysSection of ceiling was removed and replaced with new gyprock. Area was then patched and painted.
MSA-DFES | WA3569372 | Outside Marine Rescue/Alisha Carruthers desk- 1 x fluoro light is out | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 11:30:00 | Pass | COMPLETED
MSA-DTAG | WA3568817 | level 5 - Family Violence stainless steel sign has fallen off the wall outside office entry | Central Law Courts | GMP-BR-HO | Carpentry | Materials (CA) | Midolo Building Services | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-21 12:45:00 | Pass | SIGN RE INSTALLED
MSA-DTAG | WA3568970 | Ground level - A foreign device has been plugged into one of main power outlets causing short circui | Joondalup Courthouse | GMP-BR-HO | Electrical | General Electrical (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 10:00:00 | Pass | Reset tripped powerpoints circuit due to faulty appliace.
MSA-DTAG | WA3569063 | stody are having problems recording footage to discs and multiple cameras currently not recording | Joondalup Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 17:00:00 | Pass | Identified Bosch Flexidome Camera having issues with recording. Rectified I-Frame settings of the following cameras, 72, 74, 51, 61, 64, 65 & 79, re-enabled all mentioned cameras, confirmed recordings. Job completed.
MSA-DTAG | WA3569167 | Level 1, youth justice court - Network cable come out of partitioning, will require new cover | Perth Children's Court | WSM-BR-SITE | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 08:15:00 | Pass | Job complete
MSA-DTAG | WA3569211 | Lvl 1, Custody Interview Room 2 ceiling has some cracks- further info below | Midland Courthouse | GMP-BR-HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-31 09:30:00 | Fail | CEILING CRACKS REPAIRED & PAINTED
MSA-DTAG | WA3569268 | Female Staff toilet - mirror top fixings are loose | Mandurah Courthouse | GMP-BR-HO | Glazing | Mirrors (GL) | Midolo Building Services | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 12:30:00 | Pass | SECURED MIRROR BACK TO WALL
MSA-DTAG | WA3569282 | VSS Room - Carpet square stained needs replacing | Mandurah Courthouse | GMP-BR-HO | Flooring | Carpet (FL) | MALCO FLOORING PTY LTD | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-25 14:45:00 | Pass | VSS ROOM CARPET SQUARES STAINED NEEDS REPLACING
MSA-DTAG | WA3569292 | Car park - The Main electronic gate that allows access into the staff car park has ceased completely | Joondalup Courthouse | GMP-BR-HO | Building | Steel Fencing & Gates (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 16:10:00 | Pass | Found that the closed position sensor has been knocked out of place causing the gate to stop short, refit sensor and tested, all ok.
MSA-DTAG | WA3569335 | Custody Staff, holding cell 2-Person in custody has spit whilst in the cell-Mainly on door & window | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Materials (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 11:30:00 | Pass | Job carried out as per WO
MSA-DTWD | WA3568742 | G block female toilets cubicles x 2 and disabled toilet are blocked. Floor drains overflowing | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 11:27:00 | Pass | Unblockeddrain
MSA-DTWD | WA3568744 | Glasshouse boiler - fault, not starting automatically when it should be. | Murdoch Campus | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 12:30:00 | Pass | Attended site, tested for faults, found and replaced a faulty HT feed through connector, tested for correct operation and left working - ok
MSA-DTWD | WA3568748 | G block code not working on the Tcom | Rockingham Campus | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 11:30:00 | Pass | 21/08/2020, 1015-1130Checked codes in all systems and programmed new cleaners code in all systems and tested
MSA-DTWD | WA3568751 | A block, G floor - lift not working | Joondalup Kendrew Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-24 00:00:00 | Pass | attended site and reset lift
MSA-DTWD | WA3568875 | cooling tower L2 plant room roof valve leaking, dumping to sewer | East Perth Campus | GMP-BR | Air Conditioning | Cooling Tower (AC) | Precise Air Group | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-09-04 14:00:00 | Fail | Access gained. Isolation and lock out of condenser water pumps and fans.Drained sump for valve fittings access. Removed very tight valve head. Replaced with new using Teflon tape and tensioned. Installed new arm, float and inspected for movement.Filled sump back up to tower. Adjusted water level via balancing pipe and water level as 1 tower takes water. Set levels for running scenario.Tested with pump on. No leaks.
MSA-DTWD | WA3568932 | 814, gas hot water system faulty | Muresk Institute | GMP-BR | Plumbing & Drainage | Gas (PD) | Lane's Plumbing | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 15:00:00 | Pass | Job completed - repair faulty HWS
MSA-DTWD | WA3568945 | A block foyer north end Auto doors after hours exit button not working | Mandurah Campus (formerly Peel) | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-21 13:10:00 | Pass | Replaced push to exit button. Reset door as door was not locking properly. Tested all good. Door no 1096451
MSA-DTWD | WA3569025 | L4 roof access - Broken window locks | Perth Campus B2 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 12:10:00 | Pass | survey window locks to roof access. Advise best course of action for repairs. Repairs required by glazier.
MSA-DTWD | WA3569058 | D Block, Main auto door is not closing fully | Joondalup Kendrew Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 13:43:00 | Pass | Found that the door was braking early and stopping short, adjusted the drive settings for the door to run smoothly and stop at the correct position, tested all ok.
MSA-DTWD | WA3569071 | D Block, G/Floor, male toilets, 1st cubicle toilet continuously running , turned off in duct | Joondalup Kendrew Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 15:30:00 | Pass | COMPLETED
MSA-DTWD | WA3569165 | Lvl 1, Beauty- door lock broken | Perth Campus B2 | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 13:00:00 | Pass | Change function of lock and replace cylinder components to Lvl 1 beauty
MSA-DTWD | WA3569177 | Level 3, staff disabled toilet - Flushing not working | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 13:17:00 | Pass | Fix toilet
MSA-DTWD | WA3569288 | A Block, Room A354- carpet tiles ripped carpet under desk Mick Penreath | Leederville Campus | GMP-BR | Flooring | Tiling (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-11-18 19:45:00 | Fail | Replaced damaged carpet tiles as requested by site
MSA-DTWD | WA3569300 | A Block, Room A009 - the door proxy works intermittently, door does not open when swiped | Joondalup Kendrew Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 08:30:00 | Pass | Attend site to investigate fault on door A009, found the mortice lock to be intermittently working. Replaced lock, all working ok
MSA-DTWD | WA3569332 | Level 2, C214 - the door proxy does not wok when swiped | Joondalup Kendrew Campus | GMP-BR | Security | Access Control (SE) | BJ SYSTEMS | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 10:45:00 | Pass | Attend site to investigate fault on door C214, found lock to be faulty, replaced, tested multiple times, found the sensor to be a bit off, reconfigured and now it’s working as per nor
MSA-DTWD | WA3569349 | double wooden doors going into room C17 have swollen up and are hard to close, | Murdoch Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 15:00:00 | Pass | Adjust doors to c & f blocks as per work order/site request
MSA-DTWD | WA3569377 | Lvl 7, Room 708- Whiteboard has fallen off wall | Perth Campus B1 | GMP-BR | Building | Materials (BU) | AWB Co. | 3 | CLOSE | 21 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 14:30:00 | Pass | Ease door and adjust lock and strike plate. INstall new door handleInstall whiteboards
MSA-DTWD | WA3569381 | B Block, Lvl 4, Male Toilets, Cubicle Toilet missing flush button | Bentley Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 21 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 17:16:00 | Pass | Fix toilet
MSA-MRWA | WA3568766 | Level 3, female toilet - leaking please remediate | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 21 Aug 2020 | 2020-08-24 17:00:00 | 2020-08-21 13:10:00 | Pass | Did inductions and then repaired leaking cistern replacing rubbers and inlet valve
MSA-DCS | WA3569402 | Wooroloo Prison Farm- CAmeras 8,14 not working in gatehouse | Wooroloo Prison Farm | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 1 | CLOSE | 22 Aug 2020 | 2020-08-23 06:07:39 | 2020-08-22 10:30:00 | Pass | Attended site and investigated the fault.No video signal from camera 1 in zone 14.Reseted power to camera and tested.Camera is back to normal.Found blurry image on camera 2 in zone 8.Power cycle IndigoVision encoder and conducted test.Camera 2 is back to normal and operational
MSA-DCS | WA3569418 | CCTV cameras for safe cell is obscured | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 22 Aug 2020 | 2020-08-22 12:19:43 | 2020-08-22 12:30:00 | Fail | Attended site.Found that CCTV keyboard is logged out.Logged in and conducted test - CCTV keyboard is operational.Given instructions to operator.All ok at departure.
MSA-DCS | WA3569495 | Wooroloo Prison Farm- fence alarm in zone 8, zone 5 to be checked | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Seme Solutions Pty Ltd | 1 | CLOSE | 23 Aug 2020 | 2020-08-24 06:06:26 | 2020-08-23 11:00:00 | Pass | Attended site and investigated the fault.Checked microphonics cable for any damage.Checked connections and sensitivity on SENSTAR modules in zones 5 and 8.Conducted test.All ok at departure.No fault was found
MSA-DCS | WA3569508 | 9 internal and 1 internal in constant alarm. PTZ 12 not panning or tilting. | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 23 Aug 2020 | 2020-08-26 17:00:00 | 2020-09-09 09:48:00 | Fail | Investigated and repaired multiple perimeter and camera faults.Tested OK.Job Complete
MSA-DCS | WA3569518 | SITE COST Unit 1 Cell B1 - Smashed rear window. | Bandyup Prison | WSM-BR-SITE | Building | Windows (BU) | Schlager Construction Group | 0 | CLOSE | 23 Aug 2020 | 2020-08-23 14:05:46 | 2020-08-24 16:00:00 | Fail | Attended site Sunday 23/082020 to find smashed window, removed damaged window, boarded up and made safe. Re-attended site removed temporary board and install new glass.
MSA-DCS | WA3569605 | No hot water to the whole of unit 1. | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 23 Aug 2020 | 2020-08-23 17:24:54 | 2020-08-23 15:05:00 | Pass | No hot water to the unit.Boiler has shut down.Needs boilertronics.Advised site to get boilertronics.
MSA-DCS | WA3569607 | the tap in the kitchen is running can't turn it off | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 23 Aug 2020 | 2020-08-23 18:48:55 | 2020-08-23 16:25:00 | Pass | Replaced leaking taps in kitchen
MSA-DCS | WA3569618 | No hot water to the whole of unit 1. | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Boilertronics | 0 | CLOSE | 23 Aug 2020 | 2020-08-23 21:00:32 | 2020-08-23 21:30:00 | Fail | Burner faulting repeatedly at LFL position 1 or soon after. Opened burner and :- cleaned ignition electrode insulation andcable, cleaned burner head diffuser plate and flame rod, checked ignition spark and fan rotation. Reassemble burner.Check air damper is free. Reinstate flame rod cable into LFL terminal 24 and add earth to terminal 22. Test start ok.Check pilot combustion and found 19.8%O2. No more pilot fuel available. Dropped low fire air from 0.28kPa to 0.15kPaand adjusted main burner combustion to comply. Low fire 8.8%O2, high fire 4.9%O2 and fuel pressures matching dataplate. Air pressure switch now set 2mB. (As found, switch was at lowest setting) Small combustion rumble at lower firingrates (low fire to about 15%). After adjustments, no unintended faults while on site.Unable to undo nuts on water filter flanges. New bolts and gaskets left on site on top of heater.
MSA-DCS | WA3569622 | Hakea Prison - Internal perimeter - zones 12 and 13 are in fault. | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 23 Aug 2020 | 2020-08-23 22:31:39 | 2020-10-12 13:59:00 | Fail | Found when PSU in OBS post 6 is disconnected, this Sennet module fault clears, Suspect faulty power supply in OBS post 6. Constructed replacement 48V PSU in PVC Enclosure. Installed and tested new PSU OK.Found fault with Sennet module in zones 12 and 13 still intermittently reoccurring. Searched and found replacement s/h module as new parts are no longer available for this system. Installed, configured and walk tested/calibrated.Tested OK.Parts used (SEME):Power Supply componentsMounting hardwareEnclosureConsumablesParts used (PFM):1 x SM100-1 Module (Pre used/Second Hand)
MSA-DCA | WA3575393 | VESDA displaying “filter” alarm | DO NOT USE - TO BE DECOMMISSIONED State Library of WA-Main Building-Level 4 - Level 4 Stack - PFM ID 036 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 12:50:00 | Pass | Investigate VESDA fault 4th floor rare book room.
MSA-DCS | WA3569671 | Perimeter alarm - Male security section -Arunta room PE beams(displays on the screen) | Broome Regional Prison | GMP-BR- HO | ICT/Audiovisual | Maintenance (AV) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 06:03:41 | 2020-09-03 01:56:00 | Fail | Bottom PE beam only showing .5vdc alignment voltage.adjusted alignment to 1.3vdc.PE beam operational
MSA-DCS | WA3570222 | Staff Room, Female Toilet- Toilet seat snapped | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 15:15:00 | Pass | Renew toilet seat
MSA-DCS | WA3570263 | Sallyport, Resident toilet- blocked soild | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 16:00:00 | Pass | Inspect and test toilets no sign of any blockage water running free
MSA-DCS | WA3570333 | kitchen, Rear Door- door closer broken | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 24 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-31 09:00:00 | Fail | New door closer installed
MSA-DCS | WA3570376 | Front Gate, Control- Oval lights will not operate | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 10:30:00 | Pass | Attended site and checked Gallagher faults for anything related to lighting control to the Oval, found 2 x Expanders connected for lighting control offline. Checked expander location and found expanders related to Old gatehouse as part of demolition works and electrical equipment had been turned off from electrical contractors. Have advised security of the issue. Job complete
MSA-DCS | WA3570445 | Karakin, A Wing (lounge)- Sash window frame broken | Banksia Hill Detention Centre | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 24 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 13:15:00 | Pass | repair framework
MSA-DCS | WA3570486 | Woodwork- Thicknesser not working (electrical issue) | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-26 14:00:00 | Pass | Investigated faulty thicknesser in woodwork, found damaged v-belt, picked up replacement and installed. Waited for site power to be restored and tested machine
MSA-DCS | WA3570605 | SOG Pod - Outer D Fence Monitor blank | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 09:00:00 | Pass | Checked output from KVM Extender at console, no video out. Attended basement equipment room, checked video out at rear of workstation, no output. Power reset pc, confirmed DVI video out, reconnected KVM and confirmed functionality restored in control room.
MSA-DCS | WA3570794 | O D P - Sprinkler fire alarm is on. No Fire. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 2 | CLOSE | 24 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-26 14:50:00 | Pass | 27/08/20 EIAttended site and investigated fire alarm on ODP.On investigation no alarms present but 2 faults present on the FIP in the Infirmary.Faults list asM1-138 medical centre male toilets &M1-139 medical centre female toilets.Investigated the Infirmary faults in the old section of Infirmary & the new open section but faults were not in either of these areas.No access to the Infirmary area under construction to further investigate faults.
MSA-DCS | WA3571500 | Gate House - Both monitors not receiving a signal. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 10:30:00 | Pass | Traced and found HDMI plug at each of the two monitors had been partially removed from the monitor input socket causing loss of signal to the monitor. Reinserted plug correctly and video image restored.
MSA-DCS | WA3571580 | Unit 14, B & D Secure front door to unit is not working through control panel | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-26 17:00:00 | 2020-12-16 15:55:00 | Fail | Repaired doors and tested ok.Job Complete
MSA-DCS | WA3571693 | Unit 14- turnstile not responding to control office release buttons | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-24 14:30:00 | Pass | Tested operation of turnstile. Confirmed operation of IN, OUT, and Free buttons. All working correctly.
MSA-DCS | WA3571751 | Unit 13, B Wing- Cell alarmed tampered with ( pull out of wall ) | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-25 15:00:00 | Pass | Replaced failed cell call point. Needed to swap cell call face plate to fit custom sized aperture in RAP units. cell call tested to local control. Installing retaining Rivets.
MSA-DCS | WA3572295 | Unit 5 - A11 Light switch coming away from the wall. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-24 13:00:00 | Pass | Replaced light switch in cell a12 and repaired faulty lights in a6
MSA-DCS | WA3572404 | Unit 13, Cell C3- prisoner states toilet is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-24 09:30:00 | Pass | Replaced leaking inlet valve in cistern
MSA-DCS | WA3572513 | Unit 15, A & C Wing - Tap is broken in cleaning cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-24 14:00:00 | Pass | Reinstalled hot tap in cleaners room
MSA-DCS | WA3572620 | Unit 10 C and D day room Window rubbers have been tampered with | Hakea Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 08:11:34 | 2020-08-25 09:00:00 | Fail | WINDOW RUBBERS RE SECURED
MSA-DCS | WA3572657 | Amenities - Male Gym- Toilet cistern is broken | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-25 14:00:00 | Pass | Collected parts offsite. Installed new cistern and tested.
MSA-DCS | WA3573152 | Unit 4, Cell D6- water coming up from floor drain | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-24 10:30:00 | Pass | Used acid and plunger to clear blockage in fwg
MSA-DCS | WA3573383 | perimiter fence line pole number 19 both lights out | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-27 11:00:00 | Pass | Investigate and repair perimeter light pole 19
MSA-DCS | WA3573600 | Transitional Manager Lock fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 24 Aug 2020 | 2020-08-24 12:15:27 | 2020-08-24 09:15:00 | Pass | Attended site. No fault evident.
MSA-DCS | WA3573820 | Gatehouse- Missing/broken perspex on visitor booking, further info below | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-31 14:30:00 | Fail | MEASURED FOR NEW SCREEN- TOLD NOT REQUIRED
MSA-DCS | WA3573931 | Unit 7, Cell D2- Window doesnt stay up | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-03 12:45:00 | Fail | NEW WINDOW BALANCES & FEET INSTALLED
MSA-DCS | WA3574690 | Unit 15 - No hot water in the unit cells. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-26 07:50:00 | Pass | Reset gas and hot water units.
MSA-DCS | WA3574938 | Unit 16, B & D Wing- Laundry door in day room not locking | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 11:30:00 | Pass | Strike box broken away from frame, Require parts.Remove broken weld in strike box, supply and install screw in strike box and strike. Adjust strike to suit.
MSA-DCS | WA3575048 | Unit 4, B Wing Cleaning Store- lock is spinning but not functioning | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-14 11:30:00 | Fail | Temp. repair lock.Replace lock, install strike packer and adjust wall mount hold open strike.
MSA-DCS | WA3575053 | Unit 2, B & D wing grill starting to have issues while closing. Further info below | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-02 11:45:00 | Fail | 02/09/20Repairs and inspections all unit grille motors.
MSA-DCS | WA3575077 | control room MF internal screen is coming up light blue | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 24 Aug 2020 | 2020-08-24 12:46:39 | 2020-08-28 17:00:00 | Fail | Investigated comms fault and traced to two locations, repaired fibre fault between gatehouse and Zone 1 which restored all zones except 22. Sourced replacement controller for zone 22, installed, configured and calibrated zones.Tested OKJob CompleteParts:Microphonic Processor - PFM StockConsumables - SEME Stock
MSA-DCS | WA3575081 | Unit 2 A wing the wing lights on A wing are not tunrning on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-27 09:30:00 | Pass | Repaired faulty lights in unit 2
MSA-DCS | WA3575082 | Ladies toilet, toilet is blocked and constantly running | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 08:49:46 | 2020-08-25 12:00:00 | Fail | Complete
MSA-DCS | WA3575084 | Unit 1, Cell 11- Cell Call faulty, not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 08:48:55 | 2020-08-25 13:00:00 | Fail | Unit 1 cell 11. Cleared out toothpaste from cell call and all retested and working ok. Job complete
MSA-DCS | WA3575085 | Unit 1, Cell 09- Cell Call faulty, not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 08:52:57 | 2020-08-28 13:30:00 | Fail | Tested cell intercom in C09 and traced the fault to the input 1 on CI8#7. Removed and replaced CI8 with CI8a. Recabled DATA, PA and power lines between CI8s. Tested all intercoms on CI8a#7, cells C09 - C16. All cells have loud and clear audio in the cells and in U1 control. Parts used:Austco CI8a8 x RJ45 cable adaptersConsumables
MSA-DCS | WA3575086 | Unit 1, Cell 12- Cell Call faulty, not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 08:53:40 | 2020-08-25 10:30:00 | Fail | Attended site and cleared out toothpaste and dirt from cell call. All cleared out and tested working ok. Job complete
MSA-DCS | WA3575088 | Unit 4 D11 Cell Call Faulty. Not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 08:53:02 | 2020-08-25 12:00:00 | Fail | Attended site and cleared toothpaste and dirt from cell call. Retested cell call and all tested ok. Job complete
MSA-DCS | WA3575094 | Unit 4 - B Wing movement sensor dislodged- cavity exposed | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 13:30:00 | Pass | Attended unit found the cover of the 360 deg PIR partially dislodged. Removed the cover and reinstalled.
MSA-DCS | WA3575100 | Gatehouse, Air Con unit is not working correctly | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-24 13:30:00 | Pass | Removed restriction allowing more airflow. All ok.
MSA-DCS | WA3575140 | Reception - leak under the floor. leak detector may be required required. | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 09:31:55 | 2020-11-25 09:05:00 | Fail | Leak on main fixed, all copper what was exposed needs to be replaced. Walls need to be patched and plastered
MSA-DCS | WA3575198 | unit 10 Entry door not closing properly | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 10:04:11 | 2020-08-26 14:15:00 | Fail | 24/08/2020 - Attended site. Inspected door, beyond simple adjustment - parts required.26/08/2020 - On site. Supplied and fitted replacement parts and realigned door to restore normal function.
MSA-DCS | WA3575230 | Unit 9, Cell B16- Sink leaking on to floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 10:11:49 | 2020-08-25 07:20:00 | Pass | Removed trap reshaping trap and resilconing and installing
MSA-DCS | WA3575232 | Chapel- sink needs reattaching | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 10:14:22 | 2020-08-25 09:03:00 | Pass | Installed drain and connected up kitchen sink and unblocked drain
MSA-DCS | WA3575248 | Eyre, C wng Dayroo - dayroom window cracked | Wandoo Rehabilitation Facility | GMP-BR- HO | Glazing | Window Glass (GL) | Midolo Building Services | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 10:17:00 | 2020-09-09 09:15:00 | Fail | WINDOW RE GLAZED AND TINTED
MSA-DCS | WA3575258 | Unit 10, Cell C11- bottom light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 10:22:11 | 2020-08-24 15:00:00 | Pass | Repaired light
MSA-DCS | WA3575262 | Unit 7, E wing - shower tap not turning off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 10:24:29 | 2020-08-25 10:35:00 | Fail | Turned off mains water and rewasherd valves and reseated x2 hot taps only middle shower and shower on far right
MSA-DCS | WA3575356 | Unit 14, D11 - shower & hand basin blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 09:30:00 | Pass | Cleared blockage in both basin and shower drain with plunger
MSA-DCS | WA3575358 | Unit 13, Cell D2- drain plug and pipes do not drain the water completely during prisoner shower | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 10:30:00 | Pass | Used acid and plunger to clear in shower.
MSA-DCS | WA3575407 | Unit 13, Cell D7- Shower & sink are both blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 10:30:00 | Pass | Used acid and plunger to clear blockage in shower and basin
MSA-DCS | WA3575409 | Unit 1, Lobby - cold water dispenser drain block | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 14:50:00 | Pass | Drain machine used to unblock drain
MSA-DCS | WA3575552 | Amenities - Shower Block toilet in male shower block in amenities is cracked, | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 13:00:00 | Pass | Investigated all toilets both male and female. No cracks found in any toilets
MSA-DCS | WA3575581 | Unit 7, E Wing showers- Basin tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 12:51:05 | 2020-08-25 12:06:00 | Pass | Removed broken top assembly replaced with new
MSA-DCS | WA3575583 | Unit 15 Macerator/ Pump station is alarming and light is flashing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 24 Aug 2020 | 2020-08-24 16:48:19 | 2020-08-24 16:00:00 | Pass | 24/8/20 - Collected tools from yard to remove pumps. Removed, cleaned and tested 2 x pumps. Both ok and faults cleared. Removed and cleaned macerator. Motor runs but gears do not turn grinder. Rocks and rubbish continually entering sewer.
MSA-DCS | WA3575613 | Admin door- door lock does not activate | Albany Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-31 20:15:00 | Fail | Tested door functions and found door push button not working. Repaired door push button and all tested working ok. Recommend replace push button with new push button for under admin desk
MSA-DCS | WA3575617 | Unit 1 B13 Sink Tap not working | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 16:35:00 | Pass | Replaced qautor turn tap cold only
MSA-DCS | WA3575633 | Unit 1 B14 Sink Taps not turning off - see notes | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 13:20:46 | 2020-08-25 15:42:00 | Fail | Replaced quator turn tap and air rader in our let
MSA-DCS | WA3575640 | Unit 1 B14 Prisoners lock Jamming & Door Jamming in Frame | Melaleuca Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 12:15:00 | Pass | Attended site. Realigned door and replaced faulty personal lock to restore normal function.
MSA-DCS | WA3575677 | Level 3- Mens Urinal- broken disc | East Perth | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-31 15:00:00 | Fail | Complete
MSA-DCS | WA3575745 | Industries Administration - Lunch Room Leak on pipework under bench Industries staff lunchroom | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-01 08:30:00 | Fail | Nill
MSA-DCS | WA3575848 | camera 168 extenal flickering- seme on site | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-06 14:36:00 | Fail | Attended site, repaired fault with camera 168, monitored for correct operation and tested OKJob Complete
MSA-DCS | WA3828342 | * Restrospective work order * Removed Smart Terminal mimic panel from old control room | Wandoo Rehabilitation Facility | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 24 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 09:26:00 | Pass | Technician Note14/8/20 MBRemoved Smart Terminal mimic panel from old control room as directed. Old control room being decommissioned and mimic is no longerrequired.Disconnected mimic cabling from FIP.Carried out config programming change to delete smart terminal from system.Left system in normal working order.
MSA-DCS | WA3828347 | * Restrospective work order * Fire pump batteries not holding charge | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 24 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 09:22:00 | Pass | Replace pump batteries as requested
MSA-DFES | WA3575705 | BA Store (Front House) Hot water system is tripping circuit electrical breaker (240v) – No hot water | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-22 07:45:00 | Fail | No hot water in ba block got electrion to service parts tested and working
MSA-DFES | WA3575779 | dorm 5 bathroom showerhead leaking | CFRS Perth | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-26 12:00:00 | Pass | Replacing shower head in the dorm 5 bathroom. Tested, all works good, no leaks. Cleaned up the working area.
MSA-DFES | WA3575784 | Dorm 5 leaking cistern washer | CFRS Perth | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-26 13:46:00 | Pass | Servicing toilet cistern
MSA-DFES | WA3575897 | Level 1, mutiple lights out - 1x ladies toilet 1x light strip training room | South Metro Regional Office | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-25 15:15:00 | Pass | Locate faulty lights. Replaced faulty downlight with new. Gavin left site to collect a replacement light. Replaced faulty tubes and starters with new.
MSA-DFES | WA3575907 | Administration Building & external area - Multiple faulty lights (see long descrip for locations) | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-02 13:30:00 | Fail | Located 6 Lights throughout building that need attending to. 1 exit light needs to be swapped out in the hallway near the change rooms. There is 4 Fluro lights in the main building that are not working and some have missing diffuses. I recommended replacing with LED panels as there is already panels in these room and LEDs are the most suitable option and will reduce installation time. There are located- (2 in Lunch Room, 1 in Operational Office, 1 in FDP office) there is also a light out in the Applied training office that’s needs to be swapped. Will need to seek approval from PFM
MSA-DTAG | WA3575482 | Failed Hard Drive on CCTV Service 1 | Rockingham Justice Complex | GMP-BR-HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-09-01 08:53:00 | Fail | Rebuilt raid array and ring buggers system is now roking.. Required 4TB
MSA-DTAG | WA3575855 | Registry, kitchen - Kitchen faucet has snapped off at the base (may need to be replaced with new one | Armadale Courthouse | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-25 09:24:00 | Pass | COMPLETED
MSA-DTWD | WA3569720 | Sliding doors to cafe courtyard- beeping & sensor broken LHS exiting | Perth Campus B1 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 24 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-24 10:24:00 | Pass | On inspection, found battery fuse blown causing battery sound to alarm.Replaced faulty fuse, tested and adjusted, all ok.Advised management that sensor sensitivity is at its maximum. (Int) If problem occurs again, a new sensor is required.
MSA-DTWD | WA3571790 | Museum St Entry- Bollards broken | Perth Campus B1 | GMP-BR | Building | Steel Work (BU) | AWB Co. | 3 | CLOSE | 24 Aug 2020 | 2020-08-28 17:00:00 | 2020-09-18 14:00:00 | Fail | Bollards serviced and 1 x bollard replaced
MSA-DTWD | WA3571965 | A block L1 Link door to courtyard not closing properly, A B link door | East Perth Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-26 11:15:00 | Pass | Service to mortice lock A Block L1 door to courtyard
MSA-DTWD | WA3573274 | A block, G floor - lift not working | Joondalup Kendrew Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-25 00:00:00 | Pass | Reset lift
MSA-DTWD | WA3574474 | A block ground foyer Auto door not operating correctly -see notes | Mandurah Campus (formerly Peel) | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 09:51:00 | Pass | 1096451. Found door had dropped and was jamming on the floor causing door to reopen constantly, adjusted and re aligned door height, reset and checked over all ok
MSA-DTWD | WA3575050 | B block room B30 We have a broken tap | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 14:33:00 | Pass | Connect hot water and new isolation valve for hot only
MSA-DTWD | WA3575183 | N Block, Room N41 & N42- Water leaks around penetration where ducts pass through roof. | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 14:15:00 | Pass | Found 2x vent structures with perished silicone. removed all perished silicone and prepped areas. Applied new seals
MSA-DTWD | WA3575187 | F block, FG11 - Mortice lock completely broken (Will most likely need a new mortice lock?) | Carlisle Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-01 12:45:00 | Fail | F Block - Door Locks broken.Locks repaired and replaced.
MSA-DTWD | WA3575261 | Tower block ground floor male toilet flush button faulty. | West One Services | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-09-02 12:30:00 | Fail | Complete
MSA-DTWD | WA3575276 | Admin building meeting room 4 wall mounted hot water dispensing unit no water flow | West One Services | GMP-BR | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 13:34:00 | Pass | Tech closed this out in error - we have emailed Programmed to advise of this - needs approval for quotes before finishing off extremely slow out of the plv. Replaced plv, fitting and tibe. Put foam covering over tube as it’s outside. Zip hydroboil wallmount is dead, completely rusted tank. Kim would like us to quote to replace a like for like system. Waiting for approval on the quote Replaced with new capex asset installed new Zip Hydroboil 5 Litre BWU SERIAL NUMBER 2020070905029 - Asset Prog No A402011513 connected to existing filter system + drain and drip tray tested all good.
MSA-DTWD | WA3575303 | Tower block L4 damaged venetion blinds and check others for safety | West One Services | GMP-BR | Building | Windows (BU) | NEYLOR | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-09-24 12:00:00 | Fail | Job completed - no completion notes
MSA-DTWD | WA3575347 | Tower block L3 kitchen Zip auto boil unit not working | West One Services | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-25 12:25:00 | Pass | Hot pump fail on arrival, also safety solenoid not shutting off and flow meter not registering. After changing pump, solenoid and flow meter the strip sensor was reading that the tank was full when it was empty. Changed strip sensor on site, very small kitchen
MSA-DTWD | WA3575444 | T Block, Outside of room T114- water leaking from Air Con | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-25 15:33:00 | Pass | TRAVELLED TO SITE. SIGNED INTO SITE. CARRIED OUT SITESAFETY INSPECTION AND FILLED OUT APPROPRIATE PAPERWORK/FORMS/PROMAP ETC ETC. MET WITH MAINTENANCE ANDWAS SHOWN AREA THAT WATER HAD BEEN LEAKING AND CEILINGTILES WERE DAMAGED. GAINED ACCESS TO AREA AND REMOVED DAMAGED TILES. INSPECTED AND NO WATER OR WATER MARKS EVIDENT. WITH ASSISTANCE FROM SECOND TECH TO STEADY LADDER FURTHER INVESTIGATED AND FOUND MOISTURE AT PIPE SECURING HARDWARE WHERE INSULATION HAS NOT BEEN SEALED AT JOINT. USED SILVER TAPE TO SEAL AROUND SEVERAL JOINS IN INSULATION. CHECKED AND FOUND NO OTHER INDICATIONS OF WATER IN CEILING SPACE. CLEANED UP WORK AREA AS MUCH AS POSSIBLE. WAS INFORMED THAT CLEANERS WILL ATTEND AND MAINTENANCE TO ARRANGE FOR REPLACEMENT OF CEILING TILES. COMPLETED PAPERWORK AND LOGGED OFF JOB.
MSA-DTWD | WA3575476 | Block 8, EBT Office - Faulty power point | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-27 15:00:00 | Pass | Arrived on site, signed in, spoke to client about job that needed to be done and where to store the partitions and desks that were being removed , completed jsa, started pulling apart partitions and desks , removed comms cables from ducting in partitions leaving the plates and gpos on the ducting , pulled comms cable back up to existing ducting on wall and left them in there , removed all the work desks and put them in plant room on level 1, moved partitions to area client wanted them in office , cleaned and packed up work area , site happy ***job complete***
MSA-DTWD | WA3575506 | Tower block lift number 1 not working. | West One Services | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-24 15:43:00 | Pass | CONTROLLER - RELAY - STRIPPED,CLEANED,ADJUSTED
MSA-DTWD | WA3575618 | B Block, Room B005- Male toilet is blocked and is flooding into the passageway. | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 0 | CLOSE | 24 Aug 2020 | 2020-08-24 17:15:30 | 2020-08-24 15:20:00 | Pass | Used Drap jetter to clean out sewer main. Tested like and is now operating as normal.
MSA-DTWD | WA3575651 | A block, 3rd floor, storerooms A331a & A312a - Unable to unlock doors (Locks to be re- keyed to CF1) | Leederville Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-26 15:05:00 | Pass | gain entry to A331a & A312a storeroom doors and replace key barrels - keyed to CF1 key
MSA-DTWD | WA3575662 | S block L2 S200 Poor water quality reported, water testing required-see notes | Mount Lawley Campus | GMP-BR | Waste Management | Water Treatment (WM) | CAPIC - "Use vendor S12485" | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 11:30:00 | Pass | Certificate of Analysis has been sent through with the testing results as requested.
MSA-DTWD | WA3575685 | S block/wing, room S200 - Broken power socket; repair with new 20A 3P socket to be mounted on south | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-28 13:15:00 | Fail | Job complete
MSA-DTWD | WA3575717 | OCWA Nedlands, level 2 - faulty tap and water and water supply line to dental equipment | Mount Lawley Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 14:15:00 | Pass | Complete
MSA-DTWD | WA3575724 | B005 Clean up required in the Male toilets & passageway after a blocked toilet flooded the area. | Balga Campus | GMP-BR | Cleaning | Cleaning (CL) | AWB Co. | 0 | CLOSE | 24 Aug 2020 | 2020-08-24 18:16:24 | 2020-08-26 18:00:00 | Fail | 24th Aug – Extract water and treat with antimicrobial and deodoriser25th Aug – Check carpet & reapply antimicrobial and deodoriser (the carpet was still damp and customer had installed their own air mover)26th Aug – Check carpet, complete a final carpet clean and apply antimicrobial and deodoriser
MSA-DTWD | WA3575789 | N block, Level 2 - N225 Projector falling out of ceiling | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 24 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-31 09:32:00 | Fail | Resecured projecter In roof . No longer falling. Connected back projected and tested all working.job completed
MSA-DTWD | WA3575807 | C block C30 lift Doors on lift not operating correctly. | Midland Campus | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 13:21:00 | Pass | DOOR PROTECTION - PHOTOCELL - COMPONENT DUSTY, CLEANED
MSA-DTWD | WA3575826 | Level 3, next to N323- auto door - faulty/damaged closer, Repair closers as required | Perth Campus B1 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 11:30:00 | Pass | Removed faulty door closer and replaced with customer supplied ts83 closer, adjusted and tested upon completion and left in good working order.
MSA-DTWD | WA3575852 | L2 W211 Repair door closers ar required | Perth Campus B1 | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 12:14:00 | Pass | Re-secured top arm on door closer to room 211 as necessary, adjusted and tested doors upon completion and left in good working order.Also re-secured top arm as necessary to level 2 stairwell door, tested door upon completion and left in good working order.
MSA-DTWD | WA3575894 | Main switch room - electrical smell coming from the room | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-27 10:15:00 | Pass | Removed and replaced a number of electrical switchboard covers so that consultants could take pictures of circuit protection at Balga and Midland Tafe’s.
MSA-DTWD | WA3575901 | F block, FG31 - Emergency Exit Door not closing properly | Carlisle Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 16:15:00 | Pass | adjusted hinges and striker plate on door, replaced door closer.
MSA-DTWD | WA3575905 | L block, L010 - Repair/replace faulty door lock in L010 | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 24 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 12:15:00 | Pass | replaced lock
MSA-DTWD | WA3575909 | level 3 - Print screen area - No hot water | Perth Campus B6 | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 24 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-01 21:01:00 | Fail | Replaced circulating pump that wasn’t no working
MSA-DCA | WA3576464 | Investigate BMS faulty after power outage | Art Gallery of WA - James St-Administration Block (Block A)-Ground Floor-Plant Room | GMP-BR | Building | Materials (BU) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 16:30:00 | Pass | Arrived on site to find BMS off line, UPS with no power feed and battery back up empty. Safety tripped on GPO feeding UPS. Reset power, connected system on line. Multiple alarms active. Steam Boilers off line. FCU 2, 3, 4, 7 faults. RO plant faults. Reset all plant and monitored. Secured loose fill valve on feed tank. Alarms cleared.
MSA-DCA | WA3576546 | balustrade has come away from wall, need to be re-fix | Perth Cultural Centre Precinct - James Street Amphitheatre | GMP-BR | Building | Materials (BU) | ICS Australia | 0 | CLOSE | 25 Aug 2020 | 2020-08-25 16:58:26 | 2020-08-25 15:35:00 | Pass | Handrail reinstated
MSA-DCA | WA3576628 | revo work being carried suspect aspestos material need to be tested | PICA-Main Building-Level 1-Administration Office 1 | GMP-BR | Building | Internal Walls (BU) | Site Environmental & Remediation Services Pty Ltd | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-27 16:07:00 | Fail | Works completed and certificate of analysis sent to client
MSA-DCA | WA3576647 | Chiller controls failure | Collection and Research Centre Welshpool-Harry Butler Centre-Level One-Plant Room | GMP-BR | Refrigeration | Chiller (RE) | EQUANS Mechanical Services (WA) Pty Limited | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-09-09 15:30:00 | Fail | Please refer to attached Alerton service report for in depth analysis and applicable coding changes applied. During investigation it was identified that the ch2 do switch is intermittently faulting. A seperate quotation is to be submitted to remove and replace this switch.
MSA-DCA | WA3576758 | Cleaners room - Smoke detector fault. Detector in fault, system in alarm. | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Cleaners Cupboard | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Critical Fire Protection & Training | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 17:00:00 | Pass | Investigate faulty detector in cleaners cupboard
MSA-DCA | WA3576766 | Cleaners room - Exhaust fan in cleaners cupboard not working | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Cleaners Cupboard | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 16:00:00 | Pass | Fan was faulty and old. Replace with new 250mm exhaust fan, test all okay.
MSA-DCS | WA3575978 | Unable to lock/unlock critical spares cabinets | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 3 | CLOSE | 25 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-25 10:00:00 | Pass | Attended site and supplied and fitted new cabinet locks on Spares Cabinets in the Programmed Shed, as quoted to Mario Kovac.
MSA-DCS | WA3576019 | Jeelia, Cell A6- Cell light not working | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 10:00:00 | Pass | Tested light and light switch for A6 jeelia cell all ok
MSA-DCS | WA3576048 | Unit 2, Boiler Room- Hot water system has no hot water | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Boilertronics | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 07:33:23 | 2020-08-26 12:31:00 | Fail | Travelled to site and signed in. Burner has Ben faulting on LFL position 1. New pilot valve has been installed. Recommend a retune of the burner, especially pilot to prevent the loss of pilot flame. Burner faulting repeatedly at LFL position 1 or soon after. Opened burner and :- cleaned ignition electrode insulation andcable, cleaned burner head diffuser plate and flame rod, checked ignition spark and fan rotation. Reassemble burner.Check air damper is free. Reinstate flame rod cable into LFL terminal 24 and add earth to terminal 22. Test start ok.Check pilot combustion and found 19.8%O2. No more pilot fuel available. Dropped low fire air from 0.28kPa to 0.15kPaand adjusted main burner combustion to comply. Low fire 8.8%O2, high fire 4.9%O2 and fuel pressures matching dataplate. Air pressure switch now set 2mB. (As found, switch was at lowest setting) Small combustion rumble at lower firingrates (low fire to about 15%). After adjustments, no unintended faults while on site
MSA-DCS | WA3576057 | Unit 5, Control panel is flashing network error | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 25 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 11:30:00 | Pass | This (Node 133) alarm has been on Cell Call System for over Three months. It is work being undertaken as part of expansion project. Referred to DCS project manager Mr Ackland, who advised it is associated with Visits upgrade work.
MSA-DCS | WA3576058 | Unit 2, C wing grill is not opening when pressing the button | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 25 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-25 13:15:00 | Pass | ACTUAL START 25/08/2020 08:30 AM ACTUAL FINISH 25/08/2020 01:15 PMTravel to site Inspect Unit 2, C wing grill. Found gate in manual so put back into operation and found gate slamming on close. Found that the ball at the top of the limit has snapped off causing the gate to jam when closed. Left in manual release. Left site and travelled back to workshop to collect part required. Travelled back to site and installed. Tested several times, all fine.
MSA-DCS | WA3576101 | unit 2 Vesda fault on panel | Hakea Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 08:22:04 | 2020-08-25 11:56:00 | Pass | 25/8/20 MBLow airflow on pipe 3, A Wing on arrival.Inspected all Vesda sampling points in all cells on A wing. Found approx 80% of sampling points blocked with toothpaste or other materials. Cleaned out all A wing sampling points and vacuumed pipework out from Vesda unit end.Returned airflow to normal and reset system.
MSA-DCS | WA3576129 | gate house control Urn not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 13:30:00 | Pass | Replaced faulty Urn in gatehouse control
MSA-DCS | WA3576140 | Reception, Laundry Room- Ceiling Extraction fan not working | Melaleuca Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-09-02 11:15:00 | Fail | Investigated extraction fan found to be workingReplaced faulty indicator light
MSA-DCS | WA3576142 | Unit 2, upstairs plant room - Boiler hot water Pipe work is leaking (Flange seals Leaking) | Melaleuca Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 09:00:49 | 2020-09-30 17:00:00 | Fail | Travelled to site and completed tool check.Got approval to turn off hot water.Isolated hot water pumps.Closed valves in the boiler room.Drained the lines.Removed and replaced gaskets on the pump flanges, check valve flanges and filter flanges.Cut and replaced bolts on the filter flanges that had been leaking.Opened up valves on the system and bled the air out.Turned on the pumps.The water heater cycled on and off as normal once the water was flowing through the system again.Cleaned up work area.Signed out on site and completed tool check.
MSA-DCS | WA3576159 | grounds, fountain - Bore is not operating possible power supply problem at Front Dam/ Borehouse | Casuarina Prison | GMP-BR- HO | Mechanical Services | Pumps (MS) | Pumps n Pipes | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 15:30:00 | Pass | found damaged bleed lines on valve and pump. replaced cracked lines and valving.
MSA-DCS | WA3576181 | rear sally port gates in the kitchen Reed switch magnet broken | West Kimberley Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-09 14:29:00 | Fail | Modified reed switch bracket and replacedInvoice raised for costs to date
MSA-DCS | WA3576186 | House 1 C2 unit 3 cell call faulty | West Kimberley Regional Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-07 12:53:00 | Fail | Sourced replacement CI-CC attended site, installed CI-CC, still distorted.reinstalled previous CI-CC and checked CI-Hub, found damage to RJ45 connector.re-terminated and tested OK.CI-CC put into PFM stock onsite
MSA-DCS | WA3576239 | Unit 1, Cell B6- Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-31 13:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunks
MSA-DCS | WA3576247 | Unit 1, A1 - Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-31 10:00:00 | Fail | Attended site and carried out repairs to the damaged bed panels on bunks.
MSA-DCS | WA3576262 | Unit 1, A6 - Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | Schlager Construction Group | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-28 13:30:00 | Pass | Attended site and carried out repairs to the damaged bed panels on bunks.
MSA-DCS | WA3576263 | Emergency siren is not working | Roebourne Regional Prison | SPA-BR | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Aug 2020 | 2020-08-25 18:11:54 | 2020-09-02 16:30:00 | Fail | Job complete 20m figure 8 cable used from Seme off site store
MSA-DCS | WA3576270 | Unit 1 C2 Bed Panel Broken | Melaleuca Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Schlager Construction Group | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-28 13:00:00 | Pass | Attended site and carried out repairs to the damaged bed panels on bunks.
MSA-DCS | WA3576350 | Indigo terminal in the Security office is constantly turning off. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 10:41:37 | 2020-09-11 10:30:00 | Fail | No further faults reported unable to reproduce Fault.
MSA-DCS | WA3576367 | Outside office, Hinge broken on screen door | Warminda Hostel | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 10:59:19 | 2020-08-25 14:25:00 | Pass | Attended site and changed rivets in all hinges.
MSA-DCS | WA3576370 | outside tap is constantly dripping | Warminda Hostel | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 11:30:00 | Pass | Complete
MSA-DCS | WA3576534 | Air cond in bedroom 10 and air cond remote in bedroom 14 not working test and repair - see notes | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 11:30:00 | Pass | Faulty capacitor prevented compressor from running. Replaced capacitor and test ran units all operational at time of departure.
MSA-DCS | WA3576662 | kitchen light not working above prep bench behind bain marie | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-25 15:30:00 | Pass | Investigate and repair kitchen light
MSA-DCS | WA3576695 | Unit 7, D wing - door latch that holds open the outer B wing door is loos. | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-09-08 12:00:00 | Fail | Require Parts.Re install floor mount brackets and replace hold open door stops and fixings.
MSA-DCS | WA3576701 | Unit 14, Control room - Damaged tiled carpet squares in Control Room. | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-11-02 14:30:00 | Fail | NEW CARPET TILES INSTALLED
MSA-DCS | WA3576769 | kitchen faulty light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 14:30:00 | Pass | Repaired lights
MSA-DCS | WA3576772 | laundry Power point for clothes dryer on wall above dryer in laundry not working | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 13:30:00 | Pass | Checked power
MSA-DCS | WA3576788 | canteen, alarm pad is not working canteen cannot be alarmed | Wooroloo Prison Farm | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Aug 2020 | 2020-08-25 19:45:58 | 2020-08-25 18:00:00 | Pass | Stand alone burglar alarm panel (unknown brand) can’t be armed. Found mains power was off , turn on the power and manage to arm the area and test the alarm. Advice SO gatehouse to request for the upgrade of the controller and keypad. Besides from being old alarm systems it was installed unsecured in the area, main power adaptor was accessible easily. Can be replace with Bosch 3000 or equivalent .
MSA-DCS | WA3576807 | the security system is crashed and not working | Boronia Pre-release-Security Perimeter | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 25 Aug 2020 | 2020-08-25 21:11:40 | 2020-08-26 10:00:00 | Fail | Travelled to site. Checked logs for controller 1 and 2. All logs checked ok and had no connection issues overnight. Issue was related to network switch port. Switch may require replacement if issue re-occurs. Tested controller functions and fence alarms and all tested ok. Job complete
MSA-DCS | WA3578222 | Unit 5, Faulty Button in the Control Room for B wing grill.- see notes below | Casuarina Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-10-26 15:30:00 | Fail | Replaced faulty button
MSA-DFES | WA3576390 | Disabled toilet- Cistern internal flush mechanism leaking,causing water to leak onto the floor. | CFRS Murdoch | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-27 08:14:00 | Pass | Servicing toilet cistern
MSA-DFES | WA3576800 | Ground floor, toilet 1 - leak at he rubber seal where the Pipe from the cistern meets the Pan – only | Emergency Management Network (WAERN) Project | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 10:30:00 | Pass | Replace 2 key seals due to both were cracked and leaking
MSA-DFES | WA3581392 | **Retrospective work order** Zone 18 R/S App bay one roller door | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 20:50:00 | Pass | FIREFIGHTERS ONSITE. ROLLER DOOR OPEN AS CAUSE, THEY HAD BEEN OUT TO SITE. THEY ARE HAPPY FOR ME TO LEAVE. INFORMED WAOC OF OUT COME
MSA-DTAG | WA3576084 | ground FIP Technician required to assist Australian HVAC - see notes | Joondalup Courthouse | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-29 11:00:00 | Pass | Issue rectified
MSA-DTAG | WA3576130 | Chambers of Mazza JA - Flickering lights despite recent replacement – suspect wiring fault | Supreme Court | GMP-BR-HO | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 11:15:00 | Pass | Replaced tube in Mazza’s chamber
MSA-DTAG | WA3576201 | Family Violence Office- Light blub not working | Rockingham Justice Complex | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-01 10:00:00 | Pass | Replaced faulty lamps in family violence office
MSA-DTAG | WA3576342 | Ground, Court 1 Various ceiling Lights not working- see notes | Mandurah Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 09:45:00 | Pass | Renewed 6 x blown tubes, 6 x starters and 2 x burnout ballast in court 1. Check and tested. All in working order
MSA-DTAG | WA3576802 | Registry, Kitchen - Hot water unit in the kitchen is releasing large amounts of water | Armadale Courthouse | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-09-01 15:30:00 | Fail | Complete
MSA-DTWD | WA3575980 | Lvl 1, A Block, Room A126- Light is not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 25 Aug 2020 | 2020-08-25 17:00:00 | 2020-08-25 14:30:00 | Pass | Job complete
MSA-DTWD | WA3575988 | Landing above gallery- Carpet is lifting | Perth Campus B5 | GMP-BR | Flooring | Carpet (FL) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 25 Aug 2020 | 2020-08-31 17:00:00 | 2020-10-02 09:00:00 | Fail | Carried out repair works as requested by site
MSA-DTWD | WA3576008 | Fashion area- Back of lights are blown | Perth Campus B6 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 12:30:00 | Pass | Attended site and signed in. Talked to Pfm about job. Went to b6 and investigated how many lights were out. Replaced various tubes and started around the fashion area in b6 level 3. Tested all ok. Completed paperwork and Signed out. Job complete.
MSA-DTWD | WA3576126 | Tower block lift number 1 not working. | West One Services | GMP-BR | Lifts | Lifts (LI) | OTIS ELEVATOR COMPANY PTY LTD | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 10:35:00 | Pass | Upon arrival at site, the technician performed the following:CONTROLLER - RELAY - RUNNING ON ARRIVAL
MSA-DTWD | WA3576132 | L2 room 285 lect theatre light surround fallen down | Perth Campus B2 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 10:15:00 | Pass | Attended siteGot keys for accessInspect pelmet coverContact facilitiesProjector screen had been replaced by IT and cover left off hingesRe fit and hang cover back on hingesClean upReturn keys
MSA-DTWD | WA3576133 | F Block, Flood light is faulty | Balga Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 15:56:00 | Pass | Repalced faulty floodlights F block.job completed
MSA-DTWD | WA3576138 | E Block, E30 Small Scale Kitchen – Broken tap, leaking constantly | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-25 17:18:00 | Pass | Tap wouldn’t shut off replaced
MSA-DTWD | WA3576145 | L3 A356 Replace broken glass panel-contractor on site | Perth Campus B6 | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 16:30:00 | Pass | ATTENDED SITEREGLAZED BROKEN PANEL TO ROOF6.38 CLEAR LAMINATED SAFETY GLASS1-1300 X 11505 TUBES OF SILICONE USED3 MEN REQUIRED
MSA-DTWD | WA3576198 | A block ground A009 Kendrew Investigate Security system fault (Ademco) | Joondalup Kendrew Campus | GMP-BR | Security | Monitoring (SE) | BJ SYSTEMS | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-26 13:45:00 | Pass | Locate Ademco panel and keypads in C & A Block. Test and check Ness dialler and sims for each system (3). System dialling and reporting ok. System is reporting to ED Sec on different system ID:A Block 0821 is 5037A Block 0823 okC Block 0824 is 1035David to send to ED Sec
MSA-DTWD | WA3576317 | A block L3 A317 Repair internal downpipes in A317/ A319 | Leederville Campus | GMP-BR | Roofing | Guttering (RF) | Midolo Building Services | 3 | CLOSE | 25 Aug 2020 | 2020-09-01 17:00:00 | 2021-02-25 09:00:00 | Fail | REPAIRS TO INTERNAL DOWNPIPES COMPLETED
MSA-DTWD | WA3576446 | G block behind bricklaying Workshops, the water fountain near bricklaying is leaking | Clarkson Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-09-16 10:30:00 | Fail | Have ordered parts. Completed
MSA-DTWD | WA3576531 | U Block, Glass storage compound - Repair paving | Balga Campus | GMP-BR | Paving & Roadworks | Paving (PR) | M Construction (WA) | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-09-22 09:30:00 | Fail | Job complete
MSA-DTWD | WA3576581 | D Block, D3 Pastry Lab – Emergency Exit Light not working | Bentley Campus | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | AWB Co. | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-09-07 11:45:00 | Fail | Arrived on site, signed in, located area light was required, completed jsa, ran cable for light and fitted/ terminated exit light , isolated circuit, joined cable to circuit , re energised circuit, tested light , light fully operational , spoke to pfm about gpo being added in at the sign in area , installed gpo , tested all working ***job completed ***
MSA-DTWD | WA3576632 | A block ground lift shaft student has dropped keys between lift | Joondalup Kendrew Campus | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 15:25:00 | Pass | Got keys from pit returned to customer Adjusted weight on landing door Ran and tested Left in service
MSA-DTWD | WA3576636 | C Block, G Floor, Room C020- Door handle does not turn anymore to open the door | Joondalup Kendrew Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 10:22:00 | Pass | Job completed - replaced handles on CO20 internal store
MSA-DTWD | WA3576682 | Room A3- Faulty fluros | Armadale Campus? 45 Commerce Ave | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-31 15:45:00 | Fail | Replaced faulty Fluor tube and ceiling tile.
MSA-DTWD | WA3576690 | H block - Clear tree roots from sewage pit at the rear of H Block. | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-09-03 14:55:00 | Fail | Cleared drains and pit
MSA-DTWD | WA3576722 | N block N007 Repair external damaged wall panel - see notes | Balga Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-09-01 12:00:00 | Fail | Toby Bindon (01/09/2020) - Work NoteCollected materials. Checked asbestos register, listed as fibre cement. Still treated as asbestos, set up work area and exclusion zone. Put on full Acm ppe, installed colorbond patch over hole. Sealed in place. Removed broken board. Tidy area, packed away tools. Complete
MSA-DTWD | WA3576791 | A block A001.1 Alarrn panel Fault Zone 53 | Balga Campus | GMP-BR | Security | Monitoring (SE) | Casa Security Pty Ltd | 2 | CLOSE | 25 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 09:30:00 | Pass | Replaced batteries in sensor & fixed tamper switch
MSA-MRWA | WA3576232 | L6 ladies toilet Multiple flush buttons not working, inspect and remediate. | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 25 Aug 2020 | 2020-08-26 17:00:00 | 2020-08-25 16:40:00 | Pass | Repaired faulty cisterns
MSA-DCA | WA3578250 | Second light pole from Polly on the right has a flickering spot light-see notes | Perth Cultural Centre Precinct - Cultural Centre Square | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 11:30:00 | Pass | Faulty flood replaced with new LED
MSA-DCA | WA3579668 | Step lights are not working, please investigate | Perth Cultural Centre Precinct - James Street Amphitheatre | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 11:30:00 | Pass | Repaired step light control timer in PCC
MSA-DCA | WA3579834 | 2x flood lights not working | Perth Cultural Centre Precinct - Play Space | GMP-BR | Electrical | Lighting, External (EL) | Techworks Electrical | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-27 11:00:00 | Pass | Works progressed as far as possible, however fault finding was creeping into the confines of WA Museum construction area. once construction has finished fault can be remedied.. asked to close off work order until then.
MSA-DCA | WA3581245 | Cleaners Cupboard -Investigate leaking hot water unit in. it feeds the staff lunchroom | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor-Cleaners Cupboard | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-31 15:00:00 | Pass | Replaced and commissioned hwu
MSA-DCS | WA3578177 | Unit 3, Cell A11 - bed and main light not working | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 26 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-27 09:00:00 | Pass | Investigate and repair unit 3 A11 lights
MSA-DCS | WA3578181 | Zone 7- Microwave set 2 fault | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 07:17:09 | 2020-10-01 10:30:00 | Fail | Replaced zone7 set 2 with new ultrawave set, seme stock used. All installed programmed and tested ok. Job complete
MSA-DCS | WA3578183 | Zone 3- outer mircphonics cable fault | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 07:18:30 | 2020-08-26 07:19:00 | Pass | No end of line resistance measured at EC. Replaced 4 Splice kits and a number of cable ties. Tested ok back to the gatehouse. Parts used:4 x Splice kits Consumables
MSA-DCS | WA3578185 | Camera 43 - external camera no movement | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 07:19:20 | 2020-08-26 12:00:00 | Pass | Image ok, no PTZ. Traced fault to surge arrestor in external EC. Replaced with site spare. All PTZ functions tested ok at gatehouse.
MSA-DCS | WA3578191 | Gate house- download footage of door 6 19/08/20 @ 0700hrs | Casuarina Prison | WSM-BR-SITE | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 11:00:00 | Pass | Additional details provided for CCTV download. Additional video requested, over and above that already downloaded, from different cameras in the Gatehouse. Searched for and downloaded requested video. Data supplied to security section on supplied USB memory stick.
MSA-DCS | WA3578196 | Unit 2, Cell D5- Sink overflowing due to blockage | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-28 09:30:00 | Pass | Nill
MSA-DCS | WA3578202 | Waste water chlorine plant not dosing chlorine | Karnet Prison Farm | GMP-BR- HO | Waste Management | Water Treatment (WM) | TRILITY Solutions Pty Ltd | 2 | CLOSE | 26 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-26 11:23:00 | Pass | Attended site and changed chlorine gas cylinder
MSA-DCS | WA3578207 | Jasper, Cell A06- Shower constantly running | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-28 11:05:00 | Pass | Replaced faulty parts in the plumbing duct
MSA-DCS | WA3578447 | Kitchen cooking bell tap has broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-10-16 11:10:00 | Fail | Returned 16/10 and fitted required parts to kettle & tested ok.
MSA-DCS | WA3578692 | Unit 5, house 10, bedroom 3- air con not working | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-21 08:41:00 | Fail | COMPLETED
MSA-DCS | WA3578755 | Unit 4, 7x walkway lights not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-04 09:00:00 | Fail | Replaced walkway lights
MSA-DCS | WA3578832 | Unit 4, L Block, Cell L6- Top bunk light not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-04 09:30:00 | Fail | Replaced bed light
MSA-DCS | WA3578836 | kitchen slicing thickness handle faulty | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-23 10:30:00 | Fail | Kitchen meat slicer seized. Check slicer, remove for repairs. Dismantle, replace bearings, auto relay index dial. Repair seized Thickness device, lube & sharpen, test. Return to kitchen.
MSA-DCS | WA3578860 | Unit 4, L Block, Dayroom light not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-04 10:30:00 | Fail | Replaced lights in day room
MSA-DCS | WA3578884 | Unit 5, House 3- GPO between C3 & C4 not working | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-04 10:45:00 | Fail | Reset power and tested
MSA-DCS | WA3578929 | Unit 5, House 10- GPO behind microwave melted | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-04 11:15:00 | Fail | Replaced damaged PowerPoint
MSA-DCS | WA3578953 | Unit 5, house 4- Dayroom/lounge light not working | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-04 11:45:00 | Fail | Replaced oyster light
MSA-DCS | WA3578971 | Unit 5, house 7- Bedroom 2, light switch cracked | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-04 12:00:00 | Fail | Replaced cracked light switch
MSA-DCS | WA3579001 | Visits SW camera is showing picture in black and white. | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 09:00:00 | Pass | Power reset camera, confirmed color image restored
MSA-DCS | WA3579095 | Gatehouse- Blue random search light stuck on | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 08:35:16 | 2020-11-11 16:02:00 | Fail | Repaired faults with random blue light alarm.Monitored for correct operation.Tested OKJob CompleteParts (SEME Stock):PSUConsumables
MSA-DCS | WA3579554 | Unit 4C, Kitchen- floor is blubbing | Wooroloo Prison Farm | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-16 11:45:00 | Fail | DAMAGED SECTION OF FLOOR REMOVED/ REPLACED WITH NEW
MSA-DCS | WA3579860 | SITE COST Unit 6, A wing - flooding in A wing, Toilets overflowing when flushed. | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 13:04:04 | 2020-09-23 13:15:00 | Fail | Nill
MSA-DCS | WA3580392 | Level 3, Glass Door not closing correctly, making a noise like glass hitting metal | East Perth | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 09:24:28 | 2020-08-26 14:45:00 | Pass | Technician attended the site of 30 Moore Street, East Perth, WA to the Level 3 Auto Door W21169 on 26/08/2020. Following a full test and inspection of door components found fault to be the door is noisy and grinding. Technician has looses bolts on drive and also put a soft stopper on the close tested and now it's quiet. Full test and inspection of door function completed prior to leaving site.
MSA-DCS | WA3580493 | SITE COST SHU (9) - Control Room Control monitor not working, | Casuarina Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 13:31:23 | 2020-08-26 15:03:00 | Fail | Sourced HDMI extender, 2x HDMI cables and wirless keyboard and mouse.Re-attended site and installed.Labelled all monitors and corresponding Extenders/KVM.Installed wireless keyboard and mouse and removed excessive cabling.Tested CCTV system, all monitors operational and officers able to select cameras with mouse
MSA-DCS | WA3580533 | Unit 7, H6 - external light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 09:33:43 | 2020-08-26 11:30:00 | Pass | Replaced light switch
MSA-DCS | WA3580649 | Unit 8, Rear secuirty light not work | Hakea Prison | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 09:39:20 | 2020-08-28 15:00:00 | Fail | Repaired lights
MSA-DCS | WA3580655 | Unit 7 S wing light Storeroom light not working | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 09:35:03 | 2020-08-26 12:30:00 | Pass | Repaired light
MSA-DCS | WA3580658 | SHU (9)- Drain cover at the east side between SHU & infirmary is missing | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-10-09 15:00:00 | Fail | Nill
MSA-DCS | WA3580673 | Unit 6 N2 Personal lock faulty | Hakea Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 09:46:06 | 2020-08-28 15:15:00 | Fail | 26/08/2020. Attended site. Inspected lock, beyond repair. Replacement needed.28/08/2020. On site. Supplied and fitted replacement lock.
MSA-DCS | WA3580676 | unit 7, H24 - cell toilet will not flush | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 09:46:10 | 2020-08-26 13:30:00 | Pass | Replaced inlet valve and outlet washer
MSA-DCS | WA3580681 | unit 7, H11 - cell basin blocked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 09:51:57 | 2020-08-26 14:22:00 | Pass | Plunger used to unblock basin removed trap removing knifes and sugar packets
MSA-DCS | WA3580683 | Unit 10, Cell D9- Toilet constantly running | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 13:47:00 | Pass | Fixed leaking toilet
MSA-DCS | WA3580698 | Unit 8, A8 - toilet continually leaking | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 09:57:44 | 2020-08-26 15:30:00 | Pass | Replaced top entry invis inlet valve and out let washer
MSA-DCS | WA3580712 | Movements - toilet light turning itself off | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 10:03:24 | 2020-08-27 08:00:00 | Pass | Repaired light
MSA-DCS | WA3580755 | Main Kitchen - Rationale oven- not working | Karnet Prison Farm-Prisoner Accommodation Huts Unit 1 | GMP-BR- HO | Equipment | Catering Equipment (EQ) | CPB ELECTRICAL SERVICE | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 10:17:59 | 2020-11-11 15:30:00 | Fail | 26/08/20Called as requested to the oven not working correctly not finishing the cleaning cycle. Found the remineralization filter blocked due to the hard water bypass be turned on. Left both oven on hard water bypass until new filters we can be supplied and fitted. Parts required 2 x remineralization filters11/11/20Attended kitchen Fitted filters and turned off both bypass, found 1 x pressure tank turned off. Turned on and checked system for leaks.
MSA-DCS | WA3580756 | Unit 5, Cell D10- Basin is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-28 10:30:00 | Pass | Nill
MSA-DCS | WA3580761 | Unit 1, D wing, Cell D01 & D02 - sinks are blocked and needs to be rectified. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 15:00:00 | Pass | Nill
MSA-DCS | WA3580830 | Unit 13, Cell B7- Shower is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Midolo Building Services | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-31 11:45:00 | Pass | SHOWER SCREEN RE SEALED
MSA-DCS | WA3580893 | industries DO gate lock faulty | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 15:08:36 | 2020-08-26 13:10:00 | Pass | Replaced faulty lock on Industries gate adjusted gate and fitted new locking strike
MSA-DCS | WA3580898 | SITE COST Main kitchen door lock faulty | Bandyup Prison | WSM-BR-SITE | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 15:10:48 | 2020-08-26 13:10:00 | Pass | Replaced lock on Office door in Kitchen
MSA-DCS | WA3580919 | Training Demountable, North East Corner- Drain Pipe Broken & soak well collapsed | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-03 18:00:00 | Fail | There is nothing there for nothing to be broken work order is they want soakwell and down pipes installed to demaintanle waiting for confirmation from programmedInstalled x4 soakwells and connected up down pipes and cleaned out gutters
MSA-DCS | WA3580920 | unit 6, B wing - last light down the wing is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 12:00:00 | Pass | Repaired light
MSA-DCS | WA3580922 | Unit 4, Regi Area - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 13:00:00 | Pass | Repaired light
MSA-DCS | WA3580931 | Reset centre Reception Area Continuos humming sound coming from PA Speaker | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 10:00:00 | Pass | PA calls done from gatehouse via the telephone system to RESET centre. All internal and external speakers buzzing. Repaired fault with line isolator. Adjusted volume as per the wishes of the RESET staff. Tested ok.
MSA-DCS | WA3581038 | Unit 6, Officers computer room- Carpet is ripped | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-11-10 14:15:00 | Fail | DAMAGED TILES REMOVED & REPLACED WITH NEW
MSA-DCS | WA3581041 | Unit 4A, Cell 43- Bed light not working | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 13:00:00 | Pass | Replaced bed light
MSA-DCS | WA3581075 | Gatehouse - Systems failure | Melaleuca Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 17:05:20 | 2020-11-09 12:30:00 | Fail | EBI , MDAS , Keywatcher and Cell call systems rectified and fixed after power failure on site. Replaced defective Honeywell IP fix dome camera with new Axis P3245 ( sallyport CAM 051 ). Job completed.
MSA-DCS | WA3581113 | Unit 5, House 10- Cell call faulty stuck on | Bandyup Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 17:40:01 | 2020-09-04 14:30:00 | Fail | Travelled to site and replaced unit 5 house 10 with new redback PA amplifier. All replaced and tested ok. Job complete
MSA-DCS | WA3581118 | Generator- transfer pump running faulty | Wooroloo Prison Farm | GMP-BR- HO | Equipment | Compressors, Generators (EQ) | CUMMINS SOUTH PACIFIC PTY LTD (ACC No 5501269) | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-08 15:00:00 | Fail | System working correctly
MSA-DCS | WA3581122 | SITE COST Unit 16 control room self closing door mech on top of door hard to open/close | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | AAA Ability Locksmiths | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 17:46:16 | 2020-08-26 17:45:00 | Pass | Attend site Casuarina prison Unit 16 A&C wing control room door.Remove door closer arm to check opening and closing of door - Hinges are binding and prevent door from closing.Adjust hinges - door still not closing.Remove hinges, dismantle and clean grease from hinges.Top hinge was jamming/binding and has previously had the hinge pin filed and the bronze bush has gouge marks.Reassemble and install hinges, test door open and closing function - OK.Reinstall door closer arm and check door closer - OK.NOT A LOCK OR DOOR CLOSER WARRANTY ISSUE.
MSA-DCS | WA3581155 | Unit 2 B, POD 1 - when the the verandah lights are turned off the ablutions lights also turn off | Wooroloo Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 10:30:00 | Pass | Replaced cabling and light switch for lighting
MSA-DCS | WA3581293 | Visits - no communication in the non contact booths | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-12 09:33:00 | Fail | Attended site, repaired intercom server and monitored for correct operation.Tested OKJob CompleteParts:Consumables
MSA-DCS | WA3581302 | Unit 2 CG wing air lock door not locking | Melaleuca Prison | GMP-BR- HO | Building | Doors (BU) | AAA Ability Locksmiths | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 21:36:20 | 2020-08-26 19:45:00 | Pass | After Hours Attendance. Aluminium Framed Glass Door itself is out of alignment and locking side has dropped causing misalignment between lock and electric strike. Door lifted and hinges tightened to restore normal function as best we can, but really requires replacement of door.
MSA-DCS | WA3581808 | Kitchen - 3 combi ovens not working, eletrical fault | Wooroloo Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 20:00:00 | 2020-08-26 18:00:00 | Pass | Tested ovens and reset power supply
MSA-DFES | WA3580241 | ground W/S stores office Card Pass Swipe is not working properly | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 16:50:00 | Pass | 26/8/20 - Dylan ParslowFound door not responding to commands.Reset controller and tested, card access working.
MSA-DFES | WA3580955 | Applied Training - Fault in plumbing check valves and volute in pump #2 bottom dam | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 17:00:00 | 2020-11-05 11:36:00 | Fail | Malcolm Thompson have attended and completed all works.
MSA-DFES | WA3580962 | Water leak near the meter- see notes below | VFRS Bassendean | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 15:30:00 | Pass | Located to site to repair burst 20 mil copper of the meter due to tree roots has cracked the line and replaced with brand-new copper tested and hold him.
MSA-DFES | WA3581002 | No power at the site | VFRS Bassendean | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 16:01:22 | 2020-08-26 14:15:00 | Pass | Arrived on site. Spoke to Nick from Programmed about the issue. Further investigation found that lighting circuit breaker had been nuisance tripping. Replace with new circuit breaker. All working.
MSA-DFES | WA3581177 | Repair 4 damaged fence sheets & rusted posts following storm damage | VFRS Secret Harbour | GMP-BR | Building | Steel Fencing & Gates (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-04 15:04:00 | Fail | Works have been completed waiting on BRAF Approval
MSA-DFES | WA3581212 | Radio Coms kitchen - Hot water seem to be to hot, unable adjust (seem hot enough to cause a burn) | DFES Regional Office - Belmont | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-27 08:30:00 | Pass | Check and adjust hot water in comms kitchen. Unit is 13yrs old and may require replacing soon, would fit tempering valve.
MSA-DFES | WA3581263 | Ground -No water supply, Investigation of water supply from property mains to building | VFRS Bassendean | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 10:45:00 | Pass | Reconnected water supply to building
MSA-DTAG | WA3580400 | 1903 lower ground level Water running constantly in one toilet – suspect cistern fault. | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 12:40:00 | Pass | Replaced inlet valve
MSA-DTAG | WA3580694 | 1987 L2 Chambers 2 (Justice Archer) Faulty/missing lock to bathroom inside chambers. | Supreme Court | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-10-02 17:55:00 | Fail | First attendance - Attend site, view and take pictures of door to have lock replaced / installed for correct operation to return with client requested lock. Second attendance - Installed new indicator bolt.
MSA-DTAG | WA3580929 | Hay St End, Lvl 4, CBU- Plaster has detached from office wall, patch & paint required | Central Law Courts | GMP-BR-HO | Painting | Internal (PA) | PPM Project Painting & Maintenance | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-27 15:15:00 | Pass | Patched and painted wall
MSA-DTAG | WA3580983 | Level 10, front counter - Mutiple faulty/flashing lights (locations in long descrpiotion) | Westralia Square | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 12:00:00 | Pass | Replaced blown lamps in multiple Areas
MSA-DTAG | WA3581048 | External Door 14,North East corner of building.- Graffiti on steps | Supreme Court | GMP-BR-HO | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-27 12:30:00 | Pass | Removed graffiti
MSA-DTAG | WA3581141 | Lvl 6, Prisoner Review Board Office- Slight leak from fire hydrant system pipe | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-01 15:00:00 | Pass | Repairs leak in hydrant main on level 6 prisoner review board
MSA-DTAG | WA3581167 | L4 male toilets Digital lock not responding to door code - see notes | Central Law Courts | GMP-BR-HO | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 26 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-26 16:30:00 | Pass | Attended site, gained entry to locked staff toilets, L4, serviced lock, changed batteries, reset combinations to existing.
MSA-DTAG | WA3581211 | Level 4- Community Justice Services damaged to ceiling - see notes | Central Law Courts | GMP-BR-HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 09:00:00 | Pass | DAMAGED CEILING TILES REPLACED
MSA-DTWD | WA3578212 | A Block, Room A111, Female toilet student services- light not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 26 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 08:00:00 | Pass | Arrived on site, signed in, located light (actually in male toilet ,all lights in female toilets were working), completed jsa, pulled off cover of light fitting , removed old compact Fluros, replaced with new Fluros , re fitted cover , light now operational, cleaned up work area , completed paperwork, signed out **job complete***
MSA-DTWD | WA3579636 | RPZ front of campus - its badly leaking water, | Clarkson Campus | GMP-BR | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 0 | CLOSE | 26 Aug 2020 | 2020-08-26 12:55:16 | 2020-08-26 13:15:00 | Fail | COMPLETED
MSA-DTWD | WA3580797 | Admin lunch room - bill drinking unit, light flashing | Naval Base | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 12:34:00 | Pass | Tap operating by itself. Replace faulty tap. All ok
MSA-DTWD | WA3580822 | B Block, Disabled toilet - Call button does not work- See further info below | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-10-02 11:00:00 | Fail | Attended site. Replaced faulty power pack controller for assistance button in disabled toilet B block ground floor. Tested to see if it works. Job complete.
MSA-DTWD | WA3580936 | B block B005 Urinal in the Male toilet is constantly running. | Balga Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-22 12:15:00 | Fail | Replaced old leaking cistern and isolation valve
MSA-DTWD | WA3581037 | Block 3 - 2 pendant GPO broken | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 15:00:00 | Pass | Arrived on site, signed in , spoke to client, located gpo, completed jsa , went to wholesaler to get gpo , only had orange but checked with site and they were happy with that , isolated power , changed gpo to new , re energised and tested , re hung both gpos , cleaned up work area , completed paperwork **job completed ***
MSA-DTWD | WA3581039 | Side enrty door - door lock not working wont open and close | Armadale Campus - 145 Jull Street | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-27 13:10:00 | Pass | Entry door locks - hard to open and close.Locks serviced and cylinders re:pinned.
MSA-DTWD | WA3581043 | undercover work area, brick laying - South corner, the down pipe is broken on the pillar | Clarkson Campus | GMP-BR | Building | Materials (BU) | AWB Co. | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 09:30:00 | Pass | COMPLETED
MSA-DTWD | WA3581102 | tower block L4 damage to walls and wallpaper | West One Services | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-09-10 14:30:00 | Fail | Touch up painting to wallpaper level 4
MSA-DTWD | WA3581136 | B Block, B2308 - Leaking Tap | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-28 11:13:00 | Pass | Fix leaking taps
MSA-DTWD | WA3581138 | Level 2, room 255 - Repar window hardware as required | Perth Campus B2 | GMP-BR | Building | Windows (BU) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-30 12:45:00 | Fail | ATTENDED SITE TO ASSESS WORKS REQUIREDRETURNED LATER DATE TO SUPPLY & FIT 3 NEW LOCKS AND BOLTS KEYED ALIKE TO 3 ROOMS2 MEN & HARNESS REQUIRED
MSA-DTWD | WA3581175 | N block L1 N117 faulty lock to cupboard-see notes | Mount Lawley Campus | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-28 11:20:00 | Pass | Attended. Unable to access N117 as class in progress.Sandy believes this job has been cancelled. It should have been a fresh fit of a cupboard lock but the person who requested the job sent an email on Wednesday to Steve to cancel. Steve has been on holiday from Thursday returning on Monday. Sandy has sent an email to Steve to confirm if the job is to be cancelled.-No need to return, mark job as completed.
MSA-DTWD | WA3581265 | Level 2, kitchen behind library - dishwasher leaking | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-27 13:00:00 | Pass | No leaks of dish washer
MSA-DTWD | WA3581270 | Level 1, showers 20 L1 - Low pressure - hot water barely warm | Perth Campus B2 | GMP-BR | Plumbing & Drainage | Materials (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-27 16:07:00 | Pass | Fix water pressure issues
MSA-DTWD | WA3581289 | B block, Level 1, B114 Electrical compound - Fault with electrical switchboard | East Perth Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 26 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 11:30:00 | Pass | Work Complete.
MSA-MRWA | WA3580971 | Bridge compound ground floor - Water tap is constantly leaking/dripping and cannot be turned off. | Materials Engineering Branch | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 26 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-27 12:32:00 | Pass | Relaced leaking hose tap. Unable to fond isolation valve for that particular tap. Agreed with the management to turn the water off and carry out the plumbing maintenance
MSA-DCS | WA3581313 | Transponder failure for educational vocational workshop unit | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | General Building (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Aug 2020 | 2020-08-31 17:00:00 | 2020-10-01 10:38:00 | Fail | Modified MDAS system to increase data communication efficiency and reliability. Performed stress tests on all transponders and confirmed reliable high speed communication. Performed backups and tested OKJob Complete
MSA-DCS | WA3581407 | BA Store West, Storeroom- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 09:00:00 | Pass | Repaired BA room lights
MSA-DCS | WA3581410 | Unit 7, Cell H24- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 10:30:00 | Pass | Repaired light
MSA-DCS | WA3581411 | Unit 5- Cell A17- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 09:30:00 | Pass | Repaired light
MSA-DCS | WA3581431 | Unit 5, Cell D7- Water leaking from sink basin | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-28 11:30:00 | Pass | Nill
MSA-DCS | WA3581432 | SHU East wing, Cell B7- Toilet flush botton not working | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 07:46:18 | 2020-08-27 11:33:00 | Pass | nil
MSA-DCS | WA3581433 | Unit 6, Cell A12- toilet flooding when flushing. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 27 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 14:00:00 | Pass | Nill
MSA-DCS | WA3581436 | MPU & SHU- Cell call system showing Network error. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 07:49:26 | 2020-08-27 11:30:00 | Pass | This (Node 133) alarm has been on Cell Call System for over Three months. It is work being undertaken as part of expansion project. Referred to DCS project manager Mr Ackland, who advised it is associated with Visits upgrade work.
MSA-DCS | WA3581438 | Unit 4, Cell D9- window shutter is stiff and will not close | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 27 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-02 14:00:00 | Pass | RE NEW SPIRAL BALANCES AND REPAIR SASH
MSA-DCS | WA3581441 | Unit 2, C Wing, Cell C3- Viewing window surround on the inside of the cell is breaking off | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 27 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 15:00:00 | Pass | REPAIRED & RE SET FRAMEWORK
MSA-DCS | WA3581463 | Kitchen- small hot box switch not workiing | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-27 13:45:00 | Pass | Replaced main switch, thermostat & knob. Test operation ok
MSA-DCS | WA3581478 | Unit 2 B/D wing flourescent light outside control room in wing - exposed wires and missing bulb | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-01 07:30:00 | Pass | Removed damaged light in unit 2 b/d day room
MSA-DCS | WA3581483 | Woodwork - Camera 51 has a bad picture and flickers | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-11 10:30:00 | Fail | Attended site to continue with fault finding. Located problem to be the faulty Fiber receiver in equipment room and faulty Fiber patch lead in workshop area. Replaced with new parts and tested all ok. Fiber receiver 702R X 1, Fiber patch lead DSTST2M-MM X 1.
MSA-DCS | WA3581488 | ISU- intercom has network error | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 08:33:32 | 2020-08-27 15:30:00 | Pass | Alarm messages on the B wing system after power outage. Cleared all alarms. Tested an intercom from each wing. All tested ok.
MSA-DCS | WA3581499 | Kitchen- main air con was decommissioned & needs to be operational again | Bandyup Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | EQUANS Mechanical Services (WA) Pty Limited | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-10-06 10:40:00 | Fail | COMPLETED
MSA-DCS | WA3581501 | Yeeda C cameral 126 not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-27 16:00:00 | Pass | Camera did not not come back on after generator testing. Checked camera on Maxpro and EBI. Tested ok.
MSA-DCS | WA3581519 | Unit 6, A Wing- Hot tap in laundry is leaking | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-08-31 15:00:00 | Pass | Nill
MSA-DCS | WA3581569 | Unit 14, Cell C11- Light switch not working (have checked bulbs & starters) | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 08:30:00 | Pass | Repaired faulty lights in cell c11 unit 14
MSA-DCS | WA3581579 | Unit 1 Cell A6 has a smashed window. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 13:00:00 | Pass | CELL WINDOW RE GLAZED
MSA-DCS | WA3581605 | Bakery MOFFAT GAS RACK OVEN NOT WORKING. - see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 10:04:08 | 2020-09-09 15:20:00 | Fail | COMPLETED
MSA-DCS | WA3581634 | SITE COST Unit 1, Cell Call network error | Bunbury Regional Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Aug 2020 | 2020-08-27 18:38:23 | 2020-08-27 14:00:00 | Pass | Reset Node Error alarm from new unit. Alarms cleared and cell calls tested both to Unit console and delayed to Gate.
MSA-DCS | WA3581636 | Main prison fence alarm is activating but not showing on monitor & unable to view camera footage | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 10:40:05 | 2020-12-02 11:00:00 | Fail | All zones walked tested and confirmed alarm activation and activation of relevant camera switching. Sometimes officers do not use the process macro correctly and cannot clear the previous alarm and that’s why they cannot see the new alarms.
MSA-DCS | WA3581675 | Unit 7 - A Wing kitchen sink Water is leaking from the sink and surrounding work top into cupboard | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-01 10:00:00 | Pass | Nill
MSA-DCS | WA3581681 | Unit 13 - A14 sink taps are leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-08-31 08:30:00 | Pass | Nill
MSA-DCS | WA3581691 | Unit 1, D3 - Cell Observation hatch stuck open | Casuarina Prison | GMP-BR- HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-08-28 14:00:00 | Pass | REPAIRED & RE SET FRAMEWORK
MSA-DCS | WA3581708 | Unit 2, Lunch room - staff room carpet needs repalcing, as it is becoming a hygiene issue | Casuarina Prison | GMP-BR- HO | Flooring | Carpet (FL) | Midolo Building Services | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-15 13:15:00 | Fail | Carpet tiles replaced
MSA-DCS | WA3581788 | stores yard Wash Down Drain Blocked | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 12:22:55 | 2020-08-27 16:10:00 | Pass | Grease trap is full causing overflow drain in stores to be full booking in vacuume truck to empty grease traps
MSA-DCS | WA3581874 | Unit 3 - Reticulation pipe has broken (Unit 3 / Unit 4) | Casuarina Prison | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | Pumps n Pipes | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-04 12:00:00 | Fail | fixed various breaks in line and valves.
MSA-DCS | WA3581918 | SHU- Monitors have died. Unable to view any cameras. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 27 Aug 2020 | 2020-08-27 17:33:00 | 2020-08-27 14:30:00 | Pass | Operator had minimised indigo monitors 3 and 4.Restored indigo system.Advised officers how to open and close windows 1 through to 4
MSA-DCS | WA3581936 | Bakery freezer - metal plate fixed to freezer floor has popped off | Casuarina Prison | GMP-BR- HO | Refrigeration | Freezers (RE) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-08-31 07:00:00 | Pass | Plate has been resecured
MSA-DCS | WA3581955 | Unit 7, S Wing Storeroom- Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 13:30:00 | Pass | Repaired light
MSA-DCS | WA3581965 | Units 1-7 control rooms- Mould in outlets of air cons | Hakea Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-25 14:00:00 | Fail | Replaced covers and PCB as per quote
MSA-DCS | WA3582013 | unit 2 B4 Top bunk bed frame has broken and sags | Casuarina Prison | GMP-BR- HO | Furniture | Domestic Furniture (FU) | Midolo Building Services | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 11:00:00 | Pass | BED FRAME REPAIRED - WELDED
MSA-DCS | WA3582024 | ISU, A Wing yard- Flood light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 09:00:00 | Pass | Replaced damaged flood light in ISU
MSA-DCS | WA3582025 | Gate house Perimeter, Common area Karakin A wing - zones 8 & 9 perimeter fence not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-27 16:45:00 | Pass | Calibrated fence zones and confirmed operation.Checked karakan A wing common area no faults found
MSA-DCS | WA3582047 | ladies toilets door hydrolic door closer not working | Killara - Victoria Pk (Metro Youth Bail) | GMP-BR- HO | Building | Doors (BU) | Schlager Construction Group | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 14:58:52 | 2020-09-01 11:30:00 | Fail | Attended site and repairs to hydraulic closer on door
MSA-DCS | WA3582060 | demountalble room 5 training room 5 Power board makes buzzing noise.- see notes | Nyandi Training Academy | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 15:07:25 | 2020-08-28 13:30:00 | Pass | Fixed faulty lights and lighting contractor in training room 5
MSA-DFES | WA3581893 | Attend Cockburn ESC on Saturday 29 Aug for monitoring- see notes | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-29 13:15:00 | Pass | Isolate FIP & EWIS for works.Reinstate and check FIP for faults.
MSA-DFES | WA3583215 | ***Retrospective work order*** INTRUDER ALARM, Z22 REED SWITCH APP BAY 1 REAR DOOR | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-27 11:53:00 | Pass | Job completed- INTERNAL & EXTERNAL CHECK CARRIED OUT. STAFF ONSITE. ALL FINE ONSITE TRUCK WAS LEAVING
MSA-DTAG | WA3581540 | Ground level - 15x faulty flickering lights Various locations (see location in details) | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-02 12:00:00 | Fail | Replaced faulty and blown lamps throughout court
MSA-DTAG | WA3581811 | External - Graffiti on south elevation wall opposite McIver train station | Perth Children's Court | GMP-BR-HO | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-08-28 10:00:00 | Pass | Removed graffiti
MSA-DTAG | WA3581885 | Level 6- Several G Floor Lobby Cameras do not appear to be working | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 17:00:00 | Pass | Changed Live view settings for SAT Ground Level Cameras. Checked recordings. OK. Had all missing cameras Live view back.
MSA-DTAG | WA3581945 | ground security office Fault in fire panel - see notes | Perth Children's Court | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 0 | CLOSE | 27 Aug 2020 | 2020-08-27 17:45:53 | 2020-08-27 15:00:00 | Pass | Attended site for FIP FAULT, no fault on arrival. Suspected Zone 1 fault. Quote has been put through to be replaced. SYSTEM NORMAL
MSA-DTAG | WA3582014 | Registry, ground, rear door to court 3 - Card reader faulty | Armadale Courthouse | GMP-BR-HO | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-28 08:30:00 | Pass | 28/8/20 - Dylan ParslowFound door working when onsite.Dismantled lock to find cause.Unable to fault, reassembled lock and tested all ok.
MSA-DTAG | WA3582106 | ground level, Barristers Robing Room, Male Toilet - Urinal running constantly at low flow rate. | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 11:35:00 | Pass | Replaced inlet valve and outlet washer on urianl
MSA-DTWD | WA3581389 | B Block, Zip unit has produced an electrical shock | Munster Campus (ACEPT) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 1 | CLOSE | 27 Aug 2020 | 2020-08-27 17:00:00 | 2020-08-27 11:15:00 | Pass | Arrived on site, signed in, spoke to pfm about issue with zip unit , completed jsa , investigated problem about shock received from tap of unit , tested PowerPoint (passed test all in working order) , I.R tested unit( tested out fine a-e greater than 200m ohm n-e greater than 200m ohm / found out that hot water function in system isn’t working ) tagged out unit awaiting service man to come and repair , shock has been reported to western power and an investigator is being sent out to site. I believe that it was static build up that caused the shock result of Lino floors being in the building and person that was shocked wearing insulated boots , site left safe
MSA-DTWD | WA3581450 | Workshop- grinding extraction fan will not turn off | Naval Base | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 1 | CLOSE | 27 Aug 2020 | 2020-08-28 17:00:00 | 2021-03-19 09:15:00 | Fail | Works complete by contractors.
MSA-DTWD | WA3581591 | H block ground W/S locking mechanism on the fuel cabinet needs fixing or replacing | Mandurah Campus (formerly Peel) | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-01 11:45:00 | Pass | Replaced padlock
MSA-DTWD | WA3581604 | Block 9 - Smell coming from inspection cap | Thornlie Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-01 12:00:00 | Pass | Fix smelly drain
MSA-DTWD | WA3581609 | Block 3C, Door of F & M workshop - does not lock securely due to water damaged | Thornlie Campus | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-10-28 15:30:00 | Fail | 11/9/20 - Waiting on quote for parts
MSA-DTWD | WA3581610 | F block, AT9 - damaged/hole in wall | Carlisle Campus | GMP-BR | Building | Internal Walls (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-01 19:30:00 | Fail | 1/9/20 - Attended site and assessed breakdown. Works will require the preparation of a BRAF -
MSA-DTWD | WA3581618 | S Block, Room S6- water leak from under the fume cupboard | Murdoch Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 23:09:00 | Pass | Fix leaking sink
MSA-DTWD | WA3581630 | Sewer Pump- Pit full of debris, needs to be emptied. | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Sewer Drains & Septic Systems (PD) | Ballantyne Plumbing Gas & Electrical | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-28 12:15:00 | Pass | Pump out pit to remove debri
MSA-DTWD | WA3581660 | E block, ground floor, restaurant deck (balcony) - blind has broken and dropped on to the deck | Joondalup Kendrew Campus | GMP-BR | Building | Curtains & Blinds (BU) | NEYLOR | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-11 10:10:00 | Fail | Job completed
MSA-DTWD | WA3581740 | A block, Ground floor - AC1 not heating showing fan fault | Mandurah Campus (formerly Peel) | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 11:15:00 | Pass | Arrived on site signed in, checked in with Janine. Gathered tools and equipment went to a/C 1. Isolated unit complete fault check no fault located. Put unit into test mode ran unit all ok, reset unit back into auto mode unit started all ok. Possibly power surge on unit start up Monitored operation, reassembled unit cleaned up Work area, completed paperwork and signed out.
MSA-DTWD | WA3581764 | A Block - fire alarms sending out faults | Munster Campus (ACEPT) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 0 | CLOSE | 27 Aug 2020 | 2020-08-27 16:06:25 | 2020-08-27 13:22:00 | Pass | Comms down dew to Telstra outage
MSA-DTWD | WA3581786 | D block, water cooler keeps tripping the power | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 10:45:00 | Pass | Checked for any internal leaks, checked drain, couldn’t find anything. Put a cover over the electrical terminals as requested. Possibly compressor runs hot and trips circuit. Not sure what else is on the same circuit - client is going to monitor may need replacing . Arcus Fountain Cooler A40421427D
MSA-DTWD | WA3581790 | O Block - water cooler tap is leaking. | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | Water2water Pty Ltd | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 11:30:00 | Pass | Replaced faulty zip tap.
MSA-DTWD | WA3581914 | Ceramics, Washing Machine, pump is leaking | Perth Campus B5 | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-02 14:50:00 | Pass | SOrce and replace washing machine
MSA-DTWD | WA3581957 | Tree lopping multiple locations - see description for locations | Balga Campus | GMP-BR | Landscaping & Gardening | Tree Lopping (LG) | Milners Tree Solutions Pty Ltd | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-07 08:15:00 | Fail | 5 staff @ $100 per hour = $875chipper/picker 1.75 hours at $100 per unit = $350Total of actuals $1,275Budget $1,000
MSA-DTWD | WA3582101 | A block, 1st floor, A52 Chiller - Chiller control panel appears to not be powering up (no power) | Midland Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 2 | CLOSE | 27 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 09:55:00 | Pass | Picked up parts and travelled to site. Signed in and accessed chiller.Replaced phase fail relay and tested.Found fuses on chiller pc boards failed.Picked up new fuses and replaced.Ran system and found both stages operating ok.Found after shutdown there were some informational warnings.Cleared faults but they reappeared.This did not seem to lock out operation so i have quoted for airvision to attend.
MSA-DTWD | WA3582167 | 19Ab buildng - All rooms too warm | Perth Campus B6 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 27 Aug 2020 | 2020-09-03 17:00:00 | 2020-08-31 16:26:00 | Pass | Attended site gained access and investigated. Install checks carried out on 27/8/20. Building reported as hot. Site raised job to investigate. On inspections it was discovered BMS had been locked to ventilation mod only preventing cold water plant from starting. System was drawing 26deg ambient air into building. Mode change over was placed back into auto and system monitored. Chiller plant restarted. As was late afternoon plant time clock cycles building off. Returned to site today 31/8/20 to recheck equipment operation and make minnor adjustments to vav zones as required. General area temps are maintaining at 23deg. It is unclear who changed settings on BMS. Will monitor during site PM visits. Work area has been left tidy.
MSA-DCA | WA3582467 | Basement / DSATM Two toilets are out order. | His Majesty's Theatre-Theatre Building-Basement | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-28 15:30:00 | Pass | Toilet 1 remove toilet replace 100mm rubber to copper refitted toilet Toilet 2 replaced invisis outlet washer
MSA-DCA | WA3582803 | Studio & rehersal - Quality air testing | State Theatre Centre (Heath Ledger Theatre)-Main Building-Basement Level 1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Site Environmental & Remediation Services Pty Ltd | 1 | CLOSE | 28 Aug 2020 | 2020-08-31 17:00:00 | 2020-10-15 15:41:00 | Fail | Final mould monitoring & report completed reports sent to David De Villers & Reese Whitely
MSA-DCS | WA3582236 | Unit 6, A Wing- power in the Self Care kitchen trips out. | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 07:56:47 | 2020-08-28 15:00:00 | Pass | Restored power to self care kitchen in unit 6 A wing
MSA-DCS | WA3582291 | INF (10), Toilet in Cell HC8 belonging to H.C. RINGO is broken and will not flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-08-28 09:23:00 | Pass | Nill
MSA-DCS | WA3582302 | Level 1 - Reception & Carpark - 2 cameras not working | East Perth-Main Building-Level 1 | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 08:40:05 | 2020-08-28 11:42:00 | Pass | Add ntp time server to NVR, re sync time, test, all ok. Add camera 4 garage to second monitor as had been lost on panel. Check both monitors, all ok
MSA-DCS | WA3582330 | Electronic lock to unit 8 is not working | Hakea Prison | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Aug 2020 | 2020-08-28 13:00:01 | 2020-09-04 08:45:00 | Fail | All U8 electric strikes tested ok. When the UNLOCK Command is given by the PC the strikes are fed power for 5 seconds. If the door is closed during that period the tongue will bounce out of the strike, keeping the door open.
MSA-DCS | WA3582337 | SOG Base front desk base alarm not allowing staff to process alarms going off | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Sapio Pty Ltd | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-28 11:30:00 | Pass | Both alarms related to DOTL for two sliding gates. Rectified fault to West Gate by attaching fallen magnet to the gate. East Gate having problem with closing due to safety beam malfunctioning on direct sunlight to Tx. Gate contractor needs to be engaged to rectify the fault.
MSA-DCS | WA3582344 | Administration, tearoom - taps are leaking, mat need spindles replaced | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-02 08:30:00 | Pass | Nill
MSA-DCS | WA3582347 | SHU, Ambulance entrance gate, near SHU isn't fully locking only locking on one turn | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-28 10:30:00 | Pass | Remove dirt from hole in bottom locking bolt.
MSA-DCS | WA3582364 | Unit 9, Cell C4- Blocked basin in cell | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 09:29:40 | 2020-08-28 12:26:00 | Pass | Unblcoked basin in the cell
MSA-DCS | WA3582367 | House 5, Kitchen- Range hood GPO is cracked, single 10amp | Boronia Pre-release-AL10 - Prisoner Accommodation House 4 and 5-Ground Floor-House 5 - Kitchen Area | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-08-28 14:30:00 | Pass | Replaced cracked gpo
MSA-DCS | WA3582368 | unit 2,3 &4 - showing cell call unattended | Albany Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-01 15:30:00 | Pass | Reset all nodes from cell call PC. Tested all 3210 for any faults. All alarms cleared. Job complete. Travel to Perth
MSA-DCS | WA3582394 | Unit 6, Cell B5- Headboard to upper bunk requires re-fixing- see further notes below | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-02 12:30:00 | Pass | FRAME WORK RE FITTED & TIMBER BOARD
MSA-DCS | WA3582400 | CCU (11)- Transponder keeps dropping off line | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 09:58:13 | 2020-11-11 15:00:00 | Fail | Cleaned fibre patch leads, replaced fibre Modems on this circuit, tested and confirmed connection from Transponder to Fibre modem at location and replaced MDAS transponder card. Time left between each operation to confirm if fault resolved, with no change. Fibre modem in gate house is connected to a Mona. The above connection and the head-end Equipment were supplied and installed by the “Casuarina Prison Expansion Project” contractor. Fault to be forwarded to them for further attention.
MSA-DCS | WA3582423 | Admin, Main Lobby - hinge has broken entrance door | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 10:16:03 | 2020-09-09 10:30:00 | Fail | Remove door - Refit bottom strap, replace top pivot, refit threshold and door.Install custom door stop.
MSA-DCS | WA3582427 | Reception, Light not working, tombstones have broken | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-01 07:30:00 | Pass | Investigate and repair lights in reception
MSA-DCS | WA3582434 | House 5, cook top has electrical fault | Boronia Pre-release-AL10 - Prisoner Accommodation House 4 and 5 | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-28 14:00:00 | Pass | Fixed faulty cooktop
MSA-DCS | WA3582448 | Unit 1 - Cell call -Cells 5, 9, 10 & 11 do not communicate to unit 1 office or the gate control | Bunbury Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 10:33:22 | 2020-08-29 11:00:00 | Fail | Cell 9 tested ok. 5, 10 and 1 did not activate when tested from the cell or when an intercom was plugged directly into the CI8a#3 input. Power cycled U1 cell call system, no change to faulty inputs. Replace CI8a. All U1 intercoms tested ok back to U1 control. Asked by security to have a look at a buzzing sound coming from the U6 cell call station. This was an issue unrelated to the fault at U1. This is a warranty job that needs to be investigated by HONEYWELL.
MSA-DCS | WA3582610 | Unit 1, D wing cleaning room- water leak from wall | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-02 10:30:00 | Pass | Nill
MSA-DCS | WA3582647 | Officials Visits office - lock keeps jamming | Casuarina Prison | GMP-BR- HO | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-02 09:30:00 | Pass | Replace bolt throw and service lock.
MSA-DCS | WA3582666 | Unit 14- kitchen pro hot water urn is non-operable, see info below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-31 10:25:00 | Pass | Unit reported no hot water. Advised have been to unit numerous times. No fault found on arrival. Ran extensive testing and couldn’t get unit to do anything other than work correctly. Unit is 11 years old. So if issue persists would recommend replacement. If intermittent fault persists then replace unit as over 11 years so could have random compressor issues.
MSA-DCS | WA3582678 | Unit 10, A & B wing day room door- Key getting stuck in lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 12:40:53 | 2020-08-28 14:15:00 | Pass | Attended site. Serviced/repaired lock to restore normal function.
MSA-DCS | WA3582681 | Unit 10, A & B wing day room door- lock to toilet hard to double lock | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 12:42:57 | 2020-09-09 12:30:00 | Fail | 28/08/2020. On site. Lock requires replacement. Will exceed pre-authorised amount and will need approval.04/09/2020. Approval received. Parts ordered.09/09/2020. On site. Supplied and installed new lock and associated hardware.
MSA-DCS | WA3582701 | Unit 6, cell call not working | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 28 Aug 2020 | 2020-08-28 17:01:03 | 2020-08-28 15:40:00 | Pass | Cleared error messages on Officer station. Cell call and PA tested ok.
MSA-DCS | WA3582723 | Unit 1, A & C - There is a hole in the wall above the phone booth | Casuarina Prison | GMP-BR- HO | Building | Internal Walls (BU) | Midolo Building Services | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-08-28 16:45:00 | Pass | HOLE IN THE WALL HAS BEEN FILLED AND COVERED
MSA-DCS | WA3582727 | Unit 3, Control Room- Cell Call System showing network error | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 13:09:58 | 2020-08-28 14:00:00 | Pass | Cleared error messages on Officer station. Cell call and PA tested ok.
MSA-DCS | WA3582730 | Unit 2, C Wing Dayroom- GPO faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-31 12:00:00 | Pass | Replaced gpo
MSA-DCS | WA3582732 | Stores, Purchasing office- Light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-31 13:30:00 | Pass | Repaired lights
MSA-DCS | WA3582749 | Prisoners Clothing Store- Rheem 50ltr HWS leaking water., further info below | Boronia Pre-release-AJ21 - Stores - Urine Analysis and Uniform Store | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-01 10:45:00 | Pass | COMPLETED
MSA-DCS | WA3582761 | Unit 7, Control Room- Cell Call System Down. Unable to receive calls | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 13:33:13 | 2020-08-28 14:30:00 | Pass | Cleared error messages on Officer station. Cell call and PA tested ok.
MSA-DCS | WA3582774 | Unit 1, control pod - Fire Alarm Switch panel has broken glass can’t reset alarm boiler shut down | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 13:47:29 | 2020-08-28 15:04:00 | Pass | Reset ok
MSA-DCS | WA3582782 | Official Visits, non contact room - Intercom malfunctioning and uncoherent | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 28 Aug 2020 | 2020-08-29 13:51:26 | 2020-10-15 16:58:00 | Fail | Attended site and investigated.Found staff using both sides of official visits booth for holding prisoners. Security advised not to proceed with any modifications at this time.Job Complete
MSA-DCS | WA3582790 | Markets garden - Compost Tea Brewer Pipe corroded and leaking | Casuarina Prison | WSM-GR-SITE | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-04 09:30:00 | Pass | Nill
MSA-DFES | WA3582171 | Fluro Light in Dry Cleaning Room blown. | CFRS Rockingham | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 28 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 08:30:00 | Pass | Sign in 730. Locate faulty lights. The light in the dry cleaning room had a faulty ballast and no tube. Replaced faulty ballast and tube with new. In the kitchen there was also a faulty light. Replaced faulty tubes and starters with new. Sign out 830. The station received a call I did not get a rating.
MSA-DFES | WA3582175 | Engine Room- Hydrant cupboard needs repair | CFRS Claremont | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-01 11:15:00 | Pass | Loose hinge screws, fitted dowels into previous holes and installed a larger gauge screw.
MSA-DFES | WA3582332 | Kitchen - Flickering Fluoro Light | Fleet Management Services - O'Connor Workshop | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-01 13:15:00 | Pass | Located faulty flickering light and repaired it appropriately.Notified staff of works.
MSA-DFES | WA3582662 | Engine bay, female change rooms #5 - broken toilet seat | FESA RHQ - Forrestfield | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-01 11:30:00 | Pass | Replacing toilet seats in female change rooms.
MSA-DFES | WA3582854 | Area 30, toilet associated with room 6 - is blocked | CFRS Perth | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 1 | CLOSE | 28 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 17:43:00 | Pass | Unblocking the toilet.
MSA-DFES | WA3587999 | **Retrospective work order** Z22 APP BAY 1 REAR DOOR SINGLE | VFRS Mandurah | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 28 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 11:36:00 | Pass | Despatch Comments:Z22 APP BAY 1 REAR DOOR SINGLEPatrol Resolution:EXTERNAL CHECK CARRIED OUT. ALL APPEARS SECURE. NO OFFENCE DETECTED. STAFF ONSITE.
MSA-DTAG | WA3582191 | Lvl 23- Alarm acknowledgement button fails to activate when duress alarm is activated | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 28 Aug 2020 | 2020-08-28 17:00:00 | 2020-08-28 14:00:00 | Pass | Checked and tested duress on Level 23 with Annette Marie, both meeting rooms alarming to Mirvac Security and video feed received. Cleared by Luke at Mirvac.
MSA-DTAG | WA3582338 | Security office- SAPIO login provided to security not working | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 28 Aug 2020 | 2020-08-28 13:04:27 | 2020-08-28 12:00:00 | Pass | Unlocked locked out Gallagher logins. Indigo logins were all OK. Walked to each Security Work Station and re-logged into the Gallagher / Indigo programs and provided log in details.
MSA-DTAG | WA3582516 | Automated gate from Magistrates Carpark. The gate was hit with a car and has been put back | Central Law Courts | GMP-BR-HO | Building | Steel Fencing & Gates (BU) | MARSHALL BEATTIE AUTOMATION | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-31 12:30:00 | Pass | Paul Cullum (31/08/2020) - Work NoteTravel to site. Inspect gate and found gate operational. Required to inspect after being knocked off track. Test operation, all okay.
MSA-DTAG | WA3582872 | ground level, The AC is freezing both Legal Aid offices in the afternoon | Perth Children's Court | GMP-BR-HO | Air Conditioning | Room Air Conditioners (AC) | Australian HVAC Services Pty. Ltd. | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-10-09 12:00:00 | Fail | Attend site and pick up data loggers. Talked to staff and they said the temperature had been good since the sensor calibration was done. Return to workshop and download loggers. Inspect temps and found to be consistently between 22 and 24. AC system is working as normal.
MSA-DTWD | WA3582168 | Lvl 8, Plant Room- Fan belt broken | Perth Campus B1 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 28 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-11 12:04:00 | Fail | Attended site collected keys. Gained access to level 8 plant room isolated and locked out EAF system. Replaced drive belts. Checked alignment and tensioned as required. Work area left tidy. Spare belts left with EAF system.
MSA-DTWD | WA3582297 | Downstairs controller is offline | Kwinana Automotive Centre | GMP-BR | Security | Security Management System (SE) | BJ SYSTEMS | 0 | CLOSE | 28 Aug 2020 | 2020-08-28 12:37:49 | 2020-08-28 15:15:00 | Fail | Replaced faulty reed switch on roller door downstairs south east workshop. All tested ok
MSA-DTWD | WA3582309 | Block 6F - G48 Tool store glass window frame has fallen out | Thornlie Campus | GMP-BR | Building | Windows (BU) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-07 15:30:00 | Fail | Repaired track for window and re-installed window.
MSA-DTWD | WA3582350 | A block, Western entry door not closing, broken handle | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 1 | CLOSE | 28 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-31 11:20:00 | Pass | Replaced faulty lock
MSA-DTWD | WA3582393 | Main workshop under benches - Air leak in work shop | Kwinana Automotive Centre | GMP-BR | Building | General Building (BU) | Precision Automotive Equipment/Bapcor | 1 | CLOSE | 28 Aug 2020 | 2020-08-31 17:00:00 | 2021-01-27 11:00:00 | Fail | Repairs to airlines/pipes
MSA-DTWD | WA3582496 | A block, Fire hose reel nozzle leaking near room A12 | Rockingham Campus | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 28 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-28 13:00:00 | Pass | A block, Fire hose reel nozzle leaking near room A12Site:1631Location:South Metro TAFE-Rockingham CampusAddress 1:Simpson Avenue ROCKINGHAMAddress 2:WA 6168 Australia-COMPLETEDTech Note: Found nozzle open-leak stopped.
MSA-DTWD | WA3582577 | C Block, Room C210 - Large water leak from ceiling | Joondalup Kendrew Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 1 | CLOSE | 28 Aug 2020 | 2020-08-31 17:00:00 | 2020-12-02 09:36:00 | Fail | Last BRAF declined, invoice costs to date (as per BRAF 2)
MSA-DTWD | WA3582618 | Level 2, room A213 - Faulty proxy reader | Perth Campus B5 | GMP-BR | Security | Access Control (SE) | Schneider Electric Australia Pty Ltd | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-08-31 15:30:00 | Pass | Replaced faulty lock.
MSA-DTWD | WA3582642 | Level 3, B328 - faulty heat table | Perth Campus B6 | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-01 15:30:00 | Pass | Arrived on site, signed in , spoke to pfm about job , located heat table , completed jsa , isolator was faulty, went to wholesaler to get one like for like , replaced old with new , tested table , working properly, completed paperwork, signed out ***job complete***
MSA-DTWD | WA3582699 | Lvl 4, Room N421- Split air con system dripping water | Perth Campus B2 | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-22 06:38:00 | Fail | BRAF upgrade works have been completed. Pipe lagging has been replaced to prevent further condensation build up on celling tiles.
MSA-DTWD | WA3582753 | Near where Building 819 near transportable building - leak in copper under gorund | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 0 | CLOSE | 28 Aug 2020 | 2020-08-28 17:23:15 | 2020-08-28 16:30:00 | Pass | Repaired broken water pipe
MSA-DTWD | WA3582826 | K block, K006 & K600.1 - The sliding doors are hard to open and close | Balga Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-10-05 11:22:00 | Fail | Arrived at site, inspected doors with site. One set of doors was beyond repair and the other looked to need new rollers. Door was super difficult to remove because the frame was loose and the wheels would not retract. Finally got it off to find that the existing wheels where badly damage and could not be removed. Cut holes for a new set of wheels. Picked up materials and returned to site. Fitted new wheels and tried to get onto the track. Would not go, too much play in the frame was not allowing the new wheels to even get over the bottom lip. Removed new wheels and jammed door back in place but it barely slides. I let site know and they requested we submit a quote for both sets of doors to Programmed. Door/frame dimensions are 2170W x 2135H. Same for both sets of doors, please see photos for any more details.BRAF submitted and approved - Works completed.
MSA-DTWD | WA3582852 | O block,room O004 - Buzzing contactor in the switch board | Balga Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 28 Aug 2020 | 2020-09-02 17:00:00 | 2020-09-02 10:45:00 | Pass | Reset contactor . No noise now .job completes
MSA-MRWA | WA3582582 | Hard Stand area / Sea Container - Hornet’s nest on sea/shipping containers | Materials Engineering Branch | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 3 | CLOSE | 28 Aug 2020 | 2020-09-04 17:00:00 | 2020-08-31 12:40:00 | Pass | Treated wasp nest with 15Litres Biflex Aqua
MSA-DCS | WA3582906 | SITE COST Unit 4 -Power is keep on tripping | Wooroloo Prison Farm-Prisoner Accommodation Unit 4a Block 1 | WSM-BR-SITE | Electrical | Materials (EL) | EASTERN HILLS ELECTRICAL SERVICE | 0 | CLOSE | 29 Aug 2020 | 2020-08-29 12:23:52 | 2020-08-29 11:30:00 | Pass | Removed faulty hot water unit from power circuit and reset
MSA-DCS | WA3582918 | Unable to arm in house 3 of unit 3 | West Kimberley Regional Prison | GMP-BR- HO | Electrical | Materials (EL) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Aug 2020 | 2020-08-29 17:58:49 | 2020-09-07 12:56:00 | Fail | Powercycled controller and re-terminated Gbus cabling, no fault found.tested inputs and outputs.able to arm and disarm
MSA-DCS | WA3582921 | Prisoner Visits room -Intercom are not contactable ,faulty | Casuarina Prison-Prisoner Reception, Visitor Centre, Prisoner Accommodation | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Aug 2020 | 2020-08-29 14:24:47 | 2020-08-31 10:32:00 | Fail | Investigated fault, disassembled server and repaired hardware fault. Reassembled, reinstalled, reinitialised and tested intercomms OK. Monitored and confirmed stable operation.Job CompleteParts:Consumables
MSA-DCS | WA3582965 | unit4 cellB5 cell call high pitch squeal | Albany Regional Prison | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 2 | CLOSE | 29 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-31 19:15:00 | Pass | Travelled to site and attended unit 4 and replaced cell call with new cell call from site stock. All replaced and tested working ok. Reset node status and confirmed all alarms cleared. Job complete
MSA-DCS | WA3582988 | Bunbury Regional Prison-Gatehouse - Cell call system not working. | Bunbury Regional Prison-Gatehouse | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 29 Aug 2020 | 2020-08-30 02:24:54 | 2020-09-01 14:00:00 | Fail | Replaced CI-3210 Cell call control console in the Gatehouse Control Room. See work log for details.
MSA-DCS | WA3582992 | Security system - external perimeter zone B2 gate - RS has change state to open error | Albany Regional Prison-Gatehouse | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 29 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-01 09:00:00 | Pass | Replaced zone B2 gate with new heavy duty reed switch. Seme stock used. Replaced and tested, all tested working ok. Job complete
MSA-DFES | WA3582939 | Cockburn Emergency Services Centre-Main Building- Faulty Security access doors | DFES Cockburn Emergency Services Complex-Main Building | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 29 Aug 2020 | 2020-08-31 17:00:00 | 2020-08-29 15:15:00 | Pass | 29/8/20 - Dean SimpsonVarious doors on the ground floor not opening.Rebooted controllers, now working ok.Tested all ground floor doors, all ok.
MSA-DTAG | WA3582991 | all security cameras - supreme court | Supreme Court | GMP-BR-HO | Security | Security Management System (SE) | Sapio Pty Ltd | 0 | CLOSE | 29 Aug 2020 | 2020-08-29 23:34:46 | 2020-08-29 20:35:00 | Pass | Reset Security Windows Password with Sapio Administrator account. New password works; workstation logged in and Indigo running
MSA-DCS | WA3582997 | None of the cameras are activating when fence goes into alarm. | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 30 Aug 2020 | 2020-08-30 09:52:07 | 2020-08-30 08:28:00 | Pass | Found controller offline causing the hli to not function reprogrammed controller and tested all ok
MSA-DCS | WA3583010 | Unit 1 - A3 - Key has snapped in the lock. (Judith hatch) | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 30 Aug 2020 | 2020-08-30 12:39:55 | 2020-08-30 10:30:00 | Pass | After Hours Attendance. Removed broken key from lock. Normal function restored.
MSA-DCS | WA3583075 | Casuarina Prison - Units 15 and 16 - Hot water - gas boilers not working. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Gas (PD) | Boilertronics | 0 | CLOSE | 30 Aug 2020 | 2020-08-30 19:59:49 | 2020-08-30 20:00:00 | Fail | Received call out. Travelled to site and signed in. Attended new unit 15 plant room and found emergency gas valve had no power. Investigated if fire panel alarm was holding out gas, sighted instruction sheet that mentioned emergency gas stop button in tea room. Reset e-stop in tea room, reset gas valve in plant room, reset water heaters. All three heaters fired and began to heat the system. Signed out and travelled back to workshop.
MSA-DCA | WA3583415 | Basement, Fire panel - mutliple faults including Vesda | Art Gallery of WA - James St | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 12:15:00 | Pass | Attended site and found the following.1: Level 1 crate store Vesda in pre alarm, reset ok.2: Reference detector isolated.3: Centenary Ground floor east Vesda isolated.4: Level 4 conservation C/Void devices 4024 smoke detector missing5: Loop 4 open circuit fault6: Fip has 128 isolates on panel.7: Code red and EWIS isolatedAll above issues due to building works and being sorted by others.8: Centenary Level 1 East Az39 conventional fault Vesda had been in fault last week so isolated by gallery staffChecked history back to 12/8 and found no faults listed in event log.De isolated and left normal.
MSA-DCS | WA3583192 | Eyre, B2 - window does not slide | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 31 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-01 12:30:00 | Pass | STUCK WINDOW FREED / LUBRICANT APPLIED
MSA-DCS | WA3583195 | Eyre, B1 - door hinge snapped off | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 31 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-01 11:45:00 | Pass | DOOR HINGE RE SECURED
MSA-DCS | WA3583200 | security office - computer screens not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 07:28:23 | 2020-08-31 11:00:00 | Pass | Travelled to site and reset EBI computer in security office. Reprogrammed new card for key bunch 78. Set up correct descriptions in programming setup of user cards. Job complete
MSA-DCS | WA3583208 | water pressure fluctuating to the whole prison site | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-02 15:00:00 | Pass | COMPLETED
MSA-DCS | WA3583244 | Health Administration - MDAS system faulty, (see notes) | Casuarina Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 31 Aug 2020 | 2020-09-02 17:00:00 | 2020-08-31 15:30:00 | Pass | See log for detailed description.
MSA-DCS | WA3583246 | Unit 13, B11 - shower blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-04 17:00:00 | 2020-08-31 09:30:00 | Pass | Nill
MSA-DCS | WA3583249 | control room - #PTZ 16 not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 08:00:03 | 2020-08-31 09:00:00 | Pass | No image on EBI for camera 173. No image at EC. Found blown fuse for camera 173. Replaced fuseccimage and PTZ functions tested ok at EC and at gatehouse control. Parts used:Consumables
MSA-DCS | WA3583255 | Laundry - Water leaking from water trough | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-09 14:00:00 | Fail | Nill
MSA-DCS | WA3583257 | Unit 2, B wing -There is a leaking pipe in the B Wing Cleaning Cupboard. It is continually dripping | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-01 12:30:00 | Pass | Nill
MSA-DCS | WA3583275 | Unit 7 - when the vent for C/D wing is in operation a bad smell eminates through unit 7 D wing | Casuarina Prison | GMP-BR- HO | Air Conditioning | Materials (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-01 09:45:00 | Pass | Informed maintenance for removal of rats
MSA-DCS | WA3583281 | Lenard- Flood light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-01 12:00:00 | Pass | Repaired flood lights.
MSA-DCS | WA3583282 | Yeeda- Flood light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-01 14:30:00 | Pass | Repaired flood light
MSA-DCS | WA3583283 | Unit 6, C7 - Personal lock C7 needs changing (see notes) | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-08 15:30:00 | Fail | Require parts.Replace door plate, barrel and lock.Weld on strike plate
MSA-DCS | WA3583284 | External, Zone 3, Zone 4, Zone 13/14- perimeter lights not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-01 10:00:00 | Pass | Repaired perimeter lights
MSA-DCS | WA3583289 | Dairy Hut, GPOs not working | Karnet Prison Farm | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-07 10:00:00 | Pass | Investigate and repair unit 1 dairy huts power
MSA-DCS | WA3583293 | Unit 6, C wing - the shower drain is not allowing water to drain away and water is coming back up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-08-31 14:00:00 | Pass | Nill
MSA-DCS | WA3583296 | Unit 3, D Wing - auto boil faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-03 12:10:00 | Pass | Started this job at 10am as didn’t know which one to start first. Actual job start time was 10.45am 3/9/2020 completion time correct. Replaced solenoid. Water flushed through unit a couple of times due to discoloured water. All clear now. A40189236M
MSA-DCS | WA3583299 | Unit 2, Top landing - Auto boil faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-03 10:45:00 | Pass | Replaced broken tap.
MSA-DCS | WA3583302 | Farm Office - Air Con not working | Karnet Prison Farm | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-02 09:00:00 | Pass | Reset unit and performed operational checks. All ok.
MSA-DCS | WA3583303 | Unit 13, Drain for the sink in common room has a leak, flooding the bench space underneath | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-08-31 10:30:00 | Pass | Nill
MSA-DCS | WA3583313 | Unit 7, D Wing, Cell D3- Bunk has broken slat around the middle of the bed | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-04 12:00:00 | Pass | BED SLATS WELDED BACK IN PLACE
MSA-DCS | WA3583314 | Unit 5, Cell C2- Window will not stay up, Spirals may need replacing | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-02 15:00:00 | Pass | RE NEW SPIRAL BALANCES AND REPAIR SASH
MSA-DCS | WA3583323 | Gatehouse- Area of tiles in keywatch area are broken | Casuarina Prison | GMP-BR- HO | Flooring | Tiling (FL) | Midolo Building Services | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-10-02 14:30:00 | Fail | REPLACE NUTS ON KEY WATCHER STAND
MSA-DCS | WA3583329 | Unit 13, A11 - shower leaking and no water pressure | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-08-31 11:30:00 | Pass | Nill
MSA-DCS | WA3583331 | Unit 12, Cell HA09- Overhead bed light is flashing when turned on | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-03 10:00:00 | Pass | Repaired faulty lights in unit 12 ha9
MSA-DCS | WA3583337 | Unit 5, D Wing drain is draining very slowly | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-08-31 12:30:00 | Pass | Nill
MSA-DCS | WA3583417 | Kitchen, rational ovens - all three rational ovens inner and outer door seals failing | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-18 11:30:00 | Fail | Replaced Door & trolley seals on all Rational ovens.
MSA-DCS | WA3583456 | unit 2 outside between top & bottom landing leaking 40mm copper pipe | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-02 12:00:00 | Pass | COMPLETED
MSA-DCS | WA3583570 | Unit 4A, Dart room- Zip auto boil 2000B not working | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 10:24:25 | 2020-09-14 11:33:00 | Fail | New unit installed and commissionednew capex asset ZIP SERIAL NUMBER FOR WARRANTY IS2020072306002 Programmed Number A40189276Q
MSA-DCS | WA3583573 | Unit 2C, Day Room- Zip water unit keeps coming up with error | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | Water2water Pty Ltd | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 10:26:33 | 2020-09-04 15:35:00 | Fail | Restarted work 1.28pm 4/09/20Replaced Faulty Tap Kit, faulty Element, Controller PCB and solenoid. Rheem Parts -All now working ok. Also has this unit and two kettles on same outlet. When all three on trips power.
MSA-DCS | WA3583583 | Unit 3 - A2 Viewing hatch A02 needs repairing, the Aluminium track is missing across the bottom. | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-02 11:00:00 | Pass | VIEWING HATCH FRAMEWORK REPAIRED
MSA-DCS | WA3583586 | Unit 3, B & D Wing Door handle is damaged (sharp jagged areas) | Casuarina Prison | GMP-BR- HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-10-02 11:30:00 | Fail | NEW DOOR HANDLE FITTED TO DAYROOM DOOR
MSA-DCS | WA3583588 | Unit 6, D13 - toilet does not flush | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-08-31 16:00:00 | Pass | Nill
MSA-DCS | WA3583590 | Kitchen sink flick mixer tap leaking water | Boronia Pre-release-AP23 - Prisoner Accommodation House 10 and 11-Ground Floor-House 10 - Kitchen Area | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-08-31 14:00:00 | Pass | Job completed
MSA-DCS | WA3583592 | Unit 13, Oven broken (light sockets) | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-10 11:30:00 | Fail | Replaced globes and globe seal on both ovens.
MSA-DCS | WA3583599 | Unit 2, Cell 73- shower 1/4 turn taps faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-02 14:00:00 | Pass | COMPLETED
MSA-DCS | WA3583601 | Unit 4, J landing - large water filter housing cracked and leaking | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-07 12:00:00 | Fail | COMPLETED
MSA-DCS | WA3583652 | Unit 3, D wing - ablutions window will not stay open unless chocked open | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-02 13:00:00 | Pass | RE NEW SPIRAL BALANCES AND SASH REPAIRS
MSA-DCS | WA3583681 | Unit 1, D Wing, Cleaning Room- Tap in the middle is leaking & on the right hand side there is a hole | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-02 09:30:00 | Pass | Nill
MSA-DCS | WA3583734 | Unit 2, Cell A10- Light is broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 11:00:00 | Pass | Repaired light
MSA-DCS | WA3583737 | Unit 4 B15 basin tap broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 08:00:00 | Pass | Rewasherd and reseated pillar tap
MSA-DCS | WA3583738 | PCS, office- Door and lock faulty- see info below | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-01 15:15:00 | Pass | On site. Supply and fit new hinges and realign door to restore normal function.
MSA-DCS | WA3583744 | Unit 4, B Wing Showers- Sink is leaking from back of wall when tap is turned on. | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 08:58:00 | Pass | Pulled apart wall hung basin replacing split flexi on hot side only
MSA-DCS | WA3583765 | kitchen main hot box getting zapping from box | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 12:12:03 | 2020-08-31 13:20:00 | Pass | Performed earth testing on hot box and power cable, hot box has tested ok no shorts or earth leakages on unit. Power cable has internal rust and moisture in plug top, tested and found it to be faulty and new extension cord is needed.
MSA-DCS | WA3583814 | Unit 13, Cell D11- Shower floor drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-01 13:30:00 | Pass | Nill
MSA-DCS | WA3583820 | Unit 2, B Wing Dayroom- Tap broken, will not switch off | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 13:14:50 | 2020-08-31 14:07:00 | Pass | Turned off water removed and replaced quator turn tap
MSA-DCS | WA3583827 | Amenitites, the heating in the building seems to be off again | Casuarina Prison | GMP-BR- HO | Air Conditioning | Room Air Conditioners (AC) | Australian Airconditioning Services Pty Ltd | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-21 11:30:00 | Fail | New manual reset HP/LP fitted. Data logger showed no fault. Unit operational
MSA-DCS | WA3583867 | gate house light over front desk faulty | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-07 08:30:00 | Pass | Investigate and replace gate house light over front desk
MSA-DCS | WA3583870 | Unit 13, Cell D2- shower drain is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-01 14:30:00 | Pass | Nill
MSA-DCS | WA3583880 | Industries- security flood light not turning off during the day | Karnet Prison Farm | GMP-BR- HO | Electrical | Lighting, External (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-07 12:00:00 | Pass | Investigate and repair industries flood light
MSA-DCS | WA3583887 | unit 14, B12 - personal door lock not working from the inside | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-02 11:00:00 | Pass | Replace mortise lock and adjust strike.
MSA-DCS | WA3583889 | unit 13 D3 Shower Drain Blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-01 15:30:00 | Pass | Nill
MSA-DCS | WA3584050 | Zone 3 Camera 2, Zone 13 Camera 2, Zone 14 Camera 2, Zone 15 Cameras 1 and 2, Gatehouse side door ou | Wooroloo Prison Farm-Gatehouse | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 31 Aug 2020 | 2020-08-31 23:32:04 | 2020-08-31 21:45:00 | Pass | Attended site checked and found Z3C2,Z13C2,Z14C2 and Z15C1&C2 no vision in control room. Checked cameras are ok in equipment room workstation. Located problem on Control workstation. Restart Indigovision on Control workstation and tested all ok.
MSA-DFES | WA3583390 | Ground level - Multiple plumbing faults (see notes) | VFRS Bassendean | GMP-BR | Plumbing & Drainage | Materials (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-04 11:15:00 | Fail | Attended site and carried out work fixed all faults
MSA-DFES | WA3583617 | engine room rear door not functioning | CFRS Maddington | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-15 15:30:00 | Fail | Technician attended the site of Maddington Fire Station to the Engne Room Roller Door W21776 on 31/08/2020. Following full test and inspection of door components identified fault was overhead sectional door in up position and not auto-closing. Upon further inspection found that door mechanically sound but unable to operate door via controls, suspect fault with expansion board/contactors. Technician has called for electrician to attend to verify fault.Technician returned on site on 15/09/2020 to carry out quoted work to rear engine room door. He had some issues transferring controllers as parts were not match and a lot of the cable connections were different. Had also an issue with the drive chain and had to get another tech to come to help reinstall. Door is now in good working condition. Full test and inspection of door components completed prior to leaving site.This quote includes: "Removal of the existing components."Supply and installation of 1 x new replacement mcb control
MSA-DFES | WA3583644 | FF engine room washing machine drain hose inlet on rear sink S bend has snapped off | CFRS Rockingham | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-01 15:30:00 | Pass | Replacing broken trap under trough at the back of station. Connected washing machine hose to it. Tested all works good, no leaks
MSA-DFES | WA3583711 | Fire Fighters 1st Bathroom- Leaking tap | CFRS Rockingham | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-02 11:00:00 | Pass | Replacing the tap set on the basin in FF bathroom. Removed old tap set and pipes. Installed isolation valves and new set. Tested for leaks, all works good.
MSA-DFES | WA3583714 | Fire Fighters Car Park, outside area 11- Below ground, leaking tap | CFRS Rockingham | GMP-BR | Plumbing & Drainage | Water (PD) | ZAMBEZI PLUMBING & GAS PTY LTD | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-02 13:30:00 | Pass | Removing old valve box for underground tap. Altered the pipe, raised up for the new tap. Installed new tap, acumen breaker and hose end connectors.
MSA-DFES | WA3583724 | Yard, Pillar hydrant is leaking | CFRS Welshpool | GMP-BR | Fire Protection Services | Fixed Fire Equipment (Hydrant & Fire Mains, Hose Reel) (FP) | Critical Fire Protection & Training | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-09-16 15:00:00 | Fail | Attend site and repair leak to hydrant
MSA-DFES | WA3583729 | Zone – 55/68 (Front engine room door)- Trim from engine room door has come off | CFRS Perth | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 11:15:00 | Pass | Technician attended the site of Perth Fire Station on 03/09/2020. Following a full test and inspection of door components identified fault was an issue of a trim requiring repair is located on a fire truck and not an issue with one of the engine room doors. Technician was unable to rectify problem, wrong contractor sent to site. Full test and inspection of door function completed prior to leaving site.
MSA-DFES | WA3583802 | ground Zone – 55/68 (Front engine room door) trim has come off - see note | CFRS Perth | GMP-BR | Building | Doors (BU) | AWB Co. | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-02 07:45:00 | Pass | Liam Hanlon (02/09/2020) - Work NoteAttend site sign in Locate piece and door Main door to engine room Re attach flashing beneath brush seal Sign out
MSA-DFES | WA3583816 | Multiple locations - Multiple doors locking during fire excavation | DFES Cockburn Emergency Services Complex | GMP-BR | Security | Security Management System (SE) | SONTEC WA PTY LTD | 0 | CLOSE | 31 Aug 2020 | 2020-08-31 17:10:58 | 2020-09-05 15:45:00 | Fail | 31/08/20 - Dylan Parslow - investigated issues with doors not releasing on fire. found power supply faulty in main panel, requires replacement. recommend full function fire test to prove correct operations.1/09/20 - Dylan Parslow - Replaced faulty power supply & battery. tested door operations after power was reinstated, full function fire test still required.5/09/20 - Dylan Parslow - Completed full function fire test, all doors releasing correctly.
MSA-DFES | WA3583855 | Comcenter change room - bench bolted to the ground has come loose and is unstable to sit on. | DFES Cockburn Emergency Services Complex | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-02 10:00:00 | Fail | Re-bolted bench to the ground. Is now stable to sit on. Job complete
MSA-DTAG | WA3583393 | L10 coroners ct kitchen Cupboard under the kitchen sink is full of water-see notes | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 14:00:00 | Pass | Complete
MSA-DTAG | WA3583432 | ground floor & level 1 - cameras not working | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 0 | CLOSE | 31 Aug 2020 | 2020-08-31 13:24:01 | 2020-08-31 15:00:00 | Fail | Reset fibre switch and re-established video streams to all required work stations.Job completed.
MSA-DTAG | WA3583903 | Lvl 1, Storage Room - Sensor fault on the fire panel | Central Law Courts-Main Building-Level 1 | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-01 11:30:00 | Pass | Rectifies faults
MSA-DTWD | WA3583178 | Level 2 - lights out at front of room A236 | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 31 Aug 2020 | 2020-09-04 17:00:00 | 2020-09-02 12:45:00 | Pass | Replaced faulty lamps and ballasts.job completed
MSA-DTWD | WA3583505 | T,U & V block - Aircons not turning off when programmed to | Rockingham Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Icon Logic Pty Ltd | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 16:30:00 | Pass | System was fully checked, and all AC Unit within the Daikin system were found to be online.
MSA-DTWD | WA3583549 | Glass house- pipe has water leak | Muresk Institute | GMP-BR | Plumbing & Drainage | Water (PD) | Lane's Plumbing | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 14:30:00 | Pass | Repaired leaking water pipe at Glass House
MSA-DTWD | WA3583633 | E block E43 – Faulty light fitting in Tech’s Office | Bentley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 08:00:00 | Pass | Arrived on site, signed in, located light, completed jsa, set up work area, replaced tubes , light now working, cleaned up work area , completed paperwork, signed out *** job complete***
MSA-DTWD | WA3583659 | Fire pump building & Main Richmond st entrance - Graffiti to be removed | Leederville Campus | GMP-BR | Cleaning | Graffiti (CL) | GRAFFITI FORCE PTY LTD | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 12:00:00 | Pass | REMOVAL OF GRAFFITI FROM FIRE PUMP ROOM AND ENTRANCE
MSA-DTWD | WA3583693 | Lvl 2, 12Ab Room A252 broken glass pane (About 60mm square) | Perth Campus B5 | GMP-BR | Glazing | Window Glass (GL) | ACTION GLASS & ALUMINIUM | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-10-06 11:50:00 | Fail | ATTENDED SITE TO ASSESS WORKS REQUIREDRETURNED LATER DATESUPPLIED & FIT 2 NEW STAYS TO AWNING WINDOW PLUS NEW LOCK & BOLT KEYED ALIKE2 MEN & HARNESS REQUIRED
MSA-DTWD | WA3583718 | Lift 1 Button 3 not working both sides | Perth Campus B1 | GMP-BR | Lifts | Lifts (LI) | Schindler Lifts Australia | 3 | COMP | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-08-31 14:50:00 | Pass | Button three worn out Swapped with level 6 as it’s no a common floor and have ordered parts to replaceTo be closed out at $0
MSA-DTWD | WA3583746 | P block P024 Repair/replace faulty lock/key | Balga Campus | GMP-BR | Security | Locksmith (SE) | LIGHTHOUSE LOCKSMITHS | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-08-31 14:45:00 | Pass | Keys replaced
MSA-DTWD | WA3583748 | Block 8, EBT- infestation of flies- see further info below | Thornlie Campus | GMP-BR | Pest Control | General Pest (PC) | Complete Pest Management Services | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 14:45:00 | Pass | Carried out a service for flies at Thornlie Tafe. Installed pheromone pads throughout the office area where flies were located. Residually Sprayed the external perimeter creating a barrier. If problems persists after a couple of days it's recommended we treat internally after everyone has left the office.
MSA-DTWD | WA3583786 | A block, A013 - check Zip boiler water is leaking | Balga Campus | GMP-BR | Plumbing & Drainage | Materials (PD) | ECO PLUMBING AND GAS PTY LTD | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 12:15:00 | Pass | Removed leaking wall urn.
MSA-DTWD | WA3583856 | Block 8, Room 8G31- Power switch on wall arcing | Thornlie Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2020-08-31 16:00:00 | Pass | Arrived on site, signed in, spoke to pfm about job , located switch’s in block 8 g31 , completed jsa, isolated lighting, replaced old switches for new, tested and all working , cleaned up work area , completed paperwork ,signed out *** job completed ***
MSA-DTWD | WA3583881 | N block N108 vinyl bubbling | Mount Lawley Campus | GMP-BR | Flooring | Vinyl (FL) | AWB Co. | 3 | CLOSE | 31 Aug 2020 | 2020-09-07 17:00:00 | 2021-07-06 15:00:00 | Fail | work completed as per signature slip and picture
MSA-DTWD | WA3583947 | Broken light switch in staff/disabled toilet | Armadale Campus? 45 Commerce Ave | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-08-31 16:00:00 | Pass | Replaced faulty light switch
MSA-DTWD | WA3583961 | D block kitchen D19 loader on the tronic oven damaged | Bentley Campus | GMP-BR | Electrical | General Electrical (EL) | BAKE-QUIP PTY LTD | 1 | CLOSE | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-08-31 16:15:00 | Pass | completed 31/8
MSA-MRWA | WA3583664 | ground admin Male toilet blocked – cleaners noted in book on 28/8. is blocked - see note | Materials Engineering Branch | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-01 15:30:00 | Pass | Unblocked toilet (ground male lhs) and sewer line
MSA-MRWA | WA3583797 | Level 1, ladies toilet - Sanitary Bin full, please remediate | Don Aitken Centre MRWA Head Office-Main Building-First Floor | GMP-BR | Cleaning | Sanitary Services (CL) | Rentokil Initial PTY LTD | 1 | COMP | 31 Aug 2020 | 2020-09-01 17:00:00 | 2020-09-01 08:00:00 | Pass | To be closed out as per Brendan
MSA-MRWA | WA3583964 | basement & L1 male toilets not flushing | Don Aitken Centre MRWA Head Office | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-01 14:20:00 | Pass | Fixed faulty cisterns.
MSA-MRWA | WA3583994 | L2 225 Replace / refurbish faulty LED | Don Aitken Centre MRWA Head Office-Main Building-Ninth Floor-Main Plant Room | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 31 Aug 2020 | 2020-09-03 17:00:00 | 2020-09-03 12:00:00 | Pass | Attended and found room 225. Tested lights found one faulty light. Replaced LED driver and tested. All now working. Informed staff of job completion
MSA-DCA | WA3586261 | East end of A shed Smoke detector has gone into alarm. Please inspect and reset. See notes** | DO NOT USE TO BE DECOMMISSIONED A Shed, Victoria Quay, Fremantle-A Shed-Ground Floor | GMP-BR | Fire Protection Services | Smoke and Heat Detection (FP) | Critical Fire Protection & Training | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 17:00:00 | 2020-09-01 13:50:00 | Pass | Attended site - investigated alarm - was told a light sent smoke out - set detector into alarm - brigade arrived.Replaced 1x smoke detector - FIP's 2x back to normal.
MSA-DCS | WA3584051 | Banksia Hill Detention Centre - Perimeter Cameras 15 and 16 gone down due. | Banksia Hill Detention Centre | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 00:20:21 | 2020-09-04 08:15:00 | Fail | Attended site continue with the work, checked cameras 15&16 are working ok. Removed the faulty 703T&703R as office instruction. Job completed.
MSA-DCS | WA3585905 | Kitchen, work shop - hot box tripping out power - hot box fault | Wandoo Rehabilitation Facility | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 07:22:22 | 2020-09-09 13:30:00 | Fail | Returned 9/09 and replaced 4 elements and tested ok.
MSA-DCS | WA3585970 | Jeelia, A6 - Bedside light wil not turn off | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 08:21:31 | 2020-09-01 12:00:00 | Pass | Replaced faulty switch
MSA-DCS | WA3585976 | Recreation, Gym - power point will not switch off by bed | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 08:26:55 | 2020-09-01 13:00:00 | Pass | Replaced damaged gpo
MSA-DCS | WA3585988 | GATEHOUSE-CONTROL ROOM- Network 1 comms failure. | Casuarina Prison-Gatehouse | GMP-BR- HO | Building | Materials (BU) | Seme Solutions Pty Ltd | 0 | CLOSE | 01 Sep 2020 | 2020-09-01 12:28:09 | 2020-10-22 16:41:00 | Fail | Repaired multiple perimeter faults after lightning storm.Completed Repairs and tested OkJob Complete
MSA-DCS | WA3585996 | PE Zone 14 Zone in constant alarm and will not reset | Roebourne Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-03 09:00:00 | Pass | Job complete
MSA-DCS | WA3586005 | Unit 1, control pod - Fire Alarm not reset causing boilers to shut down | Melaleuca Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 08:43:35 | 2020-09-08 14:12:00 | Fail | Attended site and found alarm due to Vesda alarm in D wing cell 2. Reset alarm and boilers restarted ok.Boiler shutdown should only activate via plant room zone and pod zone only, programming update required.8/9 KS GAReturned to site to carry out software changes and found that gas is shut down via A/C shut down that needs to shot off on all alarms.So unable to carry out changes as we thought we could.To be able to do this we will need to run a new fire rated cable from FIP to MSSB in both units and will need the MSSB wiring modified to givea seperate A/C and Gas shutdown signals.Aprox 30m cable and 1 day for two men per unit to install.Have referred matter to client - will require fire engineer to approved before changes can be made.
MSA-DCS | WA3586013 | Unit 1, Ablutions sink taps faulty | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-08 14:30:00 | Pass | COMPLETED
MSA-DCS | WA3586017 | Unit 1, Shower taps missing handles | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-02 09:00:00 | Pass | COMPLETED
MSA-DCS | WA3586050 | Unit 3, Cell A12 - Roof leak | Karnet Prison Farm | GMP-BR- HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-04 11:15:00 | Pass | leak to corner of cell room. lift flashing and sheeting, repair sarking, seal penetration and replace
MSA-DCS | WA3586101 | Unit 2, B & D - Brass or Copper connection in cleaning room split/leaking. Pipe feeds showers. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-09 09:00:00 | Fail | Nill
MSA-DCS | WA3586176 | Hotham A6 obs light does not work | Wandoo Rehabilitation Facility | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 09:55:52 | 2020-09-01 14:00:00 | Pass | Replaced faulty lamp
MSA-DCS | WA3586248 | Unit 10, C& D Dayroom - Water fountain has a leaking tap | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-03 10:00:00 | Pass | Replaced leaking drinking fountain tap
MSA-DCS | WA3586253 | Unit 10, C Wing- Door lock between 15 &16 is blocked | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-01 14:30:00 | Pass | On site. Serviced duct and restored normal operation.
MSA-DCS | WA3586285 | Unit 10, Cell D2- Vinyl around toilet & sink is lifting | Hakea Prison | GMP-BR- HO | Flooring | Vinyl (FL) | Midolo Building Services | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-10-06 13:30:00 | Fail | DAMGED VINYL REMOVED - REPLACED WITH NEW
MSA-DCS | WA3586301 | Unit 5, House 5- bathroom 2 exhaust fan faulty (EDM200) | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | EASTERN HILLS ELECTRICAL SERVICE | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-04 13:00:00 | Pass | Replaced wall exhaust fan
MSA-DCS | WA3586333 | Unit 1, Cell A2- Broken Shower Floor Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-11 11:00:00 | Fail | Carried out repairs to the damaged floor tiles in shower recess and cell floor.
MSA-DCS | WA3586336 | Unit 1, Cell A4- Broken Shower Floor Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-11 15:00:00 | Fail | Carried out repairs to the damaged floor tiles in shower recess and cell floor.
MSA-DCS | WA3586345 | Unit 1, Cell A7- Broken Shower Wall Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-14 10:30:00 | Fail | Carried out repairs to the damaged floor tiles in shower recess and cell floor.
MSA-DCS | WA3586346 | Unit 1, Cell A8- Broken Shower Floor Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-14 14:00:00 | Fail | Carried out repairs to the damaged floor tiles in shower recess and cell floor.
MSA-DCS | WA3586351 | Unit 1, Cell A9- Broken Shower Floor Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-10 15:00:00 | Fail | Carried out repairs to the damaged floor tiles in shower recess and cell floor.
MSA-DCS | WA3586352 | unit 2 C12 door lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 11:37:53 | 2020-09-02 12:15:00 | Fail | 01/09/2020 - Attended site. Inspect issue and attempt repair. New lock needed.02/09/2020 - On site. Supply and fit new lock.
MSA-DCS | WA3586353 | Unit 1, Cell A10- Broken Shower Floor Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-10 14:00:00 | Fail | Carried out repairs to the damaged floor tiles in shower recess and cell floor.
MSA-DCS | WA3586357 | Unit 1, Cell A12- Broken Shower Floor Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-10 13:00:00 | Fail | Carried out repairs to the damaged floor tiles in shower recess and cell floor.
MSA-DCS | WA3586360 | Unit 1, Cell A13- Broken Shower Floor Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-10 12:00:00 | Fail | Carried out repairs to the damaged tiles in the shower recess and cell floor.
MSA-DCS | WA3586365 | Unit 1, Cell A16- Broken Shower Floor Tiles | Melaleuca Prison | GMP-BR- HO | Flooring | Tiling (FL) | Schlager Construction Group | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-10-19 10:30:00 | Fail | Carried out repairs to the damaged floor tiles in shower recess and cell floor.
MSA-DCS | WA3586367 | Turner, Cell A02- Basin wont shut off | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-02 13:30:00 | Pass | Replaced solenoid valve and adjusted pipework to suit
MSA-DCS | WA3586371 | Turner, A Wing- toilets have very low pressure | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-11 10:35:00 | Fail | Replaced faulty pressure reducing vakve and chechk valve
MSA-DCS | WA3586377 | Boot shop - Workshop Damaged and exposed wiring.-see notes | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-02 09:00:00 | Pass | Repaired damaged conduits in boot shop
MSA-DCS | WA3586385 | Cleaning - Workshop Leaking pipe. A sprinkler pipe is badly rusted and leaking in cleaning. | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-17 08:17:00 | Fail | 08.09.20attended site and investigated leaking pipeworkwill require 2x men to cut and plug off 32mm pipeworktechs will require 1x 32mm plugreciprocating saw to cut pipewill require isolate, drain down and disconnect pipework & plug. Then fill system and reset2x techs 4-6 hours17.09.20carried out repairs as directed by site
MSA-DCS | WA3586395 | Unit 3 D Wing Dayroom Basin Tap Broken | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 11:58:28 | 2020-09-01 16:10:00 | Pass | Replaced x2 hot broken and cold spindle leaking
MSA-DCS | WA3586400 | Unit 4, Cell B9- Top bed bunk slats 2 or 3 have been broken | Casuarina Prison | GMP-BR- HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-03 14:00:00 | Pass | BED SLATS HAVE BEEN REPAIRED - WELDED
MSA-DCS | WA3586404 | Unit 3, Cell D16- Main light switch broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-03 10:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3586410 | Locate buried valve/ investigate low water pressure to industries | Wooroloo Prison Farm | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-08 16:30:00 | Pass | Investigate low water pressure to industries.Scanned for the water services round the industries.Located a 100mm A/C water services coming into the industries complex.Seems ther is a major blockage in the main water supply pipe to industries. Tested the water pressure at unit 1, pressure no enough to supply the industries.
MSA-DCS | WA3586681 | Medium section temp sallyport razor wire damaged | Bunbury Regional Prison | SPA-BR | Security | Access Control (SE) | AFD Contracting | 0 | CLOSE | 01 Sep 2020 | 2020-09-01 22:30:57 | 2020-09-02 21:30:00 | Fail | 01/09/20Started at 14:30 when PFM phone call received.Source tools, materials, boom lift, load vehicles, cancel 2 x flights, book accommodation, mob to Bunbury.
MSA-DCS | WA3586705 | Corrupt ACM file, regarding cell call in unit 6 | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-02 09:35:00 | Pass | cell call server cellguard system keeps crashing, unable to load current ACM file as software will abruptly shut down.Tested multiple ACM files and found corrupted files, removed files and modifed previous ACM file with recent changes to Unit 1.Reloaded and left of test over night.Officers advised cell call system has been working with no alarms.Restarted all nodes and tested cell calls in various locations.All working with correct descriptions
MSA-DCS | WA3586723 | Ladies toilet sink tap is leaking | East Perth-Main Building-Level 2 | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-04 13:45:00 | Pass | Complete
MSA-DCS | WA3586738 | unit 2 gap in the man barrier on the roof | Bunbury Regional Prison | GMP-BR- HO | Security | Access Control (SE) | AFD Contracting | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 15:24:55 | 2020-09-02 21:30:00 | Fail | 02/09/20Repair razor wire cages
MSA-DCS | WA3586776 | gate house front door - not closing properly | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 16:09:24 | 2020-09-02 13:30:00 | Pass | Technician attended the site of Wandoo Rehabilitation Facility, Main entry internal door on 02/09/2020. Following a full test and inspection of door components found fault to be door does not close fully at times. Technician was able to adjust tension to door closer and changed closing speed. Door now seems to be working ok. Full test and inspection of door function completed prior to leaving site.
MSA-DCS | WA3586779 | gate house front door not locking when going through with fob | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 16:12:51 | 2020-09-02 13:45:00 | Pass | Technician attended the site of Wandoo Rehabilitation Facility, Main entry door on 02/09/2020. Following a full test and inspection of door components identified this is not a door issue. This job needs to be looked at by the client's access contractor and technician has informed client about this. Full test and inspection of door function completed prior to leaving site.
MSA-DCS | WA3586782 | front gate back outer visits door, not closing after walking through | Wandoo Rehabilitation Facility | GMP-BR- HO | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 16:15:12 | 2020-09-02 17:15:00 | Fail | Technician attended the site of Wandoo Rehabilitation Facility to the Gate House on 02/09/2020. Following a full test and inspection of door components found fault to be both doors leading to visitors exit after security were not closing properly. Tech first adjusted tension and speeds to internal door and now working as should. The external door seems to have an issue with the door closer, he was turning the tension screw and wasn't gaining any tension to door. Recommend replacing the door closer to fix this issue. Doors are very heavy so suitable door closer is required as tech believe the existing to be standard which may have caused the fault. Quote has been declined.
MSA-DFES | WA3586025 | Roller door - door has sheared off drive roller at the top of door | DFES - SWORD - State Wide Operational Response Div | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 0 | CLOSE | 01 Sep 2020 | 2020-09-01 12:51:35 | 2020-11-03 14:30:00 | Fail | Technician attended the site of Kewdale Fire and Emergency Services to the Warehouse Roller Door No. W28538 on 01/09/2020. Following a full test and inspection of door components found fault to be door had been opened via motor whilst shoot bolts engaged, this has totally destroyed the drive end hub, unable to carry out any repairs, recommended replacing door. Quote was submitted. Note: raised door and secured in open position as requested by client.Technician/s re-attended site of Kewdale Fire and Emergency Services on 03/11/2020 and completed quoted works. Full test and inspection of door function completed prior to leaving site. This quote includes:"Removal of existing damaged curtain from the drum assembly."Supply and installation of a new curtain to suit the existing opening sizes and being in a powder coated finish to match the existing as close as possible as the existing powder coat colour will have been faded by weather conditions."Supply and installation of 1
MSA-DFES | WA3586029 | Passage way between admin and main workshop faulty light circuit | Fleet Management Services - O'Connor Workshop-Main Building | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 17:00:00 | 2020-09-15 12:45:00 | Fail | Arrived onsite at 1145 investigated 2 seperate faults in the Office area and Hallway. The office area has a faulty sensor and requires a replacement. It also has 2 faulty and damaged fluro battens that need replacement. I also found rhe location of the switch that controls the hallway and turned it on. 1 hallway light was faulty and I repaired accordingly. 1 light has an unknown source of control. I shave spoken to Josh and we repaired the light and will see if it has a unknown automatic switching mechanism. Will need to seek approval to complete works. Installed 2 new lights and 1 sensor to get all works completed. Notified staff and are happy.
MSA-DFES | WA3586166 | L1 DOSS Office in State Operations TV channels not working in office booster is required | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-19 15:15:00 | Fail | CompleteInstalled arial booster in lvl 1 coms rack
MSA-DFES | WA3586318 | ground Applied Training & Cadre Office roof leaks - see notes | FESA RHQ - Forrestfield | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-18 14:30:00 | Fail | 2/9/20 - Have attended site and carried out repairs to A/C roof penetration suspected of causing the leak. Have contacted site today 7/9/20 it appears that the leak may have been resolved, however the ceiling is still a bit damp. Will call back later in the week to check 15/9/20 - Spoke to site. ceiling is dry with no further indication of leaking. Will need to attend to replace 1 x vinyl wrapped ceiling tile to close out works
MSA-DFES | WA3586425 | Relieving Firefighters Changeroom- Exhaust fan cover is missing | CFRS Maddington | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-10-05 09:45:00 | Fail | Located Missing fan cover in Relief Change rooms, will order a new one and seek approva
MSA-DFES | WA3586797 | internal paint an plaster peeling from water leak- photo to follow in email | WA VES Association - Guildford (old fire station) | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 17:00:00 | 2020-10-16 11:30:00 | Fail | Found gutter/flashing seperated allowing water to seep in Added knock ins to hold it up. Flashing flat to the wall, added seals to fully prevent further issue. Added touch up colour to match existingPainter to attend to repair internal wall damageScraping and plastering wall damages then prime and paint. complete.
MSA-DTAG | WA3586085 | Registry ground Back Office – JSO Workstation Water Leak from roof and down window | Armadale Courthouse | GMP-BR-HO | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-12-17 14:00:00 | Fail | roof repaired to rectify leaking
MSA-DTAG | WA3586512 | Information centre stairwell lighting & fixture - lighting & fixtures faulty, ceased working | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-02 10:30:00 | Pass | Inspected light and replaced due to age
MSA-DTAG | WA3586724 | Level 05 - Pin Pad on Eastern entry into tenant area works intermittently | Central Government Buildings - Perth David Malcom Justice Centre | GMP-BR-HO | Security | Access Control (SE) | Sapio Pty Ltd | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 17:00:00 | 2020-09-01 16:30:00 | Pass | Attended site. Reset Readers on Level 5. Checked transactions. All OK.Job completed.
MSA-DTWD | WA3585942 | Lift 1 is operating but doors will not open | Mount Lawley Campus | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 0 | CLOSE | 01 Sep 2020 | 2020-09-01 12:05:07 | 2020-09-01 10:15:00 | Pass | Lift1 MLT-Hydraulic :lift out of order with doors closed on ground floor. found main processor fault log showing start signal error s7, also found drive tripped with output phase s/c fault. checkedrelevant circuits and rest. tested operation and could not reproduce fault left in service.
MSA-DTWD | WA3585945 | A block, Level 1, Expo - A Block Auto door not working | East Perth Campus | GMP-BR | Building | Automatic Doors (BU) | Assa Abloy Entrance Systems Aust P/L-WA | 1 | CLOSE | 01 Sep 2020 | 2020-09-01 17:00:00 | 2020-09-29 15:00:00 | Fail | Technician attended the site of Central Tafe, to the A block - ground floor Auto Door no. W24312 on 01/09/2020. Following a full test and inspection of door components found fault to be door non operational. When door tried to activate, the motor was making a loud buzzing noise and tech could smell burning coming from logic. He thinks it is a faulty logic, however due to age and condition of door he recommend upgrading door controller as he believe other components are also likely to fail in future.Technician returned on site on 29/09/2020 to remove old faulty BWN EL300 replaced with a UPGRADE kit SL 500 - 2 with all parts and completed quoted works. Full test and inspection of door function completed prior to leaving site. This quote includes:" Please note: New Modernisation Upgrade Kit will be installed internally of the existing automatic door operator eliminating the need for entrance alterations"Removal of existing worn/faulty components."Supply and installation
MSA-DTWD | WA3585948 | B Block, External building E417 (Engine test cell)- Water leaks, with water seeping through external | Midland Campus | GMP-BR | Building | External Walls (BU) | AWB Co. | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-02 09:50:00 | Pass | Water leaks, with water seeping through external walls East side
MSA-DTWD | WA3585984 | Admin & tower block boilers faulty – not starting | West One Services | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 1 | CLOSE | 01 Sep 2020 | 2020-09-02 17:00:00 | 2020-09-01 13:30:00 | Pass | 1) Tower gas burner - pilot required adjustment2) Admin gas burner - works when switched to "Manual" but does not start on "Auto". BMS requires checking by others
MSA-DTWD | WA3585994 | G Block Staff room, reduce HWS temperature please as staff member has burnt herself | Rockingham Campus | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-07 17:02:00 | Fail | Leak on tank warranty inspection
MSA-DTWD | WA3586070 | B block, Eastern entry door lock jammed | Rockingham Campus | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-01 10:15:00 | Pass | repairs to lock
MSA-DTWD | WA3586087 | Sink hole opened up in delivery driveway, canteen (possibly caused by drainage issue) | Rockingham Campus | GMP-BR | Plumbing & Drainage | Drainage (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-07 15:30:00 | Fail | Fill in Hole in driveway
MSA-DTWD | WA3586151 | S block, science block - AHU5 is in fault | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-01 12:00:00 | Pass | Reset vsd and cleared error
MSA-DTWD | WA3586152 | water leaking from a hot water air conditioning pipe outside of room T114 in T Block | Murdoch Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Equans Mechanical Services Australia | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-19 15:00:00 | Fail | Repaired leak as per BRAF
MSA-DTWD | WA3586177 | E block, hallway - ants in lockers in hallway | Joondalup Kendrew Campus | GMP-BR | Pest Control | General Pest (PC) | Swan Pest Control | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-30 08:25:00 | Fail | Inspected E Block and staffrooms. Sprayed all lockers, hallways, staffrooms and external of perimeter with 20 Litres Firponil @ .6%
MSA-DTWD | WA3586196 | North Block, second level - power out | Mount Lawley Campus | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 0 | CLOSE | 01 Sep 2020 | 2020-09-01 14:04:05 | 2020-09-01 13:00:00 | Pass | Job complete
MSA-DTWD | WA3586308 | C Block, Room C102- Repair door handle to C102 inside handle | East Perth Campus | GMP-BR | Building | Doors (BU) | AWB Co. | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-04 13:00:00 | Pass | Liam Hanlon (04/09/2020) - Work Note*security signed attendance as Steve Meyer is off site Attend and get keys Inspect c block handles all working fine Working with electronic strike external gate into workshop Called Steve to confirm issue He will check with staff who had reported it
MSA-DTWD | WA3586456 | Block 6, 6A4 VBB Tool Store- Faulty ceiling light | Thornlie Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-04 10:15:00 | Pass | Attended site , signed in , spoke to pfm on site , located light needing fixing , completed jsa, set up work area , removed old tube and starter, replaced with new, tested light, light now working , cleaned up work area, completed paperwork ***job complete
MSA-DTWD | WA3586486 | A block ground courtyard Floor lights protruding out of ground and not working | Fremantle Campus (formerly WA Maritime) | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-15 15:30:00 | Fail | Attended site and signed in. Talked to nick about how we were going to cover up the up lights. Cut down metal checkered plates to correct size. Installed metal plates over down lights. Informed nick of completion of job. Job complete.
MSA-DTWD | WA3586491 | J block, External building J126 - Water leaks, above belt sander near the electrical switch board | Midland Campus | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-08 15:15:00 | Fail | COMPLETED
MSA-DTWD | WA3586555 | A Block, Room A001- Student Sevices reception area- Broken AC vent | Balga Campus | GMP-BR | Air Conditioning | Room Air Conditioners (AC) | Precise Air Group | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-10 09:00:00 | Fail | Accesssed site completed relevant sign in procedures , notified relevant personal of works to be undertaken , set up exclusion zone behind front counter of A block administration, removed old faulty grill and replaced with new , tested and inspected all working within spec
MSA-DTWD | WA3586563 | Level 2, FIP panel - Fault on Fire Panel | Perth Campus B6 | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-11 12:00:00 | Fail | Fault on fire panel.New wireless expander required due to failure.Day 1 & 2 used to investigate and day 3 to replace.
MSA-DTWD | WA3586676 | B Block, Room B310.1 and B310.2- Roof leak | East Perth Campus | GMP-BR | Roofing | Metal Roofing (RF) | Midolo Building Services | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2021-07-02 14:00:00 | Fail | roof leak repairs
MSA-DTWD | WA3586685 | W block L1 Corner of Building in courtyard Cracked corner of West Block Building | Mount Lawley Campus | GMP-BR | Building | Internal Walls (BU) | AWB Co. | 3 | CLOSE | 01 Sep 2020 | 2020-09-08 17:00:00 | 2020-10-13 12:54:00 | Fail | Work completed
MSA-DTWD | WA3586728 | A block top floor investigate dampness on brick wall & floor under carpet in office east side A48 | Midland Campus | GMP-BR | Flooring | Concrete (FL) | AWB Co. | 2 | CLOSE | 01 Sep 2020 | 2020-09-04 17:00:00 | 2020-10-05 10:00:00 | Fail | The scope covers both affected areas.Scope of Works - 2 x Shower Recess •Demo tiles on walls and shower floors only.•Patch affected walls after demo.•Supply + install water proofing as required.•Supply + install closest possible colour match tiles to shower walls and floor only.•Removal of all waste materials on completion of works.Note •Allowance for demo to be carried out due to noise restrictions.•All other works to be carried out during normal hours.Exclusions•No allowance for any works other than in the shower area only.
MSA-DCA | WA3586972 | Disabled toilet Ground floor near North Exit is blocked up. | State Library of WA-Main Building-Ground Floor-Male and Disabled Toilet | GMP-BR | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-02 17:20:00 | Pass | Unblocked disabled toilet
MSA-DCA | WA3587036 | Level 1, upstairs foyer - Led light fitting flashing intermittently | Subiaco Arts Centre-Main Building-Level 1 | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-10-27 11:30:00 | Fail | Reinstalled light that had previously had a faulty driver. All working
MSA-DCA | WA3587041 | Ground, upstairs foyer - Main entry door dragging on floor as it opens. Heritage door | Subiaco Arts Centre-Main Building | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-04 12:00:00 | Pass | Inspected door. Removed door to discover top pin locator was worn. Redrilled new locator hole, re-used latch plate and planed small section of bottom RHS of door to allow door to open and close smoothly. Job complete
MSA-DCA | WA3587170 | Door can’t be locked - see notes | Subiaco Arts Centre-Main Building-Ground Floor-Undercroft | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-02 14:30:00 | Pass | Adjustment to strike and reposition strap bolt strike and replace lw60mm 530 latch and service to lock and adjust position of lock in door. Steel and glass door in under Croft.
MSA-DCA | WA3587278 | Main Foyer front desk Unable to switch on lights at front desk - see notes | Maritime Museum Victoria Quay-Main Building-Ground Floor | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-03 12:00:00 | Pass | Works being completed under work order WA3628109.
MSA-DCS | WA3586907 | Zone 14 Perimeter - intermittently not working | Bandyup Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 07:11:29 | 2020-09-07 11:30:00 | Fail | Travelled to site and realigned microwave zone 14. All realigned and tested ok. Tested microwave activation and found alarm is clearing itself without officer processing alarm. Checked all logs and settings on programming side. All programming checked ok. Disconnected cabling from microwave and confirmed correct operation to controller . Relocated microwave input to spare input on Gallagher board and re walk tested zone. All walk tested ok. Alarm reset correctly once officer had processed alarm. All working ok. Job complete
MSA-DCS | WA3586915 | Unit 3, D wing - hot water system not working | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 07:16:15 | 2020-09-02 10:00:00 | Pass | COMPLETED
MSA-DCS | WA3586917 | Unit 2, middle landing - hand basin taps fault | Karnet Prison Farm | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-17 09:00:00 | Fail | COMPLETED
MSA-DCS | WA3586919 | Edvoc 2 - z remote arming station offline - impacting all the PIR's | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-03 11:30:00 | Pass | Edvoc 2 keypad not working. Checked voltage and found only 5mV. Traced cabling and found fuse blown. Replaced fuse but to no avail as fuse blew again. Traced LAN and found short. Re-terminated and replaced fuse. Tested and all is in working order.
MSA-DCS | WA3586923 | Zones 7-8, Inner perimeter, node 4 - mains fail, controller 114 failed | Banksia Hill Detention Centre | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-03 14:30:00 | Pass | Checked all EC cabinets up to EC4. Devices looked as if were online. Power cycled all devices in cabinet and control confirmed alarms have cleared. Tested operation and all is in working order.
MSA-DCS | WA3586949 | DCP not working/frozen | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 07:44:05 | 2020-09-07 12:57:00 | Fail | Sourced new Workstation,programmed and installed.
MSA-DCS | WA3586956 | Unit 13, C3 - shower drain block, draining very slow | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-02 13:00:00 | Pass | Nill
MSA-DCS | WA3586962 | SOP, A wing - Overhead bed light globe needs replacing it is flicking | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-03 13:00:00 | Pass | Repaired faulty lights in SOP a wing
MSA-DCS | WA3586967 | Unit 5 - light not working, cleaning cupboard in b wing, | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-03 11:30:00 | Pass | Repaired faulty lights in unit 5 store room
MSA-DCS | WA3586976 | Unit 7, Roofspace over wings C & D there is a pump which is leaking. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-10-13 16:00:00 | Fail | Nill
MSA-DCS | WA3586999 | Gatehouse - Reed switch on interlock sally port override not working | Banksia Hill Detention Centre | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 02 Sep 2020 | 2020-09-02 12:26:13 | 2020-09-03 09:30:00 | Fail | Reed switch faulty for roller door. Replaced reed switch and magnet. Removed override and tested operation, all is in working order.
MSA-DCS | WA3587003 | Lvl 2, rear stairs - Card Reader keeps beeping and not functioning correctly | East Perth | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 08:33:09 | 2020-09-02 15:00:00 | Pass | Lvl 2, rear stairs - Card Reader keeps beeping and notfunctioning correctly. Fault investigated no fault found on arrival card reader working ok check of logs performed card reader reported not responding in the past. Voltages checked panel 13.1 reader 12.6v reader on card presentation 12.2 tested ok. Card reader swapped with level 3 reader. Tested ok no fault found.
MSA-DCS | WA3587044 | Unit 1, Cell D9 - Window wont open or close | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-14 14:45:00 | Fail | RE NEW SPIRAL BALANCES
MSA-DCS | WA3587046 | Unit 2, Cell D6- Ceiling is leaking | Hakea Prison | GMP-BR- HO | Building | Ceiling (BU) | Midolo Building Services | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-02 10:45:00 | Pass | DRY AND CLEAN GUTTER, REPAIR KINKED SHEETING - OUTLET AND PATCH BOX GUTTER
MSA-DCS | WA3587049 | Unit 5, Cell B6- sink is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-07 08:30:00 | Pass | Nill
MSA-DCS | WA3587059 | Unit 4, Cell C5- Window not functioning, not opening | Casuarina Prison | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-03 14:00:00 | Pass | NEW SPIRAL BALANCES & FEET INSTALLED
MSA-DCS | WA3587133 | A10 Unit 13 light switch turns on then turns off. | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 08:30:00 | Pass | Repaired faulty lights in u13 cell a10
MSA-DCS | WA3587137 | Unit 6 - D Wing drain in the floor of the cleaning locker appears to be blocked. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-03 14:00:00 | Pass | Nill
MSA-DCS | WA3587184 | perimeter zone 1C infered in constant alarm | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 10:19:36 | 2021-01-14 09:00:00 | Fail | realign tx6rx pe beams tested ok
MSA-DCS | WA3587280 | Unit 5, House 9- Bathroom light is burnt | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-04 14:00:00 | Pass | Replaced oyster light
MSA-DCS | WA3587286 | Unit 5, House 1 & 9- passage vent winders not working | Bandyup Prison | GMP-BR- HO | Building | Windows (BU) | Schlager Construction Group | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-03 13:00:00 | Pass | Attended site and carried out repairs to the high level air vents located in the passages of units
MSA-DCS | WA3587305 | Unit 5, House 5- oven door has shattered | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 11:09:56 | 2020-09-09 12:30:00 | Fail | Replaced smashed oven in house 5
MSA-DCS | WA3587473 | Karakin, Office- hot water unit not working | Banksia Hill Detention Centre | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-07 11:07:00 | Pass | Replaced hot water unit in the office kitchen
MSA-DCS | WA3587581 | gate house front door not locking when going through with fob | Wandoo Rehabilitation Facility | GMP-BR- HO | Security | Access Control (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 13:58:34 | 2020-09-02 15:45:00 | Pass | Tested RFI lockdown for main entry airlock but to no avail. Tested override button operation but to no avail. Found logic block overridden. Cancelled override and tested, all is in working order.
MSA-DCS | WA3587632 | Unit 2 - Front Entrance Two lights need replacing outside the front door under the eaves. No longer | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-11-12 10:00:00 | Fail | Investigate and repair unit 2 external lighting
MSA-DCS | WA3587667 | unit 1 A wing kitchen HWS under bench leaking copper pipe | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-09 15:00:00 | Fail | COMPLETED
MSA-DCS | WA3587668 | 1x Kitchen & 1x Office Demountable - Flickering lights | Warminda Hostel | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 15:03:57 | 2020-09-03 10:30:00 | Pass | Repaired lighting in kitchen and office of demountable out building.
MSA-DCS | WA3587736 | admin and industries PA speakers not working | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-12-11 14:00:00 | Fail | Industries PA Speakers restored - works completeAdmin/U2 court yard speakers removed when light pole was removed from site - advised site to report this separately as not related to Industries fault, new cable routes will need to be identified.
MSA-DFES | WA3587183 | Kitchen- GPO has come away from the wall- further notes below | CFRS Welshpool | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-07 15:30:00 | Pass | Arrived on site to repair kitchen GPO. Found unit had been pulled out and cable was short. Lengthened cable and fitted new mountingblock. Refitted GPO tested and signed out
MSA-DFES | WA3587190 | Library Room in Workshop- . Card access not working and key cannot be located. | Fleet Management Services - O'Connor Workshop | GMP-BR | Security | Access Control (SE) | SONTEC WA PTY LTD | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-02 15:15:00 | Pass | 2/9/20 - Dylan ParslowFound relay not responding to input on door controller, reset and tested, all ok.
MSA-DFES | WA3587746 | admin ground Exit signs not working Training Dining Room and East Exit door. | FESA RHQ - Forrestfield | GMP-BR | Electrical | Emergency & Exit Lighting (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-09 11:00:00 | Fail | CompleteCollected gear and attended site, replaced faulty exit signs and tested all in working order. Notified staff and signed out
MSA-DTAG | WA3586933 | Level 1, FIP - Technician required to assist Australian HVAC on Saturday 5 September from 07.00am | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 02 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-05 12:03:00 | Pass | Completed HVAC testing with contractors
MSA-DTAG | WA3586937 | Level 6, plant room - door closer bracket has detached from the frame | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 02 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-04 10:00:00 | Pass | DOOR CLOSER REPLACED (FROM ONSITE)
MSA-DTAG | WA3586944 | Ground, external - water entering custody cells area, | Joondalup Courthouse | GMP-BR-HO | Roofing | Guttering (RF) | Midolo Building Services | 3 | CLOSE | 02 Sep 2020 | 2020-09-08 17:00:00 | 2020-11-23 09:00:00 | Fail | ROOF REPAIRS COMPLETED
MSA-DTAG | WA3587025 | level 8, waiting area - several seats are loosr, please drill & bolt through cross beam | Central Law Courts | GMP-BR-HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-03 14:30:00 | Pass | SEATS BOLTED TO CROSSBEAM
MSA-DTAG | WA3587084 | Lvl 2, Staff Kitchen- Overhead kitchen cabinet fixings are loose | Central Law Courts | GMP-BR-HO | Furniture | Indoor Furniture (FU) | Midolo Building Services | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-02 10:34:00 | Pass | CABINETS RE SECURED- JOB ATTENDED BEFORE LOGGED - 9.30-10.30AM
MSA-DTAG | WA3587091 | L6 Prisoner Review Board Office Replace water stained ceiling tiles in records area3 | Central Law Courts | GMP-BR-HO | Building | Ceiling (BU) | Midolo Building Services | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-02 12:00:00 | Pass | DAMAGED CEILING TILES REPLACED- JOB ATTENDED TO BEFORE IT WAS LOGGED - 7.30-9.30AM
MSA-DTAG | WA3587195 | Level 5 - Graffiti in waiting room outside Court 58 | Central Law Courts | WSM-BR-SITE | Cleaning | Graffiti (CL) | PPM Project Painting & Maintenance | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-04 12:00:00 | Pass | Removed graffiti
MSA-DTAG | WA3587389 | Lift 3 is showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 2 | COMP | 02 Sep 2020 | 2020-09-07 17:00:00 | 2021-09-02 15:43:00 | Fail | Job completed -
MSA-DTAG | WA3587394 | Level 1 - Revolving door has ceased to function | Central Law Courts | GMP-BR-HO | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-03 14:46:00 | Pass | Encoder pin had come off so door lost its position. Re fixed it But both rubbers rings are badly worn. Will need to return to replace.Returned to site replaced encoder rings and tested all ok
MSA-DTAG | WA3587421 | Court room 3, Custody - 6x Fluroescent lights have ceased working | Joondalup Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | Gilmour & Jooste Electrical | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-08 08:30:00 | Fail | Replaced faulty lighting and tested working
MSA-DTAG | WA3587673 | Registry Back office- Ceiling leaking (possibly sprinkler) with a strong urine smell in the area. | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-04 11:15:00 | Fail | Complete
MSA-DTAG | WA3587680 | ground female staff toilet last cubicle is leaking water all over floor | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-04 12:15:00 | Fail | Complete
MSA-DTAG | WA3587726 | ground staff male toilet Water from the cistern to the urinal al times would not stop. | Midland Courthouse | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-15 14:00:00 | Fail | Complete
MSA-DTWD | WA3586928 | Oil & Gas processing plant, plant - light pole - 4 lights on pole are out cherry picker required | Munster Campus (ACEPT) | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 1 | CLOSE | 02 Sep 2020 | 2020-09-02 17:00:00 | 2020-09-11 14:30:00 | Fail | Attended site, signed in , completed jsa, used ewp to replace 5 faulty street lights , replaced with led , tested lights all working , left old lights on site , cleaned up work area completed paperwork signed out ***job complete***
MSA-DTWD | WA3586988 | Q block, plant room - chiller has a flow fault on P-2 | Joondalup McLarty Campus | GMP-BR | Refrigeration | Chiller (RE) | Precise Air Group | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-09 16:00:00 | Fail | Investigate BMS fault - found AHU2 Isolation valve close and the bypass valve forced. Re-check, found ok.
MSA-DTWD | WA3586998 | E-Cafe large glass sliding door scraping on ground and hooking on top sill when closing | Clarkson Campus | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-02 15:20:00 | Pass | On inspection, found end stop missing and doors scrapping along floor.Adjusted doors and fitted new end stop, tested and adjusted, all ok.Framework not square/ level.
MSA-DTWD | WA3587063 | D block L1 Library a computer wall port PP2-P2-21/22 pushed in barely making connection | Joondalup Kendrew Campus | GMP-BR | Electrical | General Electrical (EL) | Techworks Electrical | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-03 14:30:00 | Pass | Mechs were broken from force, replaced with new.
MSA-DTWD | WA3587067 | L2 ROOM/OFFICE: D223 small roof leak near the lecturers computer | Perth Campus B4 | GMP-BR | Roofing | Metal Roofing (RF) | AWB Co. | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-07 13:30:00 | Pass | work completed as per signature slip
MSA-DTWD | WA3587290 | L1 W126 light blown | Perth Campus B1 | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 10:30:00 | Pass | Attended site, replaced multiple T5 tubes throughout lvl 1 in building 1. Job complete.
MSA-DTWD | WA3587374 | G block demo area tap leaking | Bentley Campus | GMP-BR | Plumbing & Drainage | Water (PD) | Falcetta Plumbing and Gas | 1 | CLOSE | 02 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-03 14:09:00 | Pass | Fix leaking taps
MSA-DTWD | WA3587490 | L1 student kitchen hot water leaking. | Perth Campus B1 | GMP-BR | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Falcetta Plumbing and Gas | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-30 16:30:00 | Fail | Install new billi as per braff
MSA-DTWD | WA3587561 | A block L1 Corridors and rooms Throughout most of level animals in roof void-see notes | Mandurah Campus (formerly Peel) | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-10-21 22:30:00 | Fail | 8/9/20 - Sealed all access holes into the roof space. One 600 x 600 hole left open so possums can escape. Once possums are out we need to seal this hole with cement sheet 9/9/20 - Spoke with Janine, she agreed to let us know when the possums are out so we can return to seal the remaining hole 23/10/20 - Marty on site confirmed ok to close off
MSA-DTWD | WA3587617 | Kone lift stench coming from base of lift | Perth Campus B6 | GMP-BR | Lifts | Lifts (LI) | Kone Elevators Pty Ltd | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-03 14:15:00 | Pass | no issue found
MSA-DTWD | WA3587620 | B Block, Room B203.1 - lights not working | East Perth Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 02 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 16:45:00 | Pass | Job complete
MSA-DTWD | WA3587636 | Glasshouse - Hot water boiler seems to have low gas flow | Murdoch Campus | GMP-BR | Mechanical Services | Boilers (MS) | WA BOILER SPARES & SERVICE | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-07 15:30:00 | Pass | Attended site, replaced faulty main gas solenoid valve as per BRAF
MSA-DTWD | WA3587714 | U block U022 machine shop water leak | Balga Campus | GMP-BR | Building | Ceiling (BU) | AWB Co. | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-08 09:45:00 | Fail | Multiple leaks to U block around vent systems, Penetrations etc, will need to return to complete moreReturned and checked over areas for possible leak scenarios - made multiple repairs but believe larger works still required. BRAF submitted (declined)
MSA-DTWD | WA3587952 | Store Room, P011 - Fluro tube is not working | Balga Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 02 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-07 15:30:00 | Pass | Checked lights in p 011 store. Site advised lights are okay.no action taken
MSA-DCS | WA3587824 | Reception - reception sally port door has come off the rollers | Hakea Prison | GMP-BR- HO | Building | Doors (BU) | AFD Contracting | 0 | CLOSE | 03 Sep 2020 | 2020-09-03 11:13:26 | 2020-10-14 13:39:00 | Fail | 03/09/20Roller door spring appears broken.Door was in up position. Got door down and isolated.New drum required.Need to measure and quote.08/09/20Went to site with supplier to measure. Waiting for supplier quote. BRAF to be submitted.
MSA-DCS | WA3587834 | Monitor control room - CCTV NZR2 has failed/degraded and screen view has changed | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 03 Sep 2020 | 2020-09-03 11:21:48 | 2020-09-09 12:05:00 | Fail | Traced fault to hard drives in NVR2 RAID Array. Sourced parts, replaced failed drives, and replaced is multiple steps which retained all data in array. Restored recording schedule and tested okJob CompleteParts: 2 x 3TB hard drives (SEME stock)
MSA-DCS | WA3587853 | Control room - cell call unit 3 & 5 are not able to answer the cell calls | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 07:30:55 | 2020-09-03 09:00:00 | Pass | Calls going straight to gatehouse control. Unable to conduct PA calls from the units. Checked through ACM file on cell call PC. Reloaded current file and restarted Officer stations. U2 and U5 cell call and PA tested ok locally and to the gatehouse.
MSA-DCS | WA3587883 | Unit 3, C9 - Main lock broken | Hakea Prison | GMP-BR- HO | Security | Locksmith (SE) | AAA Ability Locksmiths | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 07:58:55 | 2020-09-03 09:30:00 | Pass | Attended site and replaced faulty main lock
MSA-DCS | WA3587893 | Unit 1, A/C rear yard CCTV camera is not working | Casuarina Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 08:03:13 | 2020-11-06 15:00:00 | Fail | Replaced AC yard camera with new Indigo BX420. All replaced programmed and tested ok. Recording schedule all setup and working correctly. Job complete
MSA-DCS | WA3587911 | Unit 6, Cell A9- Toilet is not flushing, cistern doesnt seem to be filling up | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-03 13:00:00 | Pass | Nill
MSA-DCS | WA3587912 | Market Gardens, industry - red solenoid cable severed. | Casuarina Prison | GMP-BR- HO | Mechanical Services | Pumps (MS) | Pumps n Pipes | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-04 09:00:00 | Pass | section of wiring replaced
MSA-DCS | WA3587915 | Unit 1, Cell A10- Cistern is leaking water constantly into toilet | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-10 13:00:00 | Pass | Nill
MSA-DCS | WA3587920 | Gatehouse- PE Beams C01F01F03 is in constant alarm. | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-11-10 15:30:00 | Fail | Cleared and corrected with beam sets in zones C01 & F01. Beam Stack 2 in F03 has bottom beam set obstructed by raised road base and construction materials. Have strapped out bottom beam set until construction completed.
MSA-DCS | WA3587939 | Visits - Lost audio in non contact booths | Albany Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 08:34:38 | 2020-09-12 09:23:00 | Fail | Attended site and repaired Jacques Intercom Server. Tested OKJob CompleteParts:Consumables
MSA-DCS | WA3587978 | MPU, M2 - Faulty reading light in M02 | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-08 08:30:00 | Pass | Repaired faulty lights in mpu cell m2
MSA-DCS | WA3587987 | Unit 7, D wing - Pump has failed in SCU, Electrician required to disconnect so plumber can remove & | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-03 15:00:00 | Pass | Disconnected and reconnected pump in scu d wing plantroom
MSA-DCS | WA3588020 | Paint Shop - Toilet Bad smell emitting from toilets. | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-03 16:00:00 | Pass | Nill
MSA-DCS | WA3588090 | Unit 1, A/B kitchen - hot tap wont wont turn off | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 10:42:41 | 2020-09-03 14:47:00 | Pass | Rewashed kitchen taps
MSA-DCS | WA3588106 | Vocational Skills- Sink in the Kitchen requires silicon seal around sink | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-07 14:00:00 | Pass | Nill
MSA-DCS | WA3588111 | Vocational Skills- Tap leaking in the laundry room | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-07 13:00:00 | Pass | Nill
MSA-DCS | WA3588134 | Unit 9 cell A2 Water leaking into cell from burst pipe | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 11:11:39 | 2020-09-03 13:30:00 | Pass | replaced section of burst cold water pipe in ceiling. Times do not match to signature slip, as when we arrived on site we were asked to begin this job to stop water coming through ceiling into the cell, while the work order was created. However there was a delay in the job being created.Therefore times added on work order represent 2 hrs being the time spend but not the correct start and finish times.
MSA-DCS | WA3588139 | Master control MDAS system description of alarms is reading different to location | Greenough Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 11:14:13 | 2020-09-04 14:39:00 | Fail | Technician attended site - investigated fault - Found MDAS Unit 2 and 3 Location Area Description swapped - Changed and Tested OKWorks Compete
MSA-DCS | WA3588155 | SOG Pod - Control Room Simplex fire alarm system consistantly alarming - see notes | Casuarina Prison | GMP-BR- HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Automatic Fire Protection (ARA) | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 11:19:53 | 2020-09-04 11:15:00 | Pass | 4/9/20GAAttended site & inspected POD graphics18 x faults relate to node 3-Industries FIP due to building works. Generator room no detection due to Recovery Maintenance under building works.59 x faults relate to node 11-Reception FIP due to building works. Visits area is under building works.49 x faults relate to node 12-Infirmary FIP due to building works. Infirmary area is under building works.Unit 13Wing b/d 15&16 vesda in low airflow faultFound pipe 3 sampling point fully blocked with toothpaste causing issue cleared and left normalUnit 14B/d cells 9&14 vesda in fault causing by closed valves on pipes 2&4 cleared fault and left normal.B/d cells 3&4 vesda in fault caused by low airflow on pipe 3 cleared pipes and left normal.Unit 15Inspected and found the following faultsCell b16 in flow/sep faultCell b11 in flow/sep faultCell a2 in flow/sep faultStill under warranty requires dlp to rectifyUnit 15Cell c2 in flow/sep faultStill under warranty requires d
MSA-DCS | WA3588182 | Unit 4, Regi Oven - Oven seal is broken | Hakea Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-24 12:45:00 | Fail | Replaced door & trolley seal
MSA-DCS | WA3588211 | Boilerhouse Boiler 3 flame scanner fault | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 14:00:00 | Pass | INVESTIGATE FAULTS ON BOILER #3 - FOUND SKP70 ACTUATOR LEAKING
MSA-DCS | WA3588212 | Unit 2, Cell B1- Blocked drain | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Drainage (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 11:31:22 | 2020-09-03 16:20:00 | Pass | Unblocked basin drain. Prisoner threw a can of coca cola in the drai
MSA-DCS | WA3588215 | Boilerhouse, Boiler No 3- Blowdown valve leaking & very stiff to use | Hakea Prison | GMP-BR- HO | Mechanical Services | Boilers (MS) | Boilertronics | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 11:33:30 | 2020-09-07 14:30:00 | Fail | Put new service kit into blowdown cleaned up faces and re installed on boiler. Put pressure in boiler checked for leaks all good.
MSA-DCS | WA3588325 | Unit 15, Office- Key stuck in Lock, Officer is stuck until rectified | Casuarina Prison | WSM-MW-HO | Security | Locksmith (SE) | Lock It Locksmiths | 0 | CLOSE | 03 Sep 2020 | 2020-09-03 16:08:51 | 2020-09-03 19:42:00 | Fail | Open jammed lock, remove lock body and re install as per manufactures specifications and adjust strike to suit.Lockwood 213 streamlock deadbolt on roof hatches are installed incorrectly by the builder/roof hatch manufacturer. They are not fitted as per manufacturers instructions, this is causing the lock to jam up.
MSA-DCS | WA3588350 | external front gate, PE beams zone I in constant fault | Bunbury Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-11-18 12:17:00 | Fail | Beam stack housing and internal wiring to be fixed on LVM WA3746575
MSA-DCS | WA3588429 | Unit 4A, Cell 15 , Door lock can not lock | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 0 | CLOSE | 03 Sep 2020 | 2020-09-03 17:22:25 | 2020-09-03 16:00:00 | Pass | Replaced faulty cell lock on cell 15 Unit 4A
MSA-DCS | WA3588443 | Internal zone 21 - Microwave fault | Hakea Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-03 16:00:00 | Pass | Unable to secure zone for more than a few minutes at a time. Power and alignment checked ok. R3moved a number of large weeds from around the transmitter and receiver microwave Posts. Tested ok locally and back at control.
MSA-DCS | WA3588456 | Vegetable Preparation - CL60 not working, not turning | Casuarina Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | RUSSELLS MECHANICAL & GAS | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-10-16 09:15:00 | Fail | Vegetable Preparation - CL60 not working, not turning. Check slicer, remove for repairs. Dismantle, replace all faulty parts. Assemble & test. Return to store.
MSA-DCS | WA3588458 | Gatehouse, Control - Mdas screen not responding correctly | Banksia Hill Detention Centre | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-04 16:45:00 | Pass | MDAS and DoJ wireless mouse not working. Middle wheel broken on MDAS and movement not working correctly. DoJ middle wheel not working. Replaced both 2x wireless keyboard and mouse. Tested operation and all is in working order.
MSA-DCS | WA3588502 | L4 disabled and female toilet buttons are damaged | East Perth | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-09 11:01:00 | Fail | Complete
MSA-DCS | WA3588516 | Lenard bathroom - Led light not working | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 12:48:00 | Pass | Attend with new led oyster light to replace in bathroom, had to leave site to get a larger fitting to cover holes in the ceiling
MSA-DCS | WA3588535 | Unit 1 D8 Sink Taps leaking from spout running across top of sink onto the floor | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-04 16:00:00 | Pass | Replaced faulty hot spindle
MSA-DCS | WA3588581 | Duress hardwired button is not working in work camp admin building | Roebourne Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-04 13:00:00 | Pass | Job complete
MSA-DCS | WA3588582 | Unit 4A cell 25 door handle will not turn and cannot lock door | Wooroloo Prison Farm | GMP-BR- HO | Security | Locksmith (SE) | ACE LOCK & SAFE | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 15:53:48 | 2020-09-03 17:00:00 | Pass | Replace cell lock and cut new key on Cell 25 Unit 4A
MSA-DCS | WA3588649 | Unit 13 - Boiler is not working. | Casuarina Prison-Prisoner Accommodation Unit 14 | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Boilertronics | 0 | CLOSE | 03 Sep 2020 | 2020-09-03 21:39:20 | 2020-09-03 22:30:00 | Fail | Attended site and signed in.Escorted to unit 13.Plant room was quite.Made some calls and found out that fire alarm in cell was enough to shut everything down.Reset alarm and witnessed plant room restart.Boiler started as well.Escorted out and signed out
MSA-DCS | WA3589976 | Possible exposed live mains found by another contractor, please investigate and make safe | Banksia Hill Detention Centre | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 03 Sep 2020 | 2020-09-09 17:00:00 | 2020-10-12 12:00:00 | Fail | Made cable safe and installed new cable duct to plus cut out floor tiles
MSA-DFES | WA3588337 | ground external front ESC Uneven paving located one metre from steps at front of ESC building. | DFES Cockburn Emergency Services Complex | GMP-BR | Paving & Roadworks | Paving (PR) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-10-11 13:00:00 | Fail | Attended Sunday 11th works now complete.
MSA-DFES | WA3588413 | External door to ladies toilet, opposite Reception is very stiff to open. | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-07 15:30:00 | Pass | Sand back top edge of sticking door to female W/C door adjacent to admin reception. Now opening smoothly. Job complete
MSA-DFES | WA3588504 | Rear of Floor, next to Kitchen, Ladies toilet- Exhaust fan not operating correctly- see notes below | DFES Regional Office - Joondalup | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-16 13:30:00 | Fail | Located Faulty fan in women’s toilet, I proved power and the fan has seized. I have taken down the model numbers and will seek approval before ordering a replacement.Replaced faulty exhaust fan in woman’s toilet and checked that everything is working correctly.
MSA-DFES | WA3597482 | RETROSPECTIVE WORK ORDER-INTERNAL & EXTERNAL CHECK CARRIED OUT - DO NOT ATTEND | CFRS Midland | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-03 18:35:00 | Pass | Despatch Comments:Z13 REED ON ROLLER DOOR 4 SINGLEPatrol Resolution:INTERNAL & EXTERNAL CHECK CARRIED OUT. NO OFFENCE DETECTED. NO PERSONS FOUND ONSITE. ALL APPEARS SECURE. SEAL CONFIRMED JUNE MONITORING
MSA-DTAG | WA3588079 | Ground - Exit door threshold plate is buckled | Joondalup Courthouse | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-05 09:30:00 | Pass | exit door threshold replaced
MSA-DTAG | WA3588085 | Staff Kitchen - Hot water unit under sink is leaking | Central Law Courts | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-08 11:05:00 | Pass | Complete
MSA-DTAG | WA3588114 | Registry, Water dripping from sprinkler head – extremely high ceiling | Central Law Courts | GMP-BR-HO | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-04 13:00:00 | Pass | Works to be quoted see other description
MSA-DTAG | WA3588244 | Registry, above front counter - Flickering light | Armadale Courthouse | WSM-BR-SITE | Electrical | Lighting, Internal (EL) | AWB Co. | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-03 13:30:00 | Pass | Job complete.
MSA-DTAG | WA3588330 | Basement, entry gate- no visual in our control room | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-16 16:30:00 | Fail | Attended site. Replaced faulty Cisco Switch with new Allied Alliance Network Switch.rack. Checked and tested, all OK.Job completed.
MSA-DTAG | WA3588396 | Door within Court 52 leading to toilets – lock not engaging - see notes | Central Law Courts | WSM-BR-SITE | Security | Locksmith (SE) | Bullant Security Pty Ltd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-15 13:45:00 | Fail | Attended site and swapped handles around to secure and be working. Replacement handles required.Date on site: 04/09/2020Time on site: 12:55pm - 01:20pmReturned to site to install replacement handle.Date on site: 15/09/2020Time on site: 01:00pm - 01:45pm
MSA-DTAG | WA3588406 | custody control cameras having problems with coverage - see notes | Joondalup Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-04 14:00:00 | Pass | Repairs to camera's
MSA-DTAG | WA3588518 | Lvl 7, Quasi Judicial - Shelving panel has detached from office wall | Central Law Courts | GMP-BR-HO | Building | Materials (BU) | Midolo Building Services | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 08:45:00 | Pass | SHELVING PANELS RE SECURED
MSA-DTAG | WA3588601 | ground/L1 No hot water from the taps | Midland Courthouse | WSM-BR-SITE | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-17 09:30:00 | Fail | Complete
MSA-DTAG | WA3588602 | ground supreme museum alarm is activating and cannot turn off | Supreme Court | GMP-BR-HO | Security | Monitoring (SE) | Sapio Pty Ltd | 0 | CLOSE | 03 Sep 2020 | 2020-09-03 20:58:47 | 2020-09-04 16:30:00 | Fail | job completed - Replaced alarm panel battery, confirmed low battery alarm has restored. Tightened Zone 7 termination, PIR tested OK.System is obsolete, if issue reoccurs, recommend replacing with new
MSA-DTAG | WA3589988 | Lag in CCTV footage on custody workstation - Retrospective W/order | Midland Courthouse | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 3 | CLOSE | 03 Sep 2020 | 2020-09-09 17:00:00 | 2020-10-05 10:00:00 | Fail | job completed - Attended site. Installed new PCIe network card inside PC workstation. Installed driver, programmed IP, connected to thenetwork and tested operation. Connected new wireless keyboard and mouse and tested operation. Checked all camerasstreams settings and setup recording and live view streams to appropriate value. Checked workstation performance.Job completed.
MSA-DTWD | WA3587923 | S Block, Room S115- Light not working | Mount Lawley Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 10:37:00 | Pass | Repalced faulty lamps to classroom.job completed
MSA-DTWD | WA3587949 | **RETROSPECTIVE WORK ORDER **Fire pump running unexpectly- further notes below | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 03 Sep 2020 | 2020-09-03 17:00:00 | 2020-09-03 08:15:00 | Pass | *RETROSPECTIVE WORK ORDER **Fire pump running unexpectly- further notes belowSite:5739Location:South Metro TAFE-Mandurah Campus (formerly Peel)Address 1:Education Drive GREENFIELDSAddress 2:WA 6210 Australia-COMPLETEDNEW PLUG INSTALLED TODAYBRAF TO FOLLOW FOR REQUIRED WORK
MSA-DTWD | WA3588004 | T Block, Ground floor, Male student next to café - W.C pan blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-04 09:13:00 | Pass | Unblocked toilets
MSA-DTWD | WA3588006 | T Block, L1 Female stude - W.C pan blocked | Murdoch Campus | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-04 09:15:00 | Pass | unblocked toilet
MSA-DTWD | WA3588064 | G block ground female toilets blocked | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 15:29:00 | Pass | Unblock toilets
MSA-DTWD | WA3588065 | G Block, Male Toilet- Urinal closest to sink is overflowing | Mandurah Campus (formerly Peel) | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | Falcetta Plumbing and Gas | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 15:28:00 | Pass | Unblock urinal
MSA-DTWD | WA3588124 | Classroom C14- High level florescent lights and fittings Broken | Murdoch Campus | GMP-BR | Electrical | Lighting, Internal (EL) | AWB Co. | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-25 16:15:00 | Fail | attended site , signed in , spoke with fm about job, completed jsa, isolated power, removed old light fittings , replaced with led fittings , re energised circuit, tested lighting, all working as intended, cleaned up work area , completed paperwork, signed out ***job complete***
MSA-DTWD | WA3588356 | L1 B148 door closer not working | Perth Campus B6 | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-04 09:48:00 | Pass | Attend the site, found door was banging when closing found door closer is faulty.Returned to site, removed faulty door closer and replaced with new ts83 closer, adjusted and tested operation upon completion and left in good working order.
MSA-DTWD | WA3588369 | E block ground EG19 Upright freezer not working correctly (2 x glass door). Food defrosting. | Mandurah Campus (formerly Peel) | GMP-BR | Refrigeration | Freezers (RE) | Equans Mechanical Services Australia | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-07 12:00:00 | Fail | ARRIVED ON SITE SIGNED IN, CHECKED IN WITH SHARON. GAINED ACCESS KEYS, GATHERED TOOLS AND EQUIPMENT. CHECKED FREEZER FOUND IT TURNED OFF. SWITCHED UNIT ON TESTED OPERATION, COMPLETED LEAK CHECKS ALL OK. CHECKED OPERATION ALL OK. FREEZER GOT DOWN TEMPERATURE -21 OK. CLEANED CONDENSERCOIL. MONITORED OPERATION NO FAULTS LOCATED. POSSIBLY DOORS NOT CLOSED PROPERLY AND OVER NIGHT HAD EVAPORATIVE COILICED UP. EXCESS WATER FOUND IN DRAIN TRAY. WITH TURNING FREEZER OFF OVER NIGHT CORRECTED FAULT AS AN TEMPERATURE ALARM APPARENTLY ALARMING. CLEANED UP WORK AREA COMPLETED PAPERWORK AND SIGNED OUT.
MSA-DTWD | WA3588375 | c block, ground secuirty lighting not working | Bentley Campus | GMP-BR | Electrical | Lighting, External (EL) | AWB Co. | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-03 14:30:00 | Pass | Attended site and signed in. Located faulty lights. Checked all electrical switchboards. Found a timer not programmed correctly. Showed site. All now working.
MSA-DTWD | WA3588486 | D Block, Kitchen D3- Timer on rotal oven is broken | Bentley Campus | GMP-BR | Equipment | Catering Equipment (EQ) | BAKE-QUIP PTY LTD | 2 | CLOSE | 03 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 14:45:00 | Pass | COMPLETED 7/9/20
MSA-DTWD | WA3588534 | A/C plant room - Boiler faults- not starting | West One Services | GMP-BR | Mechanical Services | Boilers (MS) | Precise Air Group | 3 | CLOSE | 03 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-08 10:00:00 | Pass | Attended site to check operation of admin boiler. Found comms issue with Chiller Two board. Old issue with power points not working. Have spoken to Kim onsite to get issue resolved. Reconnected temporary power to switch and now okay. Checked admin boiler and now working, running okay. Also found Tower Boiler tripped, reset and now okay.
MSA-DTWD | WA3657494 | **RETROSPECTIVE WORK ORDER **Fire pump running unexpectly- further notes below | Mandurah Campus (formerly Peel) | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | SCAVENGER SUPPLIES PTY LTD | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-29 16:12:00 | Fail | **RETROSPECTIVE WORK ORDER **Fire pump running unexpectly- further notes belowSite:5739Location:South Metro TAFE-Mandurah Campus (formerly Peel)Address 1:Education Drive GREENFIELDSAddress 2:WA 6210 Australia-COMPLETED
MSA-MRWA | WA3588595 | room 620 Cupboard lock missing please remediate to working order. | Don Aitken Centre MRWA Head Office-Main Building-Sixth Floor | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 03 Sep 2020 | 2020-09-04 17:00:00 | 2020-09-04 12:00:00 | Pass | Attended to cabinet lock. Not able to cut keys on site. Client has another solution. No further action required.
MSA-DCA | WA3589214 | Disable lift making grinding noise - keeps happeing please provide recoomendations | His Majesty's Theatre-Theatre Building-Ground Floor | GMP-BR | Lifts | Lifts (LI) | TK Elevator Australia Pty Ltd | 1 | CLOSE | 04 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-04 14:30:00 | Pass | Lift3 DisHoist HMT-Accessibility unit :on arrival found lift making good a noise in the down direction, applied lubricants, this reduced the noise slightly, I found the noise only happens if a personstands right at three front of the platform, if you stand in the middle or to the basement door side there is no noise .to adjust guides and clean old lubricant from rails wall panels need to be removed.follow up this option.COMP at $0
MSA-DCA | WA3589298 | carpark, beer refrigeration unit is not working. | Perth Concert Hall-Main Building-Basement | GMP-BR | Refrigeration | Refrigerators (RE) | Precise Air Group | 1 | CLOSE | 04 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-29 14:57:00 | Fail | BRAF declined by client
MSA-DCA | WA3589363 | Flush button on urinal pops out and lands on floor | State Library of WA-Main Building-Level 3-3.97 - Staff Male Toilet | GMP-BR | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-08 10:35:00 | Pass | Replaced Induct cistern for urinal
MSA-DCS | WA3588713 | Control room - PTZ camera 36, not recording and multiple others not recording | Boronia Pre-release-AS14 - Administration and Visitors Centre-Ground Floor-Security Room | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 04 Sep 2020 | 2020-09-04 11:16:27 | 2020-09-07 10:07:00 | Fail | Investigated faults, repaired NVR recording issues. Tested OKJob Complete
MSA-DCS | WA3588744 | Unit 2, B wing, Cleaning Cupboard - water leaking from pipes, can see it clearly when showers in use | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 15:00:00 | Pass | Nill
MSA-DCS | WA3588748 | 6, C2 - Broken light switch | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 07:54:29 | 2020-09-04 10:00:00 | Pass | Replaced broken light switch
MSA-DCS | WA3588753 | Unit 6, A8 - toilet pan cracked | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 07:59:37 | 2020-09-04 14:50:00 | Pass | Replaced broken tpilet pan
MSA-DCS | WA3588810 | Visits area- CCTV camera feed screens in the Lobby are not working | Casuarina Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-04 13:00:00 | Pass | On arrival at Prison at 07:00 requested to attend to Fault. Tested and confirmed PC would no start. Arranged for temp PC and installed to provide visibility to Visits Officer. Removed workstation PC to Crypt and stripped down. Checked mother board for component damage cleaned all contacts and reseated PCB’s. Tested and confirmed power supply, reassembled and tested. Returned to site, reinstalled, and setup monitors.
MSA-DCS | WA3588816 | Unit 8, Cell B7- Light switch outside cell broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 08:34:09 | 2020-09-04 11:30:00 | Pass | Replaced broken light switch
MSA-DCS | WA3588837 | Unit 2B, Cell 7- window vent is damaged | Wooroloo Prison Farm | GMP-BR- HO | Building | Windows (BU) | Midolo Building Services | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 08:43:42 | 2020-09-04 15:00:00 | Pass | REPAIR WINDOW FRAME & REPLACE VENT
MSA-DCS | WA3588869 | Control computer monitor not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-07 12:52:00 | Pass | monitors working ,cameras had dropped off freeze frame pc. rebooted & all back to normal.2 x monitors sent to site
MSA-DCS | WA3588980 | L4 and L2 male toilets urinals bad smell coming from urinal | East Perth | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-04 15:00:00 | Pass | Complete
MSA-DCS | WA3589017 | Unit 4, Cell D9- leak seems to be coming from behind the tile- see further notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 11:00:00 | Pass | Nill
MSA-DCS | WA3589049 | Unit 13- No hot water | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-10-06 08:30:00 | Fail | NOTE: Uv light and guardian has also tripped and an issue was found and reported to casuarina maintenance, further investigation to be carried Out
MSA-DCS | WA3589116 | entry control pod mixer tap faulty - AHS on site | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 11:42:43 | 2020-09-04 14:05:00 | Pass | COMPLETED
MSA-DCS | WA3589145 | Academy Accommodation Wing - Light in bedroom No.14 not working.Power point in dining room is faulty | Hakea Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-07 09:30:00 | Pass | Repaired light replaced gpo
MSA-DCS | WA3589189 | unit 3 MMU prisoner kitchen tap leaking | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-10 08:30:00 | Fail | Completed, 2 x enware qtr turn detention spindles replaced
MSA-DCS | WA3589192 | unit 6 cell 11 shower head damaged and leaking-non ligeture shower head | Bandyup Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-10-05 15:00:00 | Fail | COMPLETED
MSA-DCS | WA3589203 | Vocational Skills- Light in office not working- see notes below | Casuarina Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-11 08:30:00 | Pass | Repaired faulty lights in in voc skills office
MSA-DCS | WA3589205 | Command centre not responding | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 13:03:00 | 2020-09-09 02:24:00 | Fail | Gallagher software not working correctly.Reloaded software onto workstation and tested system.All working
MSA-DCS | WA3589207 | ICF not responding | West Kimberley Regional Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 13:06:57 | 2020-09-09 14:27:00 | Fail | Arrived onsite, ICF workstation keyboard and mouse not operating correctly.replaced with Seme stock.logged into ICF and checked Gallagher systems and Indigo.confirmed all operational
MSA-DCS | WA3589223 | Unit 8 D9 faulty bunk light | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 15:00:00 | Pass | Repaired bed light
MSA-DCS | WA3589226 | Unit 8, Cell D1- Resecure toilet pan to floor | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-14 09:38:00 | Fail | Removed toilet cleaning floor resilconing pan back down with x4 pan screws
MSA-DCS | WA3589232 | Unit 8, B Wing- No cold water to showers- see further notes below | Hakea Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-14 10:30:00 | Fail | Hot tap was leaking and cold had broken off in set causing no water to pass throw replaced both tap quator turn spindles
MSA-DCS | WA3589244 | Cleaning Party, dayroom - light broken | Hakea Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | Danny Hellwig Electrical Contractors Trust | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 11:00:00 | Pass | Repaired cleaning light
MSA-DCS | WA3589260 | Unit 4, Red 50 power point keeps tripping in the computer room | Casuarina Prison | GMP-BR- HO | Electrical | General Electrical (EL) | Danny Hellwig Electrical Contractors Trust | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 08:30:00 | Pass | Investigate and repair unit 4 circuit red 50
MSA-DCS | WA3589291 | Unit 4, Cell C5- Personal lock needs changing - see further notes below | Casuarina Prison | WSM-BR-SITE | Security | Locksmith (SE) | Lock It Locksmiths | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-09 13:00:00 | Pass | Replace door plate, barrel, lock and weld on strike plate.
MSA-DCS | WA3589307 | Unit 1, Cell A13- Toilet is blocked | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 14:38:20 | 2020-09-04 15:57:00 | Pass | Prisoner intentionally blocked toilet
MSA-DCS | WA3589335 | Imfirmary, Cell B6- Tap is faulty - notes below | Casuarina Prison | GMP-BR- HO | Plumbing & Drainage | Water (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 15:03:13 | 2020-09-04 16:03:00 | Pass | No fault found, job is a double up ofWA3586605
MSA-DCS | WA3589364 | Unit 4, Cell C5- Cell Call not working | Hakea Prison | GMP-BR- HO | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 15:35:01 | 2020-09-08 08:30:00 | Fail | Tested input on the CI8 before I could access the cell. Tested ok at the CI8 and tested ok from the cell.
MSA-DCS | WA3589373 | Kitchen, prisoners toilet - blocked toilet | Melaleuca Prison | GMP-BR- HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 1 | CLOSE | 04 Sep 2020 | 2020-09-05 15:47:22 | 2020-09-04 17:35:00 | Pass | unblocked toilet
MSA-DFES | WA3588932 | ComCen Kitchen - Several lights are not working | DFES Cockburn Emergency Services Complex | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 08:45:00 | Pass | CompleteAttended site and replaced several lights in the comcen kitchen, tested and all in working order
MSA-DFES | WA3589042 | Training Product Development Manager's Office- Door very stiff to open. | FESA RHQ - Forrestfield | GMP-BR | Building | Doors (BU) | Protek 24/7 Building & Maintenance | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-07 16:00:00 | Pass | Drill out door frame inside door striker to allow lockset to latch. Job complete
MSA-DFES | WA3589137 | Administration, BA Service Area - Power Points in BA Service Area not working #B3 – 2 x double power | FESA RHQ - Forrestfield | GMP-BR | Electrical | Lighting, Internal (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-16 16:30:00 | Fail | Completenstalled new circuit in ba room and tested all in working order. Notified staff and signed out
MSA-DTAG | WA3588815 | Ground level, lift 9 - showing out of service | Central Law Courts | GMP-BR-HO | Lifts | Lifts (LI) | Schindler Lifts Australia | 1 | COMP | 04 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-04 09:30:00 | Pass | Replaced car door hanger roller-to be closed out $0
MSA-DTAG | WA3589052 | Lvl 7, Quasi Judicial - Internal office door is slightly tight when opening or closing | Central Law Courts | GMP-BR-HO | Building | Doors (BU) | Midolo Building Services | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-04 12:30:00 | Pass | DOOR ADJUSTMENT MADE- ATTENDED BEFORE LOGGED - 10.00 - 11.30AM
MSA-DTAG | WA3589135 | L6 All cameras displaying “Connection to Server Failed” | State Administrative Tribunal (SAT) | GMP-BR-HO | Security | CCTV Surveillance (SE) | Sapio Pty Ltd | 1 | CLOSE | 04 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-04 16:15:00 | Pass | Checked both Servers all OK
MSA-DTAG | WA3589155 | 1903 lower ground level High pitched, intermittent noise from toilet closest to sinks. | Supreme Court | GMP-BR-HO | Plumbing & Drainage | Toilets/Cisterns (PD) | GPS Plumbing & Gas Services PtyLtd | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 07:35:00 | Pass | Replaced broken inlet valve on female toilet
MSA-DTAG | WA3589295 | Level 5, St Georges Terrace end - Male public toilet blocked | Central Law Courts | GMP-BR-HO | Plumbing & Drainage | Materials (PD) | AHS Services WA Pty Ltd (Anchor) | 1 | CLOSE | 04 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-07 10:00:00 | Pass | Complete
MSA-DTAG | WA3589358 | custody Bio Clean as per notes below | Joondalup Courthouse | WSM-BR-SITE | Cleaning | Emergency Cleans (CL) | ALLCLEAN PROPERTY SERVICES PLUS PTY LTD | 1 | CLOSE | 04 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-05 15:00:00 | Pass | Job carried out as per work order
MSA-DTWD | WA3588907 | S Block, Room S106- Clear faults on fire Panel from Alarm activation | Mount Lawley Campus | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Fire Services Australia (WA) Pty Ltd | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-07 11:00:00 | Pass | False alarm occurrd the previous week
MSA-DTWD | WA3589187 | Residence Laundry - Faulty washing machine | Perth Campus B5 | GMP-BR | Equipment | Cleaning Equipment (EQ) | Falcetta Plumbing and Gas | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-25 11:12:00 | Fail | Had to wait on unit Replaced unit
MSA-DTWD | WA3589228 | E block, E36 pantry store - faulty lock | Bentley Campus | GMP-BR | Security | Locksmith (SE) | SENTINEL LOCK SERVICE PTY LTD | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 15:15:00 | Pass | E Block - faulty door locks.Locks repaired and faulty keys replaced.
MSA-DTWD | WA3589330 | Carpark , bollard - key not working to lower bollard | Kwinana Automotive Centre | GMP-BR | Security | Locksmith (SE) | PEEL LOCK SERVICES PTY LTD | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 11:40:00 | Pass | Key not working bollard
MSA-DTWD | WA3589357 | Lvl 2, Main Entrance - Securex alarm on fault | Perth Campus B2 | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 3 | CLOSE | 04 Sep 2020 | 2020-09-11 17:00:00 | 2020-09-08 08:15:00 | Pass | 08/09/2020, 730-815Bugs inside sensor. Cleaned and tested ok.
MSA-DTWD | WA3589371 | G block woodwork shop Suspended power point socket damaged. Has been tagged. | Mandurah Campus (formerly Peel) | GMP-BR | Electrical | General Electrical (EL) | AWB Co. | 2 | CLOSE | 04 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-08 08:15:00 | Pass | Attended site. Admin not open till 8. Found G block. Located damaged suspended Gpo. Repaired Gpo and tested. All now working. Informed lecture on site. Completed paper work. Waiting on admin to open at 8 for css
MSA-MRWA | WA3589171 | North West auto door - Exit button for sliding door is inoperable, please remediate | Road Network Operation Centre (RNOC)-Main Building-Second Floor-Real Time Traffic Operations | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 04 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-04 15:26:00 | Pass | A40568470N - Inspected and problem with internal push button that is controlled by access control. Requires access to rectify
MSA-DCS | WA3589585 | SITE COST Operational area Sink is leaking and water damage to the cupboard and affecting electrical | Hakea Prison-Main Gatehouse | WSM-BR-SITE | Plumbing & Drainage | Water (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 05 Sep 2020 | 2020-09-05 12:02:56 | 2020-09-05 10:03:00 | Pass | Locate and repair leak to sink
MSA-DCS | WA3589597 | Main oven in the kitchen is not working | Bandyup Prison | GMP-BR- HO | Equipment | Catering Equipment (EQ) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 05 Sep 2020 | 2020-09-05 13:20:33 | 2020-09-05 17:10:00 | Fail | Returned after verbal approval with part. Replaced Main pcb and tested ok.
MSA-DCS | WA3589615 | Bandyup Prison - main kitchen second oven fan needs to be repalced | Bandyup Prison | GMP-BR- HO | Electrical | General Electrical (EL) | COMCARE (FOODSERVICE) REPAIRS P/L | 0 | CLOSE | 05 Sep 2020 | 2020-09-05 15:31:31 | 2020-09-15 11:30:00 | Fail | Returned 15/09 with fan motor, replaced and tested ok.
MSA-DCS | WA3589623 | unit 5 cell C7 mainlock stucjk in lock and prisoner in there URG | Hakea Prison | GMP-BR- HO | Building | Materials (BU) | AAA Ability Locksmiths | 0 | CLOSE | 05 Sep 2020 | 2020-09-05 16:46:49 | 2020-09-07 14:30:00 | Fail | 05/09/2020 After hours attendance (Saturday). Forcibly gained entry to release trapped prisoner. Replacement lock required.07/09/2020 On site. Replaced main lock to restore normal function.
MSA-DCS | WA3589626 | SITE COST Unit 1- Security monitors are frozen /down | Melaleuca Prison | WSM-BR-SITE | Security | Security Management System (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 05 Sep 2020 | 2020-09-05 17:01:00 | 2020-09-05 15:45:00 | Pass | Found unit 1 cctv had frozen on both screen, restart workstation, bring up views, tested all ok.
MSA-DCS | WA3589634 | dinning room bainmarie - blown a fuse | Bandyup Prison | GMP-BR- HO | Electrical | Lighting, Internal (EL) | EASTERN HILLS ELECTRICAL SERVICE | 1 | CLOSE | 05 Sep 2020 | 2020-09-06 15:45:04 | 2020-09-05 18:00:00 | Pass | Isolated faulty Bain Marie in dinning room and reset power
MSA-DFES | WA3590974 | **Retrospective work order** Main Fire panel, test fire panel, further notes below | DFES Cockburn Emergency Services Complex | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 05 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-05 12:00:00 | Pass | Attended site to meet Sontec Set alarms off on FIP for testing and repairs of fire door/access controlsGenerated alarms and reset as requestedIssues resolved by Sontect
MSA-DCA | WA3589658 | MAritime Museum - no lights in the entire site | Maritime Museum Victoria Quay | GMP-BR | Electrical | General Electrical (EL) | INSIGHT ELECTRICAL TECHNOLOGY | 0 | CLOSE | 06 Sep 2020 | 2020-09-06 11:27:14 | 2020-09-06 13:45:00 | Fail | Dynalite system is outdated and obsolete. System is continually having issues and needs upgrading. Have been able to restore lighting but same issues will happen again.
MSA-DCA | WA3589755 | water leak in art gallery from ceiling | Art Gallery of WA - James St-Centenary Gallery-Ground Floor | GMP-BR | Building | Materials (BU) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 06 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-08 09:15:00 | Fail | 08/09/2020 09:48 AM (UTC+08:00) - crispin@protek247.com.au Have attended site and carried out repairs to suspected source of leak. Will need to confirm later this week with further rain forecast to see if the problem has been resolved. Will need to discus scope of ceiling repair works with site once leak has been resolved.
MSA-DCS | WA3589652 | SITE COST Zone 14- alarms on the omnitrax has stopped working altogether. | Bandyup Prison | WSM-BR-SITE | Security | Monitoring (SE) | Seme Solutions Pty Ltd | 0 | CLOSE | 06 Sep 2020 | 2020-09-06 09:21:40 | 2020-09-07 08:30:00 | Fail | Attended site checked and found Zone14 Microwave alarm not activated during test. Further check located the problem to be the microwave alarm output cable fault to Cardax controller. Rectified the cable fault and tested it ok. Job actual start time is 6:45 06/09/20, finished time 8:30 06/09/20. Accidentally selected wrong date on Promap app.
MSA-DCS | WA3589662 | SALLYPORT Main gate- Ram at the front is sticking. Barrier keeps jamming. | Melaleuca Prison | GMP-BR- HO | Building | Materials (BU) | AFD Contracting | 1 | CLOSE | 06 Sep 2020 | 2020-09-07 08:53:14 | 2020-09-07 13:30:00 | Fail | 07/09/20Loaded vehicle.Cleaned out all pins and degreased.Grub screw missing on pin collar.Sourced then collected grub screw.Reinserted collar so pins all line up and replaced grub screw.
MSA-DCS | WA3589730 | SITE COST CCU -Cell H 8 Toilet in the cell is continuously running but not flushing. | Hakea Prison | WSM-BR-SITE | Plumbing & Drainage | Materials (PD) | GPS Plumbing & Gas Services PtyLtd | 0 | CLOSE | 06 Sep 2020 | 2020-09-06 15:27:02 | 2020-09-06 13:32:00 | Pass | Renew inlet valve and outlet washer to cistern
MSA-DCS | WA3589750 | one of the computer in control room not working | West Kimberley Regional Prison | GMP-BR- HO | Security | Keys & Access (SE) | Seme Solutions Pty Ltd | 2 | CLOSE | 06 Sep 2020 | 2020-09-09 17:00:00 | 2020-09-09 14:31:00 | Pass | Fault displaying senstar integration module not installed on server.Shutdown Gallagher services and attempted to repair. Unable to. Unistalled and reinstalled.Restarted server and tested system
MSA-DCS | WA3589753 | SITE COST S.O.G base, water leaking between window and ceiling | Hakea Prison | WSM-BR-SITE | Building | Materials (BU) | Midolo Building Services | 0 | CLOSE | 06 Sep 2020 | 2020-09-06 19:48:39 | 2020-09-09 12:15:00 | Fail | LEAK LOCATED & REPAIRED
MSA-DFES | WA3592902 | RETROSPECTIVE WORK ORDER-wind has set off alarm - DO NOT ATTEND | CFRS Midland | GMP-BR | Security | Monitoring (SE) | Securex Security Systems & Services | 1 | CLOSE | 06 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-06 12:22:00 | Pass | Despatch Comments:SINGLE ZN 13 R/S ROLLER DOOR 4Patrol Resolution:ROLLER DOOR SECURED VERY WINDY SO I THINK ITS MOVING THE DOOR SLIGHTLY RESET PANEL WITH GOOD SEAL FROM DANNY
MSA-DFES | WA3593334 | Retrospective work order - SINGLE ZONE 13 R/S ROLLER DOOR 4 | CFRS Midland | GMP-BR | Security | Security Management System (SE) | Securex Security Systems & Services | 1 | CLOSE | 06 Sep 2020 | 2020-09-07 17:00:00 | 2020-09-06 11:21:00 | Pass | Job completed - ALL SECURE AND CORRECT BACK DOOR ROLLER DOOR WAS SLIGHTLY OPEN NOW SECURED
MSA-DCA | WA3589770 | Automatic door-Side access disability door is not opening at all. | Maritime Museum Victoria Quay | GMP-BR | Building | Doors (BU) | Dormakaba Australia Pty Ltd | 0 | CLOSE | 07 Sep 2020 | 2020-09-07 09:35:29 | 2020-09-07 09:27:00 | Pass | Inspected door and replaced old relay, tested door and found no signal coming back down from access system, advised site to canal out access tech.
MSA-DCA | WA3590028 | step lights not working | PICA-Main Building-Ground Floor-PICA Performance Space | GMP-BR | Electrical | Lighting, Internal (EL) | Techworks Electrical | 2 | CLOSE | 07 Sep 2020 | 2020-09-10 17:00:00 | 2020-09-09 14:52:00 | Pass | Repaired step lights not working in performance area
MSA-DCA | WA3590234 | Basement Corridor fire exit door, mechanism intermittently faulty, door latch does not fully depress | His Majesty's Theatre-Theatre Building-Basement | GMP-BR | Security | Locksmith (SE) | ADVANCED LOCK & KEY | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 15:30:00 | Pass | replace faulty heavy duty adjustable latch to stairwell fire exit internal door
MSA-DCA | WA3590287 | Fault on Vesda 6 which covers collection boxes 2 and 3 | Collection and Research Centre Welshpool-CRC & Warehouse-Ground Floor | GMP-BR | Fire Protection Services | Fire Protection - Monitor System (FP) | Critical Fire Protection & Training | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-08 13:30:00 | Pass | Inspect Vesda 6 faultsReplace filters reprogramme vesdareset panel and vesda
MSA-DCA | WA3590356 | Ladies toilet/ disabled toilet - rain water leak | The Blue Room-Main Building-Ground Floor-Female Toilets | GMP-BR | Roofing | Metal Roofing (RF) | Protek 24/7 Building & Maintenance | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-14 09:00:00 | Fail | 8/9/20 - Have attended and completed half of the repair work. Were advised by site that we couldn't continue as a performance was going to start in the theatre below where we were working Will need to return to completeScheduled to return to complete Monday Sept 14 .30/9 No further leaks reported
MSA-DCA | WA3590373 | Toilet Door Not Closing | Sunset Hospital Heritage Precinct-Building G-Two Storey Ward Block-Ground Floor-Disabled Toilet - New Toilet Block | GMP-BR | Building | Automatic Doors (BU) | Dormakaba Australia Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 17:00:00 | 2020-09-07 14:47:00 | Pass | Arrived onsite and rang David from Programmed and to confirm the door is for the disabled toilet, found door had a manual closer. Found the bottom of the door is rubbing against the floor due to the wood has swollen from water tried to lift the door but requires a carpenter to repair. Rang David and explained the problem and he said he will organise a contractor to repair.
MSA-DCS | WA3589837 | front gate kitchen hot water billy not operating | Wandoo Rehabilitation Facility | GMP-BR- HO | Plumbing & Drainage | HWS/Units Electric & Gas (PD) | Water2water Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 07:13:59 | 2020-09-07 16:43:00 | Pass | Reports of steam and hissing coming from unit this morning and isolated at GPO. On arrival reactivated unit. All worked ok and appeared to be filling and heating correctly. Came back in arvo to hook unit up toDiagnostic computer program and all working as would be normal.
MSA-DCS | WA3589845 | Unit 1 control room CCTV not working | Hakea Prison | GMP-BR- HO | Security | CCTV Surveillance (SE) | Seme Solutions Pty Ltd | 1 | CLOSE | 07 Sep 2020 | 2020-09-08 07:21:59 | 2020-09-07 10:00:00 | Pass | Attended site checked and found Unit 1 Control room right hand side monitor not showing cameras. Further check located problem to be Indigovision Control Center problem. Reassigned cameras to monitor and tested it ok.